## EO66 Points (v2.15 - Released).
Definition | Definition (Numbers) | Display Name | Display Name (Numbers) | Documentation | Regular Expression | Trend in BMS | Import into SkySpark | Totalized | Kind/Type Order | Units/Facets (Boolean) | Units/Facets (String/Enumeration) | Units/Facets (Imperial) | Units/Facets (Metric) | Precision (Imperial) | Precision (Metric) | Stage | Phase | Markers | Equipment | Versions
ahuDischargeDamper | ahuDischargeDamper | AHU Discharge Damper Command | AHU Discharge Damper Command |  | ahuDischargeDamper | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | parent,entering,air,damper,position,cmd | DH,FPB,HP,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
ahuDischargeDamperFb | ahuDischargeDamperFb | AHU Discharge Damper Feedback | AHU Discharge Damper Feedback |  | ahuDischargeDamperFb | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | parent,entering,air,damper,position,sensor | DH,FPB,HP,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
ahuDischargeFanStatus | ahuDischargeFanStatus | AHU Discharge Fan Status | AHU Discharge Fan Status |  | ahuDischargeFanStatus | No | No | No | Bool | On/Off | On/Off | [6 empty] | parent,entering,air,fan,status,sensor | DH,FPB,HP,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
ahuDischargeFlow | ahuDischargeFlow | AHU Discharge Flow | AHU Discharge Flow |  | ahuDischargeFlow | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | parent,entering,air,flow,sensor | DH,FPB,HP,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
ahuDischargeFlowSp | ahuDischargeFlowSp | AHU Discharge Flow Setpoint | AHU Discharge Flow Setpoint |  | ahuDischargeFlowSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | parent,entering,air,flow,sp | DH,FPB,HP,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
ahuDischargePressure | ahuDischargePressure | AHU Discharge Pressure | AHU Discharge Pressure |  | ahuDischargePressure | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | parent,entering,air,pressure,sensor | DH,FPB,HP,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
ahuDischargeTemp | ahuDischargeTemp | AHU Discharge Temperature | AHU Discharge Temperature |  | ahuDischargeTemp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | parent,entering,air,temp,sensor | DH,FPB,HP,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
airConditionerAlarm | airConditionerXXXXAlarm | Air Conditioner Alarm | Air Conditioner XX Alarm |  | airConditioner(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | airConditioner,common,alarm | AC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
airConditioner | airConditionerXXXX | Air Conditioner Command | Air Conditioner XX Command |  | airConditioner(\d{0,4}) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | airConditioner,status,cmd | AC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
airConditionerStatus | airConditionerXXXXStatus | Air Conditioner Status | Air Conditioner XX Status |  | airConditioner(\d{0,4})Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | airConditioner,status,sensor | AC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexBypassDamperAlarm | aexBypassDamperAlarm | Air Exchanger Bypass Damper Alarm | Air Exchanger Bypass Damper Alarm |  | aexBypassDamperAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | aex,bypass,damper,position,alarm | AHU,DHU,DOAS,ERU,HRU,RTU | 2.15 (Released),2.16 (Pre-Release)
aexBypassDamper | aexBypassDamper | Air Exchanger Bypass Damper Command | Air Exchanger Bypass Damper Command |  | aexBypassDamper | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | aex,bypass,damper,position,cmd | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexBypassDamperFb | aexBypassDamperFb | Air Exchanger Bypass Damper Feedback | Air Exchanger Bypass Damper Feedback |  | aexBypassDamperFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | aex,bypass,damper,position,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexDischargeEnthalpy | aexDischargeEnthalpy | Air Exchanger Discharge Enthalpy | Air Exchanger Discharge Enthalpy |  | aexDischargeEnthalpy | Yes | Yes | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | aex,discharge,air,enthalpy,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexDischargeFanAlarm | aexDischargeFanAlarm | Air Exchanger Discharge Fan Alarm | Air Exchanger Discharge Fan Alarm |  | aexDischargeFanAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | aex,discharge,air,fan,common,alarm | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexDischargeFanAlarmReset | aexDischargeFanAlarmReset | Air Exchanger Discharge Fan Alarm Reset | Air Exchanger Discharge Fan Alarm Reset |  | aexDischargeFanAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | aex,discharge,air,fan,alarm,reset | AHU,DHU,DOAS,ERU,HRU,RTU | 2.15 (Released),2.16 (Pre-Release)
aexDischargeFan | aexDischargeFan | Air Exchanger Discharge Fan Command | Air Exchanger Discharge Fan Command |  | aexDischargeFan | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | aex,discharge,air,fan,status,cmd | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexDischargeFanCurrent | aexDischargeFanCurrent | Air Exchanger Discharge Fan Current | Air Exchanger Discharge Fan Current |  | aexDischargeFanCurrent | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | aex,discharge,air,fan,current,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexDischargeFanEnteringPressure | aexDischargeFanEnteringPressure | Air Exchanger Discharge Fan Entering Pressure | Air Exchanger Discharge Fan Entering Pressure |  | aexDischargeFanEnteringPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | aex,discharge,air,fan,entering,pressure,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexDischargeFanFault | aexDischargeFanFault | Air Exchanger Discharge Fan Fault | Air Exchanger Discharge Fan Fault |  | aexDischargeFanFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | aex,discharge,air,fan,fault | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexDischargeFanLeavingPressure | aexDischargeFanLeavingPressure | Air Exchanger Discharge Fan Leaving Pressure | Air Exchanger Discharge Fan Leaving Pressure |  | aexDischargeFanLeavingPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | aex,discharge,air,fan,leaving,pressure,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexDischargeFanMaintSwitch | aexDischargeFanMaintSwitch | Air Exchanger Discharge Fan Maintenance Switch | Air Exchanger Discharge Fan Maintenance Switch |  | aexDischargeFanMaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | maintenance,switch,cmd,aex,discharge,fan,air | AHU,DHU,DOAS,ERU,HRU,RTU | 2.15 (Released),2.16 (Pre-Release)
aexDischargeFanOvr | aexDischargeFanOvr | Air Exchanger Discharge Fan Override | Air Exchanger Discharge Fan Override |  | aexDischargeFanOvr | No | No | No | Bool | On/Off | On/Off | [6 empty] | aex,discharge,air,fan,status,ovr | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexDischargeFanPressureDelta | aexDischargeFanPressureDelta | Air Exchanger Discharge Fan Pressure Delta | Air Exchanger Discharge Fan Pressure Delta |  | aexDischargeFanPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | aex,discharge,air,fan,common,pressure,delta,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexDischargeFanPressureHiAlarm | aexDischargeFanPressureHiAlarm | Air Exchanger Discharge Fan Pressure High Alarm | Air Exchanger Discharge Fan Pressure High Alarm |  | aexDischargeFanPressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | aex,discharge,air,fan,pressure,high,alarm | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexDischargeFanPressureHiSp | aexDischargeFanPressureHiSp | Air Exchanger Discharge Fan Pressure High Setpoint | Air Exchanger Discharge Fan Pressure High Setpoint |  | aexDischargeFanPressureHiSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | aex,discharge,air,fan,pressure,high,sp | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexDischargeFanPressureLoAlarm | aexDischargeFanPressureLoAlarm | Air Exchanger Discharge Fan Pressure Low Alarm | Air Exchanger Discharge Fan Pressure Low Alarm |  | aexDischargeFanPressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | aex,discharge,air,fan,pressure,low,alarm | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexDischargeFanPressureLoSp | aexDischargeFanPressureLoSp | Air Exchanger Discharge Fan Pressure Low Setpoint | Air Exchanger Discharge Fan Pressure Low Setpoint |  | aexDischargeFanPressureLoSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | aex,discharge,air,fan,pressure,low,sp | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexDischargeFanRuntime | aexDischargeFanRuntime | Air Exchanger Discharge Fan Runtime | Air Exchanger Discharge Fan Runtime |  | aexDischargeFanRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,DHU,DOAS,ERU,HRU,RTU | 2.15 (Released),2.16 (Pre-Release)
aexDischargeFanSpeed | aexDischargeFanSpeed | Air Exchanger Discharge Fan Speed | Air Exchanger Discharge Fan Speed |  | aexDischargeFanSpeed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | aex,discharge,air,fan,speed,cmd | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexDischargeFanSpeedFb | aexDischargeFanSpeedFb | Air Exchanger Discharge Fan Speed Feedback | Air Exchanger Discharge Fan Speed Feedback |  | aexDischargeFanSpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | aex,discharge,air,fan,speed,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexDischargeFanSpeedMaxSp | aexDischargeFanSpeedMaxSp | Air Exchanger Discharge Fan Speed Max Setpoint | Air Exchanger Discharge Fan Speed Max Setpoint |  | aexDischargeFanSpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | aex,discharge,air,fan,speed,max,sp | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexDischargeFanSpeedMinSp | aexDischargeFanSpeedMinSp | Air Exchanger Discharge Fan Speed Min Setpoint | Air Exchanger Discharge Fan Speed Min Setpoint |  | aexDischargeFanSpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | aex,discharge,air,fan,speed,min,sp | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexDischargeFanSpeedOvr | aexDischargeFanSpeedOvr | Air Exchanger Discharge Fan Speed Override | Air Exchanger Discharge Fan Speed Override |  | aexDischargeFanSpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | aex,discharge,air,fan,speed,ovr | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexDischargeFanSpeedSp | aexDischargeFanSpeedSp | Air Exchanger Discharge Fan Speed Setpoint | Air Exchanger Discharge Fan Speed Setpoint |  | aexDischargeFanSpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | aex,discharge,air,fan,speed,effective,sp | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexDischargeFanStatus | aexDischargeFanStatus | Air Exchanger Discharge Fan Status | Air Exchanger Discharge Fan Status |  | aexDischargeFanStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | aex,discharge,air,fan,status,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexDischargeFlow | aexDischargeFlow | Air Exchanger Discharge Flow | Air Exchanger Discharge Flow |  | aexDischargeFlow | Yes | Yes | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | aex,discharge,air,flow,sensor | AFMS,AHU,CU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexDischargeHumidity | aexDischargeHumidity | Air Exchanger Discharge Humidity | Air Exchanger Discharge Humidity |  | aexDischargeHumidity | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | aex,discharge,air,humidity,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexDischargeIsoDamper | aexDischargeIsoDamper | Air Exchanger Discharge Isolation Damper Command | Air Exchanger Discharge Isolation Damper Command |  | aexDischargeIsoDamper | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | aex,discharge,iso,air,damper,status,cmd | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexDischargeIsoDamperFb | aexDischargeIsoDamperFb | Air Exchanger Discharge Isolation Damper Feedback | Air Exchanger Discharge Isolation Damper Feedback |  | aexDischargeIsoDamperFb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | aex,discharge,iso,air,damper,status,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexDischargePressure | aexDischargePressure | Air Exchanger Discharge Pressure | Air Exchanger Discharge Pressure |  | aexDischargePressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | aex,discharge,air,static,pressure,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexDischargeTemp | aexDischargeTemp | Air Exchanger Discharge Temperature | Air Exchanger Discharge Temperature |  | aexDischargeTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | aex,discharge,air,temp,sensor | AFMS,AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexDischargeTempLoAlarm | aexDischargeTempLoAlarm | Air Exchanger Discharge Temperature Low Alarm | Air Exchanger Discharge Temperature Low Alarm |  | aexDischargeTempLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | aex,discharge,air,temp,low,alarm | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexDischargeVelPressure | aexDischargeVelPressure | Air Exchanger Discharge Velocity Pressure | Air Exchanger Discharge Velocity Pressure |  | aexDischargeVelPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | aex,discharge,air,dynamic,pressure,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexExhaustEnthalpy | aexExhaustEnthalpy | Air Exchanger Exhaust Enthalpy | Air Exchanger Exhaust Enthalpy |  | aexExhaustEnthalpy | Yes | Yes | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | aex,exhaust,air,enthalpy,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexExhaustFanAlarm | aexExhaustFanAlarm | Air Exchanger Exhaust Fan Alarm | Air Exchanger Exhaust Fan Alarm |  | aexExhaustFanAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | aex,exhaust,air,fan,common,alarm | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexExhaustFanAlarmReset | aexExhaustFanAlarmReset | Air Exchanger Exhaust Fan Alarm Reset | Air Exchanger Exhaust Fan Alarm Reset |  | aexExhaustFanAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | aex,air,fan,alarm,reset,exhaust | AHU,DHU,DOAS,ERU,HRU,RTU | 2.15 (Released),2.16 (Pre-Release)
aexExhaustFan | aexExhaustFan | Air Exchanger Exhaust Fan Command | Air Exchanger Exhaust Fan Command |  | aexExhaustFan | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | aex,exhaust,air,fan,status,cmd | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexExhaustFanCurrent | aexExhaustFanCurrent | Air Exchanger Exhaust Fan Current | Air Exchanger Exhaust Fan Current |  | aexExhaustFanCurrent | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | aex,exhaust,air,fan,current,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexExhaustFanEnteringPressure | aexExhaustFanEnteringPressure | Air Exchanger Exhaust Fan Entering Pressure | Air Exchanger Exhaust Fan Entering Pressure |  | aexExhaustFanEnteringPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | aex,exhaust,air,fan,entering,pressure,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexExhaustFanFault | aexExhaustFanFault | Air Exchanger Exhaust Fan Fault | Air Exchanger Exhaust Fan Fault |  | aexExhaustFanFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | aex,exhaust,air,fan,fault | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexExhaustFanLeavingPressure | aexExhaustFanLeavingPressure | Air Exchanger Exhaust Fan Leaving Pressure | Air Exchanger Exhaust Fan Leaving Pressure |  | aexExhaustFanLeavingPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | aex,exhaust,air,fan,leaving,pressure,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexExhaustFanMaintSwitch | aexExhaustFanMaintSwitch | Air Exchanger Exhaust Fan Maintenance Switch | Air Exchanger Exhaust Fan Maintenance Switch |  | aexExhaustFanMaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | maintenance,switch,cmd,aex,fan,air,exhaust | AHU,DHU,DOAS,ERU,HRU,RTU | 2.15 (Released),2.16 (Pre-Release)
aexExhaustFanOvr | aexExhaustFanOvr | Air Exchanger Exhaust Fan Override | Air Exchanger Exhaust Fan Override |  | aexExhaustFanOvr | No | No | No | Bool | On/Off | On/Off | [6 empty] | aex,exhaust,air,fan,status,ovr | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexExhaustFanPressureDelta | aexExhaustFanPressureDelta | Air Exchanger Exhaust Fan Pressure Delta | Air Exchanger Exhaust Fan Pressure Delta |  | aexExhaustFanPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | aex,exhaust,air,fan,common,pressure,delta,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexExhaustFanPressureHiAlarm | aexExhaustFanPressureHiAlarm | Air Exchanger Exhaust Fan Pressure High Alarm | Air Exchanger Exhaust Fan Pressure High Alarm |  | aexExhaustFanPressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | aex,exhaust,air,fan,pressure,high,alarm | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexExhaustFanPressureHiSp | aexExhaustFanPressureHiSp | Air Exchanger Exhaust Fan Pressure High Setpoint | Air Exchanger Exhaust Fan Pressure High Setpoint |  | aexExhaustFanPressureHiSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | aex,exhaust,air,fan,pressure,high,sp | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexExhaustFanPressureLoAlarm | aexExhaustFanPressureLoAlarm | Air Exchanger Exhaust Fan Pressure Low Alarm | Air Exchanger Exhaust Fan Pressure Low Alarm |  | aexExhaustFanPressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | aex,exhaust,air,fan,pressure,low,alarm | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexExhaustFanPressureLoSp | aexExhaustFanPressureLoSp | Air Exchanger Exhaust Fan Pressure Low Setpoint | Air Exchanger Exhaust Fan Pressure Low Setpoint |  | aexExhaustFanPressureLoSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | aex,exhaust,air,fan,pressure,low,sp | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexExhaustFanRuntime | aexExhaustFanRuntime | Air Exchanger Exhaust Fan Runtime | Air Exchanger Exhaust Fan Runtime |  | aexExhaustFanRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,DHU,DOAS,ERU,HRU,RTU | 2.15 (Released),2.16 (Pre-Release)
aexExhaustFanSpeed | aexExhaustFanSpeed | Air Exchanger Exhaust Fan Speed | Air Exchanger Exhaust Fan Speed |  | aexExhaustFanSpeed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | aex,exhaust,air,fan,speed,cmd | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexExhaustFanSpeedFb | aexExhaustFanSpeedFb | Air Exchanger Exhaust Fan Speed Feedback | Air Exchanger Exhaust Fan Speed Feedback |  | aexExhaustFanSpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | aex,exhaust,air,fan,speed,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexExhaustFanSpeedMaxSp | aexExhaustFanSpeedMaxSp | Air Exchanger Exhaust Fan Speed Max Setpoint | Air Exchanger Exhaust Fan Speed Max Setpoint |  | aexExhaustFanSpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | aex,exhaust,air,fan,speed,max,sp | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexExhaustFanSpeedMinSp | aexExhaustFanSpeedMinSp | Air Exchanger Exhaust Fan Speed Min Setpoint | Air Exchanger Exhaust Fan Speed Min Setpoint |  | aexExhaustFanSpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | aex,exhaust,air,fan,speed,min,sp | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexExhaustFanSpeedOvr | aexExhaustFanSpeedOvr | Air Exchanger Exhaust Fan Speed Override | Air Exchanger Exhaust Fan Speed Override |  | aexExhaustFanSpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | aex,exhaust,air,fan,speed,ovr | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexExhaustFanSpeedSp | aexExhaustFanSpeedSp | Air Exchanger Exhaust Fan Speed Setpoint | Air Exchanger Exhaust Fan Speed Setpoint |  | aexExhaustFanSpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | aex,exhaust,air,fan,speed,effective,sp | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexExhaustFanStatus | aexExhaustFanStatus | Air Exchanger Exhaust Fan Status | Air Exchanger Exhaust Fan Status |  | aexExhaustFanStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | aex,exhaust,air,fan,status,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexExhaustFlow | aexExhaustFlow | Air Exchanger Exhaust Flow | Air Exchanger Exhaust Flow |  | aexExhaustFlow | Yes | Yes | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | aex,exhaust,air,flow,sensor | AFMS,AHU,CU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexExhaustHumidity | aexExhaustHumidity | Air Exchanger Exhaust Humidity | Air Exchanger Exhaust Humidity |  | aexExhaustHumidity | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | aex,exhaust,air,humidity,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexExhaustIsoDamper | aexExhaustIsoDamper | Air Exchanger Exhaust Isolation Damper Command | Air Exchanger Exhaust Isolation Damper Command |  | aexExhaustIsoDamper | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | aex,exhaust,iso,air,damper,status,cmd | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexExhaustIsoDamperFb | aexExhaustIsoDamperFb | Air Exchanger Exhaust Isolation Damper Feedback | Air Exchanger Exhaust Isolation Damper Feedback |  | aexExhaustIsoDamperFb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | aex,exhaust,iso,air,damper,status,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexExhaustPressure | aexExhaustPressure | Air Exchanger Exhaust Pressure | Air Exchanger Exhaust Pressure |  | aexExhaustPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | aex,exhaust,air,static,pressure,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexExhaustTemp | aexExhaustTemp | Air Exchanger Exhaust Temperature | Air Exchanger Exhaust Temperature |  | aexExhaustTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | aex,exhaust,air,temp,sensor | AFMS,AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexExhaustVelPressure | aexExhaustVelPressure | Air Exchanger Exhaust Velocity Pressure | Air Exchanger Exhaust Velocity Pressure |  | aexExhaustVelPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | aex,exhaust,air,dynamic,pressure,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexFaceBypassDamperAlarm | aexFaceBypassDamperAlarm | Air Exchanger Face Bypass Damper Alarm | Air Exchanger Face Bypass Damper Alarm |  | aexFaceBypassDamperAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | aex,faceBypass,damper,position,alarm | AHU,DHU,DOAS,ERU,HRU,RTU | 2.15 (Released),2.16 (Pre-Release)
aexFaceBypassDamper | aexFaceBypassDamper | Air Exchanger Face Bypass Damper Command | Air Exchanger Face Bypass Damper Command |  | aexFaceBypassDamper | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | aex,faceBypass,damper,position,cmd | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexFaceBypassDamperFb | aexFaceBypassDamperFb | Air Exchanger Face Bypass Damper Feedback | Air Exchanger Face Bypass Damper Feedback |  | aexFaceBypassDamperFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | aex,faceBypass,damper,position,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexFaceDamper | aexFaceDamper | Air Exchanger Face Damper Command | Air Exchanger Face Damper Command |  | aexFaceDamper | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | aex,face,damper,position,cmd | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexFaceDamperEnableDb | aexFaceDamperEnableDb | Air Exchanger Face Damper Enable Deadband | Air Exchanger Face Damper Enable Deadband |  | aexFaceDamperEnableDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | aex,face,damper,position,enable,deadband,sp | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexFaceDamperFb | aexFaceDamperFb | Air Exchanger Face Damper Feedback | Air Exchanger Face Damper Feedback |  | aexFaceDamperFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | aex,face,damper,position,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexOutsideEnthalpy | aexOutsideEnthalpy | Air Exchanger Outside Enthalpy | Air Exchanger Outside Enthalpy |  | aexOutsideEnthalpy | Yes | Yes | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | aex,outside,air,enthalpy,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexOutsideFanAlarm | aexOutsideFanAlarm | Air Exchanger Outside Fan Alarm | Air Exchanger Outside Fan Alarm |  | aexOutsideFanAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | aex,outside,air,fan,common,alarm | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexOutsideFanAlarmReset | aexOutsideFanAlarmReset | Air Exchanger Outside Fan Alarm Reset | Air Exchanger Outside Fan Alarm Reset |  | aexOutsideFanAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | aex,air,fan,alarm,reset,outside | AHU,DHU,DOAS,ERU,HRU,RTU | 2.15 (Released),2.16 (Pre-Release)
aexOutsideFan | aexOutsideFan | Air Exchanger Outside Fan Command | Air Exchanger Outside Fan Command |  | aexOutsideFan | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | aex,outside,air,fan,status,cmd | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexOutsideFanCurrent | aexOutsideFanCurrent | Air Exchanger Outside Fan Current | Air Exchanger Outside Fan Current |  | aexOutsideFanCurrent | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | aex,outside,air,fan,current,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexOutsideFanEnteringPressure | aexOutsideFanEnteringPressure | Air Exchanger Outside Fan Entering Pressure | Air Exchanger Outside Fan Entering Pressure |  | aexOutsideFanEnteringPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | aex,outside,air,fan,entering,pressure,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexOutsideFanFault | aexOutsideFanFault | Air Exchanger Outside Fan Fault | Air Exchanger Outside Fan Fault |  | aexOutsideFanFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | aex,outside,air,fan,fault | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexOutsideFanLeavingPressure | aexOutsideFanLeavingPressure | Air Exchanger Outside Fan Leaving Pressure | Air Exchanger Outside Fan Leaving Pressure |  | aexOutsideFanLeavingPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | aex,outside,air,fan,leaving,pressure,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexOutsideFanMaintSwitch | aexOutsideFanMaintSwitch | Air Exchanger Outside Fan Maintenance Switch | Air Exchanger Outside Fan Maintenance Switch |  | aexOutsideFanMaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | maintenance,switch,cmd,aex,fan,air,outside | AHU,DHU,DOAS,ERU,HRU,RTU | 2.15 (Released),2.16 (Pre-Release)
aexOutsideFanOvr | aexOutsideFanOvr | Air Exchanger Outside Fan Override | Air Exchanger Outside Fan Override |  | aexOutsideFanOvr | No | No | No | Bool | On/Off | On/Off | [6 empty] | aex,outside,air,fan,status,ovr | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexOutsideFanPressureDelta | aexOutsideFanPressureDelta | Air Exchanger Outside Fan Pressure Delta | Air Exchanger Outside Fan Pressure Delta |  | aexOutsideFanPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | aex,outside,air,fan,common,pressure,delta,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexOutsideFanPressureHiAlarm | aexOutsideFanPressureHiAlarm | Air Exchanger Outside Fan Pressure High Alarm | Air Exchanger Outside Fan Pressure High Alarm |  | aexOutsideFanPressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | aex,outside,air,fan,pressure,high,alarm | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexOutsideFanPressureHiSp | aexOutsideFanPressureHiSp | Air Exchanger Outside Fan Pressure High Setpoint | Air Exchanger Outside Fan Pressure High Setpoint |  | aexOutsideFanPressureHiSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | aex,outside,air,fan,pressure,high,sp | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexOutsideFanPressureLoAlarm | aexOutsideFanPressureLoAlarm | Air Exchanger Outside Fan Pressure Low Alarm | Air Exchanger Outside Fan Pressure Low Alarm |  | aexOutsideFanPressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | aex,outside,air,fan,pressure,low,alarm | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexOutsideFanPressureLoSp | aexOutsideFanPressureLoSp | Air Exchanger Outside Fan Pressure Low Setpoint | Air Exchanger Outside Fan Pressure Low Setpoint |  | aexOutsideFanPressureLoSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | aex,outside,air,fan,pressure,low,sp | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexOutsideFanRuntime | aexOutsideFanRuntime | Air Exchanger Outside Fan Runtime | Air Exchanger Outside Fan Runtime |  | aexOutsideFanRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,DHU,DOAS,ERU,HRU,RTU | 2.15 (Released),2.16 (Pre-Release)
aexOutsideFanSpeed | aexOutsideFanSpeed | Air Exchanger Outside Fan Speed | Air Exchanger Outside Fan Speed |  | aexOutsideFanSpeed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | aex,outside,air,fan,speed,cmd | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexOutsideFanSpeedFb | aexOutsideFanSpeedFb | Air Exchanger Outside Fan Speed Feedback | Air Exchanger Outside Fan Speed Feedback |  | aexOutsideFanSpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | aex,outside,air,fan,speed,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexOutsideFanSpeedMaxSp | aexOutsideFanSpeedMaxSp | Air Exchanger Outside Fan Speed Max Setpoint | Air Exchanger Outside Fan Speed Max Setpoint |  | aexOutsideFanSpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | aex,outside,air,fan,speed,max,sp | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexOutsideFanSpeedMinSp | aexOutsideFanSpeedMinSp | Air Exchanger Outside Fan Speed Min Setpoint | Air Exchanger Outside Fan Speed Min Setpoint |  | aexOutsideFanSpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | aex,outside,air,fan,speed,min,sp | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexOutsideFanSpeedOvr | aexOutsideFanSpeedOvr | Air Exchanger Outside Fan Speed Override | Air Exchanger Outside Fan Speed Override |  | aexOutsideFanSpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | aex,outside,air,fan,speed,ovr | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexOutsideFanSpeedSp | aexOutsideFanSpeedSp | Air Exchanger Outside Fan Speed Setpoint | Air Exchanger Outside Fan Speed Setpoint |  | aexOutsideFanSpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | aex,outside,air,fan,speed,effective,sp | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexOutsideFanStatus | aexOutsideFanStatus | Air Exchanger Outside Fan Status | Air Exchanger Outside Fan Status |  | aexOutsideFanStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | aex,outside,air,fan,status,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexOutsideFilterAlarm | aexOutsideFilterAlarm | Air Exchanger Outside Filter Alarm | Air Exchanger Outside Filter Alarm |  | aexOutsideFilterAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | aex,outside,air,filter,common,alarm | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexOutsideFilterAlarmReset | aexOutsideFilterAlarmReset | Air Exchanger Outside Filter Alarm Reset | Air Exchanger Outside Filter Alarm Reset |  | aexOutsideFilterAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | aex,outside,air,filter,reset,alarm | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexOutsideFilterPressureDelta | aexOutsideFilterPressureDelta | Air Exchanger Outside Filter Pressure Delta | Air Exchanger Outside Filter Pressure Delta |  | aexOutsideFilterPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | aex,outside,air,filter,pressure,delta,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released)
aexOutsideFilterRuntime | aexOutsideFilterRuntime | Air Exchanger Outside Filter Runtime | Air Exchanger Outside Filter Runtime |  | aexOutsideFilterRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,DHU,DOAS,ERU,HRU,RTU | 2.15 (Released),2.16 (Pre-Release)
aexOutsideFlow | aexOutsideFlow | Air Exchanger Outside Flow | Air Exchanger Outside Flow |  | aexOutsideFlow | Yes | Yes | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | aex,outside,air,flow,sensor | AFMS,AHU,CU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexOutsideHumidity | aexOutsideHumidity | Air Exchanger Outside Humidity | Air Exchanger Outside Humidity |  | aexOutsideHumidity | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | aex,outside,air,humidity,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexOutsideIsoDamper | aexOutsideIsoDamper | Air Exchanger Outside Isolation Damper Command | Air Exchanger Outside Isolation Damper Command |  | aexOutsideIsoDamper | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | aex,outside,iso,air,damper,status,cmd | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexOutsideIsoDamperFb | aexOutsideIsoDamperFb | Air Exchanger Outside Isolation Damper Feedback | Air Exchanger Outside Isolation Damper Feedback |  | aexOutsideIsoDamperFb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | aex,outside,iso,air,damper,status,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexOutsidePressure | aexOutsidePressure | Air Exchanger Outside Pressure | Air Exchanger Outside Pressure |  | aexOutsidePressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | aex,outside,air,static,pressure,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexOutsideTemp | aexOutsideTemp | Air Exchanger Outside Temperature | Air Exchanger Outside Temperature |  | aexOutsideTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | aex,outside,air,temp,sensor | AFMS,AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexOutsideVelPressure | aexOutsideVelPressure | Air Exchanger Outside Velocity Pressure | Air Exchanger Outside Velocity Pressure |  | aexOutsideVelPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | aex,outside,air,dynamic,pressure,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexPressureDeltaHiAlarm | aexPressureDeltaHiAlarm | Air Exchanger Pressure Delta High Alarm | Air Exchanger Pressure Delta High Alarm |  | aexPressureDeltaHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | aex,pressure,delta,high,alarm | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexReturnEnthalpy | aexReturnEnthalpy | Air Exchanger Return Enthalpy | Air Exchanger Return Enthalpy |  | aexReturnEnthalpy | Yes | Yes | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | aex,return,air,enthalpy,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexReturnFanAlarm | aexReturnFanAlarm | Air Exchanger Return Fan Alarm | Air Exchanger Return Fan Alarm |  | aexReturnFanAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | aex,return,air,fan,common,alarm | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexReturnFanAlarmReset | aexReturnFanAlarmReset | Air Exchanger Return Fan Alarm Reset | Air Exchanger Return Fan Alarm Reset |  | aexReturnFanAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | aex,air,fan,alarm,reset,return | AHU,DHU,DOAS,ERU,HRU,RTU | 2.15 (Released),2.16 (Pre-Release)
aexReturnFan | aexReturnFan | Air Exchanger Return Fan Command | Air Exchanger Return Fan Command |  | aexReturnFan | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | aex,return,air,fan,status,cmd | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexReturnFanCurrent | aexReturnFanCurrent | Air Exchanger Return Fan Current | Air Exchanger Return Fan Current |  | aexReturnFanCurrent | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | aex,return,air,fan,current,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexReturnFanEnteringPressure | aexReturnFanEnteringPressure | Air Exchanger Return Fan Entering Pressure | Air Exchanger Return Fan Entering Pressure |  | aexReturnFanEnteringPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | aex,return,air,fan,entering,pressure,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexReturnFanFault | aexReturnFanFault | Air Exchanger Return Fan Fault | Air Exchanger Return Fan Fault |  | aexReturnFanFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | aex,return,air,fan,fault | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexReturnFanLeavingPressure | aexReturnFanLeavingPressure | Air Exchanger Return Fan Leaving Pressure | Air Exchanger Return Fan Leaving Pressure |  | aexReturnFanLeavingPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | aex,return,air,fan,leaving,pressure,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexReturnFanMaintSwitch | aexReturnFanMaintSwitch | Air Exchanger Return Fan Maintenance Switch | Air Exchanger Return Fan Maintenance Switch |  | aexReturnFanMaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | maintenance,switch,cmd,aex,fan,air,return | AHU,DHU,DOAS,ERU,HRU,RTU | 2.15 (Released),2.16 (Pre-Release)
aexReturnFanOvr | aexReturnFanOvr | Air Exchanger Return Fan Override | Air Exchanger Return Fan Override |  | aexReturnFanOvr | No | No | No | Bool | On/Off | On/Off | [6 empty] | aex,return,air,fan,status,ovr | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexReturnFanPressureDelta | aexReturnFanPressureDelta | Air Exchanger Return Fan Pressure Delta | Air Exchanger Return Fan Pressure Delta |  | aexReturnFanPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | aex,return,air,fan,common,pressure,delta,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexReturnFanPressureHiAlarm | aexReturnFanPressureHiAlarm | Air Exchanger Return Fan Pressure High Alarm | Air Exchanger Return Fan Pressure High Alarm |  | aexReturnFanPressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | aex,return,air,fan,pressure,high,alarm | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexReturnFanPressureHiSp | aexReturnFanPressureHiSp | Air Exchanger Return Fan Pressure High Setpoint | Air Exchanger Return Fan Pressure High Setpoint |  | aexReturnFanPressureHiSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | aex,return,air,fan,pressure,high,sp | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexReturnFanPressureLoAlarm | aexReturnFanPressureLoAlarm | Air Exchanger Return Fan Pressure Low Alarm | Air Exchanger Return Fan Pressure Low Alarm |  | aexReturnFanPressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | aex,return,air,fan,pressure,low,alarm | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexReturnFanPressureLoSp | aexReturnFanPressureLoSp | Air Exchanger Return Fan Pressure Low Setpoint | Air Exchanger Return Fan Pressure Low Setpoint |  | aexReturnFanPressureLoSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | aex,return,air,fan,pressure,low,sp | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexReturnFanRuntime | aexReturnFanRuntime | Air Exchanger Return Fan Runtime | Air Exchanger Return Fan Runtime |  | aexReturnFanRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,DHU,DOAS,ERU,HRU,RTU | 2.15 (Released),2.16 (Pre-Release)
aexReturnFanSpeed | aexReturnFanSpeed | Air Exchanger Return Fan Speed | Air Exchanger Return Fan Speed |  | aexReturnFanSpeed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | aex,return,air,fan,speed,cmd | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexReturnFanSpeedFb | aexReturnFanSpeedFb | Air Exchanger Return Fan Speed Feedback | Air Exchanger Return Fan Speed Feedback |  | aexReturnFanSpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | aex,return,air,fan,speed,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexReturnFanSpeedMaxSp | aexReturnFanSpeedMaxSp | Air Exchanger Return Fan Speed Max Setpoint | Air Exchanger Return Fan Speed Max Setpoint |  | aexReturnFanSpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | aex,return,air,fan,speed,max,sp | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexReturnFanSpeedMinSp | aexReturnFanSpeedMinSp | Air Exchanger Return Fan Speed Min Setpoint | Air Exchanger Return Fan Speed Min Setpoint |  | aexReturnFanSpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | aex,return,air,fan,speed,min,sp | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexReturnFanSpeedOvr | aexReturnFanSpeedOvr | Air Exchanger Return Fan Speed Override | Air Exchanger Return Fan Speed Override |  | aexReturnFanSpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | aex,return,air,fan,speed,ovr | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexReturnFanSpeedSp | aexReturnFanSpeedSp | Air Exchanger Return Fan Speed Setpoint | Air Exchanger Return Fan Speed Setpoint |  | aexReturnFanSpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | aex,return,air,fan,speed,effective,sp | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexReturnFanStatus | aexReturnFanStatus | Air Exchanger Return Fan Status | Air Exchanger Return Fan Status |  | aexReturnFanStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | aex,return,air,fan,status,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexReturnFilterAlarm | aexReturnFilterAlarm | Air Exchanger Return Filter Alarm | Air Exchanger Return Filter Alarm |  | aexReturnFilterAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | aex,return,air,filter,common,alarm | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexReturnFilterAlarmReset | aexReturnFilterAlarmReset | Air Exchanger Return Filter Alarm Reset | Air Exchanger Return Filter Alarm Reset |  | aexReturnFilterAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | aex,return,air,filter,reset,alarm | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexReturnFilterPressureDelta | aexReturnFilterPressureDelta | Air Exchanger Return Filter Pressure Delta | Air Exchanger Return Filter Pressure Delta |  | aexReturnFilterPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | aex,return,air,filter,pressure,delta,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released)
aexReturnFilterRuntime | aexReturnFilterRuntime | Air Exchanger Return Filter Runtime | Air Exchanger Return Filter Runtime |  | aexReturnFilterRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,DHU,DOAS,ERU,HRU,RTU | 2.15 (Released),2.16 (Pre-Release)
aexReturnFlow | aexReturnFlow | Air Exchanger Return Flow | Air Exchanger Return Flow |  | aexReturnFlow | Yes | Yes | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | aex,return,air,flow,sensor | AFMS,AHU,CU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexReturnHumidity | aexReturnHumidity | Air Exchanger Return Humidity | Air Exchanger Return Humidity |  | aexReturnHumidity | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | aex,return,air,humidity,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexReturnIsoDamper | aexReturnIsoDamper | Air Exchanger Return Isolation Damper Command | Air Exchanger Return Isolation Damper Command |  | aexReturnIsoDamper | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | aex,return,iso,air,damper,status,cmd | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexReturnIsoDamperFb | aexReturnIsoDamperFb | Air Exchanger Return Isolation Damper Feedback | Air Exchanger Return Isolation Damper Feedback |  | aexReturnIsoDamperFb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | aex,return,iso,air,damper,status,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexReturnPressure | aexReturnPressure | Air Exchanger Return Pressure | Air Exchanger Return Pressure |  | aexReturnPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | aex,return,air,static,pressure,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexReturnTemp | aexReturnTemp | Air Exchanger Return Temperature | Air Exchanger Return Temperature |  | aexReturnTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | aex,return,air,temp,sensor | AFMS,AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
aexReturnVelPressure | aexReturnVelPressure | Air Exchanger Return Velocity Pressure | Air Exchanger Return Velocity Pressure |  | aexReturnVelPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | aex,return,air,dynamic,pressure,sensor | AHU,DHU,DOAS,ERU,HRU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
kFactor | kFactor | Airflow Calibration Factor | Airflow Calibration Factor |  | kFactor | No | No | No | Number |  |  |  |  | 2 | 2 |  |  | kFactor,sp | FPB,VAV | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
antiLegionellaEnable | antiLegionellaEnable | Anti- Legionella Enable Command | Anti- Legionella Enable Command |  | antiLegionellaEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | antiLegionella,enable,cmd | BLR,DHWS,HWS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
antiLegionellaAlarm | antiLegionellaAlarm | Anti-Legionella Alarm | Anti-Legionella Alarm |  | antiLegionellaAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | antiLegionella,alarm | BLR,DHWS,HWS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
antiLegionellaTempSp | antiLegionellaTempSp | Anti-Legionella Temperature Setpoint | Anti-Legionella Temperature Setpoint |  | antiLegionellaTempSp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | antiLegionella,temp,sp | BLR,DHWS,HWS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
energyApparent | energyApparent | Apparent Energy | Apparent Energy |  | energyApparent | Yes | Yes | Yes | Number |  |  | kilovolt_ampere_hour | kilovolt_ampere_hour | 0 | 0 |  | N | common,energy,apparent,sensor | AHU,ATS,ATU,BLR,BRK,CLR,CRAC,CRAH,CU,CUH,CWS,DH,DHU,DOAS,EC,EF,FCU,FPB,GEO,HP,HWS,MAU,PDU,PM,PRLY,PV,RPP,RTU,SMS,STS,TVS,TWR,UPS,UV,VAV,VPM,FCU,HP,HX | 2.15 (Released),2.16 (Pre-Release)
energyApparentPhaseA | energyApparentPhaseA | Apparent Energy (Phase A) | Apparent Energy (Phase A) |  | energyApparentPhaseA | Yes | Yes | Yes | Number |  |  | kilovolt_ampere_hour | kilovolt_ampere_hour | 0 | 0 |  | A | common,energy,apparent,sensor | AHU,ATS,ATU,BLR,BRK,CLR,CRAC,CRAH,CU,CUH,CWS,DH,DHU,DOAS,EC,EF,FCU,FPB,GEO,HP,HWS,MAU,PDU,PM,PRLY,PV,RPP,RTU,SMS,STS,TVS,TWR,UPS,UV,VAV,VPM,FCU,HP,HX | 2.15 (Released),2.16 (Pre-Release)
energyApparentPhaseB | energyApparentPhaseB | Apparent Energy (Phase B) | Apparent Energy (Phase B) |  | energyApparentPhaseB | Yes | Yes | Yes | Number |  |  | kilovolt_ampere_hour | kilovolt_ampere_hour | 0 | 0 |  | B | common,energy,apparent,sensor | AHU,ATS,ATU,BLR,BRK,CLR,CRAC,CRAH,CU,CUH,CWS,DH,DHU,DOAS,EC,EF,FCU,FPB,GEO,HP,HWS,MAU,PDU,PM,PRLY,PV,RPP,RTU,SMS,STS,TVS,TWR,UPS,UV,VAV,VPM,FCU,HP,HX | 2.15 (Released),2.16 (Pre-Release)
energyApparentPhaseC | energyApparentPhaseC | Apparent Energy (Phase C) | Apparent Energy (Phase C) |  | energyApparentPhaseC | Yes | Yes | Yes | Number |  |  | kilovolt_ampere_hour | kilovolt_ampere_hour | 0 | 0 |  | C | common,energy,apparent,sensor | AHU,ATS,ATU,BLR,BRK,CLR,CRAC,CRAH,CU,CUH,CWS,DH,DHU,DOAS,EC,EF,FCU,FPB,GEO,HP,HWS,MAU,PDU,PM,PRLY,PV,RPP,RTU,SMS,STS,TVS,TWR,UPS,UV,VAV,VPM,FCU,HP,HX | 2.15 (Released),2.16 (Pre-Release)
powerApparent | powerApparent | Apparent Power | Apparent Power |  | powerApparent | Yes | Yes | No | Number |  |  | kilovolt_ampere | kilovolt_ampere | 1 | 1 |  | N | common,power,apparent,sensor | ATS,BRK,CU,INV,PDU,PFC,PM,PRLY,PV,RECT,RPP,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
powerApparentPhaseA | powerApparentPhaseA | Apparent Power (Phase A) | Apparent Power (Phase A) |  | powerApparentPhaseA | Yes | Yes | No | Number |  |  | kilovolt_ampere | kilovolt_ampere | 1 | 1 |  | A | common,power,apparent,sensor | ATS,BRK,CU,INV,PDU,PFC,PM,PRLY,PV,RECT,RPP,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
powerApparentPhaseB | powerApparentPhaseB | Apparent Power (Phase B) | Apparent Power (Phase B) |  | powerApparentPhaseB | Yes | Yes | No | Number |  |  | kilovolt_ampere | kilovolt_ampere | 1 | 1 |  | B | common,power,apparent,sensor | ATS,BRK,CU,INV,PDU,PFC,PM,PRLY,PV,RECT,RPP,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
powerApparentPhaseC | powerApparentPhaseC | Apparent Power (Phase C) | Apparent Power (Phase C) |  | powerApparentPhaseC | Yes | Yes | No | Number |  |  | kilovolt_ampere | kilovolt_ampere | 1 | 1 |  | C | common,power,apparent,sensor | ATS,BRK,CU,INV,PDU,PFC,PM,PRLY,PV,RECT,RPP,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
powerApparentMax | powerApparentMax | Apparent Power Maximum | Apparent Power Maximum |  | powerApparentMax | Yes | Yes | No | Number |  |  | kilovolt_ampere | kilovolt_ampere | 1 | 1 |  | N | common,power,apparent,max,calc | PRLY | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
powerApparentMaxDateTime | powerApparentMaxDateTime | Apparent Power Maximum Date & Time | Apparent Power Maximum Date & Time |  | powerApparentMaxDateTime | Yes | No | No | Str | [7 empty] | N | common,power,apparent,dateTime,calc | PRLY | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
areaServed | areaServed | Area Served | Area Served |  | areaServed | No | No | No | Str | [8 empty] | blacklist | AC,AFMS,AHU,ATS,ATU,BATT,BLND,BLR,BRK,BTU,CF,CLR,CM,CMP,CRAC,CRAH,CU,CUH,CWS,DAC,DCU,DCWS,DH,DHU,DHWS,DOAS,DOOR,DRY,EC,EF,ELV,ENC,ERU,FC,FCU,FDS,FEXT,FP,FPB,FSD,FSEP,FSS,GBL,GDS,GEN,GEO,GINT,GM,HDS,HP,HRU,HT,HUM,HVHS,HVLS,HWS,INV,LDS,LS,LTGE,LTGI,MAU,MMS,MSC,NC,OF,PDU,PFC,PH,PINT,PIU,PM,PMP,PRLY,PV,PWS,REC,RECT,RF,RFG,ROS,RP,RPC,RPF,RPP,RRS,RTU,SCRB,SEC,SKYL,SM,SMEX,SMP,SMS,STS,SUP,TF,TNK,TRN,TVS,TWR,UH,UPS,UV,VAV,VBTU,VFD,VGM,VPM,VRF,VWM,WH,WM,WNDW,WS,WSS,WTHR,WTS,XFMR,ZD,ZN,FCU,HP,GATE,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
assistanceButton | assistanceButton | Assistance Button (Emergency) | Assistance Button (Emergency) |  | assistanceButton | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | assistance,button,sensor | MSC,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
auxHeatingEnable | auxHeatingEnable | Auxiliary Heating Enable Command | Auxiliary Heating Enable Command |  | auxHeatingEnable | No | No | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | auxHeat,enable,cmd | AHU,CRAC,CRAH,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
auxHeatingEnableSp | auxHeatingEnableSp | Auxiliary Heating Enable Setpoint | Auxiliary Heating Enable Setpoint |  | auxHeatingEnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | auxHeat,enable,sp | AHU,CRAC,CRAH,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
auxHeatingStageAlarm | auxHeatingStageXXXXAlarm | Auxiliary Heating Stage Alarm | Auxiliary Heating Stage XX Alarm |  | auxHeatingStage(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal |  |  |  |  | XX |  | auxHeat,alarm | AHU,CRAC,CRAH,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
auxHeatingStage | auxHeatingStageXXXX | Auxiliary Heating Stage Command | Auxiliary Heating Stage XX Command |  | auxHeatingStage(\d{0,4}) | Yes | Yes | No | Bool | On/Off | On/Off |  |  |  |  | XX |  | auxHeat,status,cmd | AHU,CRAC,CRAH,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
auxHeatingStageMod | auxHeatingStageXXXXMod | Auxiliary Heating Stage Modulation | Auxiliary Heating Stage XX Modulation |  | auxHeatingStage(\d{0,4})Mod | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 | XX |  | auxHeat,modulation,cmd | AHU,CRAC,CRAH,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
auxHeatingStageOvr | auxHeatingStageXXXXOvr | Auxiliary Heating Stage Override | Auxiliary Heating Stage XX Override |  | auxHeatingStage(\d{0,4})Ovr | Yes | Yes | No | Bool | On/Off | On/Off |  |  |  |  | XX |  | auxHeat,status,ovr | AHU,CRAC,CRAH,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
auxHeatingStageStatus | auxHeatingStageXXXXStatus | Auxiliary Heating Stage Status | Auxiliary Heating Stage XX Status |  | auxHeatingStage(\d{0,4})Status | Yes | Yes | No | Bool | On/Off | On/Off |  |  |  |  | XX |  | auxHeat,status,sensor | AHU,CRAC,CRAH,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
balanceMode | balanceMode | Balance Mode | Balance Mode |  | balanceMode | No | No | No | Str |  | Open/Closed/Maximum Flow Position/Minimum Flow Position | [6 empty] | balance,mode,sp | FPB,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
batteryAlarm | batteryAlarm | Battery Alarm | Battery Alarm |  | batteryAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | battery,common,alarm,general | BATT,GEN,MSC,UPS | 2.15 (Released)
batteryChargerAlarm | batteryChargerAlarm | Battery Charger Alarm | Battery Charger Alarm |  | batteryChargerAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | battery,charger,alarm | BATT,GEN,MSC,UPS | 2.15 (Released)
batteryChargerFault | batteryChargerFault | Battery Charger Fault | Battery Charger Fault |  | batteryChargerFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | battery,charger,fault | BATT,GEN,MSC,UPS | 2.15 (Released)
batteryCurrent | batteryCurrent | Battery Current | Battery Current |  | batteryCurrent | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | battery,current,sensor | BATT,GEN,MSC,UPS | 2.15 (Released)
batteryFault | batteryFault | Battery Fault | Battery Fault |  | batteryFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | battery,common,fault | BATT,GEN,MSC,UPS | 2.15 (Released)
batteryLevel | batteryLevel | Battery Level | Battery Level |  | batteryLevel | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | battery,level,sensor | BATT,GEN,MSC,UPS | 2.12,2.13,2.14,2.15 (Released)
batteryLevelLoAlarm | batteryLevelLoAlarm | Battery Level Low Alarm | Battery Level Low Alarm |  | batteryLevelLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | battery,level,low,alarm | BATT,GEN,MSC,UPS | 2.12,2.13,2.14,2.15 (Released)
batteryMode | batteryMode | Battery Mode | Battery Mode |  | batteryMode | Yes | No | No | Str |  | Charging/Discharging/Floating/Resting/Unknown/Disconnected/UnderTest/CheckBattery | [6 empty] | battery,mode,sp | BATT,GEN,MSC,UPS | 2.12,2.13,2.14,2.15 (Released)
batteryReplaceAlarm | batteryReplaceAlarm | Battery Replacement Alarm | Battery Replacement Alarm |  | batteryReplaceAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | battery,replacement,alarm | BATT,GEN,MSC,UPS | 2.12,2.13,2.14,2.15 (Released)
batteryResistance | batteryResistance | Battery Resistance | Battery Resistance |  | batteryResistance | Yes | Yes | No | Number |  |  | ohm | ohm | 1 | 1 |  |  | battery,resistance,sensor | BATT,GEN,MSC,UPS | 2.12,2.13,2.14,2.15 (Released)
batteryResistanceHiAlarm | batteryResistanceHiAlarm | Battery Resistance High Alarm | Battery Resistance High Alarm |  | batteryResistanceHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | battery,resistance,high,alarm | BATT,GEN,MSC,UPS | 2.15 (Released)
batteryStatus | batteryStatus | Battery Status | Battery Status |  | batteryStatus | Yes | Yes | No | Bool | Charged/Uncharged | Charged/Uncharged | [6 empty] | battery,status,sensor | BATT,GEN,MSC,UPS | 2.12,2.13,2.14,2.15 (Released)
batteryTemp | batteryTemp | Battery Temperature | Battery Temperature |  | batteryTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | battery,temp,sensor | BATT,GEN,MSC,UPS | 2.12,2.13,2.14,2.15 (Released)
batteryTempAlarm | batteryTempAlarm | Battery Temperature Alarm | Battery Temperature Alarm |  | batteryTempAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | battery,temp,common,alarm | BATT,GEN,MSC,UPS | 2.15 (Released)
batteryTempHiAlarm | batteryTempHiAlarm | Battery Temperature High Alarm | Battery Temperature High Alarm |  | batteryTempHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | battery,temp,high,alarm | BATT,GEN,MSC,UPS | 2.12,2.13,2.14,2.15 (Released)
batteryTempHiSp | batteryTempHiSp | Battery Temperature High Setpoint | Battery Temperature High Setpoint |  | batteryTempHiSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | battery,temp,high,sp | BATT,GEN,MSC,UPS | 2.15 (Released)
batteryTempLoAlarm | batteryTempLoAlarm | Battery Temperature Low Alarm | Battery Temperature Low Alarm |  | batteryTempLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | battery,temp,low,alarm | BATT,GEN,MSC,UPS | 2.15 (Released)
batteryTempLoSp | batteryTempLoSp | Battery Temperature Low Setpoint | Battery Temperature Low Setpoint |  | batteryTempLoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | battery,temp,low,sp | BATT,GEN,MSC,UPS | 2.15 (Released)
batteryTime | batteryTime | Battery Time | Battery Time |  | batteryTime | Yes | No | No | Number |  |  | minute | minute | 0 | 0 |  |  | battery,time,sensor | BATT,GEN,MSC,UPS | 2.15 (Released)
batteryVoltage | batteryVoltage | Battery Voltage | Battery Voltage |  | batteryVoltage | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  | N | battery,volt,sensor | BATT,GEN,MSC,UPS | 2.12,2.13,2.14,2.15 (Released)
batteryVoltageAvg | batteryVoltageAvg | Battery Voltage (Average) | Battery Voltage (Average) |  | batteryVoltageAvg | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  |  | battery,volt,avg,calc | BATT,GEN,MSC,UPS | 2.12,2.13,2.14,2.15 (Released)
batteryVoltageHiAlarm | batteryVoltageHiAlarm | Battery Voltage High Alarm | Battery Voltage High Alarm |  | batteryVoltageHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | battery,volt,high,alarm | BATT,GEN,MSC,UPS | 2.12,2.13,2.14,2.15 (Released)
batteryVoltageHiSp | batteryVoltageHiSp | Battery Voltage High Setpoint | Battery Voltage High Setpoint |  | batteryVoltageHiSp | No | No | No | Number |  |  | volt | volt | 1 | 1 |  |  | battery,volt,high,sp | BATT,GEN,MSC,UPS | 2.15 (Released)
batteryVoltageLoAlarm | batteryVoltageLoAlarm | Battery Voltage Low Alarm | Battery Voltage Low Alarm |  | batteryVoltageLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | battery,volt,low,alarm | BATT,GEN,MSC,UPS | 2.12,2.13,2.14,2.15 (Released)
blind | blind | Blind Command | Blind Command |  | blind | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | blind,status,cmd | BLND | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
blindFb | blindFb | Blind Feedback | Blind Feedback |  | blindFb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | blind,status,sensor | BLND | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
blowDownValve | blowDownValve | Blow Down Valve Command | Blow Down Valve Command |  | blowDownValve | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | blowDown,valve,position,cmd | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
blowDownValveFb | blowDownValveFb | Blow Down Valve Feedback | Blow Down Valve Feedback |  | blowDownValveFb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | blowDown,valve,position,sensor | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
boilerLoad | boilerLoad | Boiler Actual Energy Production | Boiler Actual Energy Production |  | boilerLoad | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | boiler,load,sensor | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
boilerAlarm | boilerAlarm | Boiler Alarm | Boiler Alarm |  | boilerAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | boiler,common,alarm | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
boilerAlarmReset | boilerAlarmReset | Boiler Alarm Reset | Boiler Alarm Reset |  | boilerAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | boiler,reset,alarm | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
boiler | boiler | Boiler Command | Boiler Command |  | boiler | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | boiler,status,common,cmd | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
boilerDelayOnSp | boilerDelayOnSp | Boiler Delay-On Setpoint | Boiler Delay-On Setpoint |  | boilerDelayOnSp | No | No | No | Number |  |  | minute | minute | 0 | 0 |  |  | boiler,delay,on,sp | HWS | 2.15 (Released),2.16 (Pre-Release)
boilerEfficiency | boilerEfficiency | Boiler Efficiency of Combustion | Boiler Efficiency of Combustion |  | boilerEfficiency | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | boiler,efficiency,sensor | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
boilerEnable | boilerEnable | Boiler Enable Command | Boiler Enable Command |  | boilerEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | boiler,enable,cmd | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
boilerFault | boilerFault | Boiler Fault | Boiler Fault |  | boilerFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | boiler,fault | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
boilerFlameFailAlarm | boilerFlameFailAlarm | Boiler Flame Alarm | Boiler Flame Alarm |  | boilerFlameFailAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | boiler,flame,alarm | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
boilerHandMode | boilerHandMode | Boiler Hand/Auto Mode | Boiler Hand/Auto Mode |  | boilerHandMode | Yes | Yes | No | Bool | Hand/Auto | Hand/Auto | [6 empty] | boiler,handMode,sensor | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
boilerLagEnable | boilerLagEnable | Boiler Lag Enable | Boiler Lag Enable |  | boilerLagEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | boiler,lag,enable,cmd | HWS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
boilerLagReq | boilerLagReq | Boiler Lag Request | Boiler Lag Request |  | boilerLagReq | No | No | No | Bool | Request/No Request | Request/No Request | [6 empty] | boiler,lag,request,cmd | HWS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
boilerLead | boilerLead | Boiler Lead | Boiler Lead |  | boilerLead | Yes | Yes | No | Bool | Lead 1/Lead 2 | Lead 1/Lead 2 | [6 empty] | boiler,lead,sp | HWS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
boilerLeadXor | boilerLeadXor | Boiler Lead Change Over | Boiler Lead Change Over |  | boilerLeadXor | No | No | No | Bool | On/Off | On/Off | [6 empty] | boiler,lead,changeOver,cmd | HWS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
boilerLeadXorRuntimeSp | boilerLeadXorRuntimeSp | Boiler Lead Change Over Runtime Setpoint | Boiler Lead Change Over Runtime Setpoint |  | boilerLeadXorRuntimeSp | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | HWS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
boilerMaintSwitch | boilerMaintSwitch | Boiler Maintenance Switch | Boiler Maintenance Switch |  | boilerMaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | boiler,maintenance,switch,cmd | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
boilerMinOffSp | boilerMinOffSp | Boiler Minimum Off Setpoint | Boiler Minimum Off Setpoint |  | boilerMinOffSp | No | No | No | Number |  |  | second | second | 0 | 0 |  |  | boiler,min,off,sp | HWS | 2.15 (Released),2.16 (Pre-Release)
boilerMinOnSp | boilerMinOnSp | Boiler Minimum On Setpoint | Boiler Minimum On Setpoint |  | boilerMinOnSp | No | No | No | Number |  |  | second | second | 0 | 0 |  |  | boiler,min,on,sp | HWS | 2.15 (Released),2.16 (Pre-Release)
boilerOvr | boilerOvr | Boiler Override | Boiler Override |  | boilerOvr | No | No | No | Bool | On/Off | On/Off | [6 empty] | boiler,status,ovr | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
boilerDemand | boilerDemand | Boiler Percent of Max Output | Boiler Percent of Max Output |  | boilerDemand | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | boiler,demand,sensor | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
boilerReq | boilerReq | Boiler Request | Boiler Request |  | boilerReq | No | No | No | Bool | Request/No Request | Request/No Request | [6 empty] | boiler,common,request,cmd | HWS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
boilerRuntime | boilerRuntime | Boiler Runtime | Boiler Runtime |  | boilerRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | BLR | 2.15 (Released),2.16 (Pre-Release)
boilerStage | boilerStageXXXX | Boiler Stage | Boiler Stage XX |  | boilerStage(\d{0,4}) | Yes | Yes | No | Bool | On/Off | On/Off |  |  |  |  | XX |  | boiler,status,cmd | HWS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
boilerStageAlarm | boilerStageXXXXAlarm | Boiler Stage Alarm | Boiler Stage XX Alarm |  | boilerStage(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal |  |  |  |  | XX |  | boiler,alarm | HWS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
boilerStageOffSp | boilerStageXXXXOffSp | Boiler Stage Off Setpoint | Boiler Stage XX Off Setpoint |  | boilerStage(\d{0,4})OffSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 | XX |  | boiler,off,sp | HWS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
boilerStageOnSp | boilerStageXXXXOnSp | Boiler Stage On Setpoint | Boiler Stage XX On Setpoint |  | boilerStage(\d{0,4})OnSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 | XX |  | boiler,on,sp | HWS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
boilerStageUpSp | boilerStageUpSp | Boiler Stage Up Setpoint | Boiler Stage Up Setpoint |  | boilerStageUpSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | boiler,stageUp,effective,sp | HWS | 2.15 (Released),2.16 (Pre-Release)
boilerStarts | boilerStarts | Boiler Starts | Boiler Starts |  | boilerStarts | Yes | No | No | Number |  |  |  |  | 0 | 0 |  |  | boiler,starts,sensor | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
boilerStatus | boilerStatus | Boiler Status | Boiler Status |  | boilerStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | boiler,status,common,sensor | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
boosterPumpAlarm | boosterPumpXXXXAlarm | Booster Pump Alarm | Booster Pump XX Alarm |  | boosterPump(\w{0,4}(?=[A-Z]¦$))Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | booster,water,pump,common,alarm | DCWS,DHWS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
boosterPumpAlarmReset | boosterPumpXXXXAlarmReset | Booster Pump Alarm Reset | Booster Pump XX Alarm Reset |  | boosterPump(\w{0,4}(?=[A-Z]¦$))AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | booster,water,pump,reset,alarm | DCWS,DHWS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
boosterPump | boosterPumpXXXX | Booster Pump Command | Booster Pump XX Command |  | boosterPump(\w{0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | booster,water,pump,status,cmd | DCWS,DHWS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
boosterPumpFault | boosterPumpXXXXFault | Booster Pump Fault | Booster Pump XX Fault |  | boosterPump(\w{0,4}(?=[A-Z]¦$))Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | booster,water,pump,fault | DCWS,DHWS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
boosterPumpHandMode | boosterPumpXXXXHandMode | Booster Pump Hand/Auto Mode | Booster Pump XX Hand/Auto Mode |  | boosterPump(\w{0,4}(?=[A-Z]¦$))HandMode | Yes | Yes | No | Bool | Hand/Auto | Hand/Auto | [6 empty] | booster,water,pump,handMode,sensor | DCWS,DHWS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
boosterPumpStatus | boosterPumpXXXXStatus | Booster Pump Status | Booster Pump XX Status |  | boosterPump(\w{0,4}(?=[A-Z]¦$))Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | booster,water,pump,status,sensor | DCWS,DHWS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
breakStart | breakStart | Break Start | Break Start |  | breakStart | Yes | No | No | Bool | On/Off | On/Off | [6 empty] | blacklist | MSC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
breakStop | breakStop | Break Stop | Break Stop |  | breakStop | Yes | No | No | Bool | On/Off | On/Off | [6 empty] | blacklist | MSC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
breakerAlarm | breakerXXXXAlarm | Breaker Alarm | Breaker XX Alarm |  | breaker(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | breaker,common,alarm | BRK,LTGE,LTGI,MSC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
breaker | breakerXXXX | Breaker Command | Breaker XX Command |  | breaker(\d{0,4}) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | breaker,status,cmd | BRK,LTGE,LTGI,MSC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
breakerDimLevel | breakerXXXXDimLevel | Breaker Dimming Level Command | Breaker XX Dimming Level Command |  | breaker(\d{0,4})DimLevel | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | breaker,dimming,cmd | BRK,LTGE,LTGI,MSC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
breakerDimLevelFb | breakerXXXXDimLevelFb | Breaker Dimming Level Feedback | Breaker XX Dimming Level Feedback |  | breaker(\d{0,4})DimLevelFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | breaker,dimming,sensor | BRK,LTGE,LTGI,MSC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
breakerDimLevelOvr | breakerXXXXDimLevelOvr | Breaker Dimming Level Override | Breaker XX Dimming Level Override |  | breaker(\d{0,4})DimLevelOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | breaker,dimming,ovr | BRK,LTGE,LTGI,MSC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
breakerDimLevelSp | breakerXXXXDimLevelSp | Breaker Dimming Level Setpoint | Breaker XX Dimming Level Setpoint |  | breaker(\d{0,4})DimLevelSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | breaker,dimming,sp | BRK,LTGE,LTGI,MSC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
breakerHandMode | breakerXXXXHandMode | Breaker Hand/Auto Mode | Breaker XX Hand/Auto Mode |  | breaker(\d{0,4})HandMode | Yes | Yes | No | Bool | Hand/Auto | Hand/Auto | [6 empty] | breaker,handMode,sensor | BRK,LTGE,LTGI,MSC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
breakerOvr | breakerXXXXOvr | Breaker Override | Breaker XX Override |  | breaker(\d{0,4})Ovr | No | No | No | Bool | On/Off | On/Off | [6 empty] | breaker,status,ovr | BRK,LTGE,LTGI,MSC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
breakerStatus | breakerXXXXStatus | Breaker Status | Breaker XX Status |  | breaker(\d{0,4})Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | breaker,status,sensor | BRK,LTGE,LTGI,MSC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
buildingPowerStatus | buildingPowerStatus | Building Power Status | Building Power Status |  | buildingPowerStatus | Yes | Yes | No | Str | [8 empty] | building,power,status | GBL,MSC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
buildingPressure | buildingPressureXXXX | Building Pressure | Building Pressure XX |  | buildingPressure(\d{0,4}) | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 3 | 1 |  |  | building,air,pressure,sensor | AHU,ATU,DHU,DOAS,EF,FCU,GBL,HP,MAU,RTU,SMEX,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
buildingPressureAvg | buildingPressureAvg | Building Pressure (Average) | Building Pressure (Average) |  | buildingPressureAvg | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 3 | 1 |  |  | building,air,pressure,avg,calc | AHU,ATU,DHU,DOAS,EF,FCU,GBL,HP,MAU,RTU,SMEX,ZN,FCU,HP | 2.15 (Released),2.16 (Pre-Release)
buildingPressureDb | buildingPressureXXXXDb | Building Pressure Deadband | Building Pressure XX Deadband |  | buildingPressure(\d{0,4})Db | No | No | No | Number |  |  | inches_of_water | pascal | 3 | 1 |  |  | building,air,pressure,deadband,sp | AHU,ATU,DHU,DOAS,EF,FCU,GBL,HP,MAU,RTU,SMEX,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
buildingPressureHiAlarm | buildingPressureXXXXHiAlarm | Building Pressure High Alarm | Building Pressure XX High Alarm |  | buildingPressure(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | building,air,pressure,high,alarm | AHU,ATU,DHU,DOAS,EF,FCU,GBL,HP,MAU,RTU,SMEX,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
buildingPressureHiSp | buildingPressureXXXXHiSp | Building Pressure High Setpoint | Building Pressure XX High Setpoint |  | buildingPressure(\d{0,4})HiSp | No | No | No | Number |  |  | inches_of_water | pascal | 3 | 1 |  |  | building,air,pressure,high,sp | AHU,ATU,DHU,DOAS,EF,FCU,GBL,HP,MAU,RTU,SMEX,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
buildingPressureLoAlarm | buildingPressureXXXXLoAlarm | Building Pressure Low Alarm | Building Pressure XX Low Alarm |  | buildingPressure(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | building,air,pressure,low,alarm | AHU,ATU,DHU,DOAS,EF,FCU,GBL,HP,MAU,RTU,SMEX,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
buildingPressureLoSp | buildingPressureXXXXLoSp | Building Pressure Low Setpoint | Building Pressure XX Low Setpoint |  | buildingPressure(\d{0,4})LoSp | No | No | No | Number |  |  | inches_of_water | pascal | 3 | 1 |  |  | building,air,pressure,low,sp | AHU,ATU,DHU,DOAS,EF,FCU,GBL,HP,MAU,RTU,SMEX,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
buildingPressureMaxSp | buildingPressureXXXXMaxSp | Building Pressure Max Setpoint | Building Pressure XX Max Setpoint |  | buildingPressure(\d{0,4})MaxSp | No | No | No | Number |  |  | inches_of_water | pascal | 3 | 1 |  |  | building,air,pressure,max,sp | AHU,ATU,DHU,DOAS,EF,FCU,GBL,HP,MAU,RTU,SMEX,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
buildingPressureMinSp | buildingPressureXXXXMinSp | Building Pressure Min Setpoint | Building Pressure XX Min Setpoint |  | buildingPressure(\d{0,4})MinSp | No | No | No | Number |  |  | inches_of_water | pascal | 3 | 1 |  |  | building,air,pressure,min,sp | AHU,ATU,DHU,DOAS,EF,FCU,GBL,HP,MAU,RTU,SMEX,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
buildingPressureSp | buildingPressureXXXXSp | Building Pressure Setpoint | Building Pressure XX Setpoint |  | buildingPressure(\d{0,4})Sp | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 3 | 1 |  |  | building,air,pressure,effective,sp | AHU,ATU,DHU,DOAS,EF,FCU,GBL,HP,MAU,RTU,SMEX,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
bypassButton | bypassButtonXXXX | Bypass Button Command | Bypass Button XX Command |  | bypassButton(\w{0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | bypass,button,cmd | AHU,CRAC,CRAH,DHU,DOAS,LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
bypassDamper | bypassDamperXXXX | Bypass Damper Command | Bypass Damper XX Command |  | bypassDamper(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | bypass,damper,air,position,cmd | AHU,CRAC,CRAH,DHU,DOAS,MAU,RTU,UV | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
bypassDamperFb | bypassDamperXXXXFb | Bypass Damper Feedback | Bypass Damper XX Feedback |  | bypassDamper(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | bypass,damper,air,position,sensor | AHU,CRAC,CRAH,DHU,DOAS,MAU,RTU,UV | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
bypassDamperOvr | bypassDamperXXXXOvr | Bypass Damper Override | Bypass Damper XX Override |  | bypassDamper(\d{0,4})Ovr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | bypass,damper,air,position,ovr | AHU,CRAC,CRAH,DHU,DOAS,MAU,RTU,UV | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
bypassMode | bypassMode | Bypass Mode | Bypass Mode |  | bypassMode | Yes | No | No | Bool | On/Off | On/Off | [6 empty] | bypass,mode,common,sp | CRAC,CRAH,DHU,DOAS,LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
bypassModeTime | bypassModeTime | Bypass Mode Time Remaining | Bypass Mode Time Remaining |  | bypassModeTime | Yes | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | bypass,mode,time,sensor | CRAC,CRAH,DHU,DOAS,LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
bypassModeTimeSp | bypassModeTimeSp | Bypass Mode Time Remaining Setpoint | Bypass Mode Time Remaining Setpoint |  | bypassModeTimeSp | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | bypass,mode,time,sp | CRAC,CRAH,DHU,DOAS,LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
bypassSwitch | bypassSwitchXXXX | Bypass Switch Command | Bypass Switch XX Command |  | bypassSwitch(\w{0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | common,bypass,switch,cmd | CRAC,CRAH,DHU,DOAS,LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
bypassValve | bypassValveXXXX | Bypass Valve Command | Bypass Valve XX Command |  | bypassValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | common,water,bypass,valve,position,cmd | BLR,CLR,CWS,HWS,WS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
bypassValveFb | bypassValveXXXXFb | Bypass Valve Feedback | Bypass Valve XX Feedback |  | bypassValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | common,water,bypass,valve,position,sensor | BLR,CLR,CWS,HWS,WS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
bypassValveOvr | bypassValveXXXXOvr | Bypass Valve Override | Bypass Valve XX Override |  | bypassValve(\d{0,4})Ovr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | common,water,bypass,valve,position,ovr | BLR,CLR,CWS,HWS,WS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
powerCapacitive | powerCapacitive | Capacitive Power (Average) | Capacitive Power (Average) |  | powerCapacitive | Yes | Yes | No | Number |  |  | kilovolt_ampere_reactive | kilovolt_ampere_reactive | 1 | 1 |  | N | common,power,capacitive,sensor | ATS,BRK,CU,INV,PDU,PFC,PM,PRLY,PV,RECT,RPP,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
powerCapacitivePhaseA | powerCapacitivePhaseA | Capacitive Power (Phase A) | Capacitive Power (Phase A) |  | powerCapacitivePhaseA | Yes | Yes | No | Number |  |  | kilovolt_ampere_reactive | kilovolt_ampere_reactive | 1 | 1 |  | A | common,power,capacitive,sensor | ATS,BRK,CU,INV,PDU,PFC,PM,PRLY,PV,RECT,RPP,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
powerCapacitivePhaseB | powerCapacitivePhaseB | Capacitive Power (Phase B) | Capacitive Power (Phase B) |  | powerCapacitivePhaseB | Yes | Yes | No | Number |  |  | kilovolt_ampere_reactive | kilovolt_ampere_reactive | 1 | 1 |  | B | common,power,capacitive,sensor | ATS,BRK,CU,INV,PDU,PFC,PM,PRLY,PV,RECT,RPP,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
powerCapacitivePhaseC | powerCapacitivePhaseC | Capacitive Power (Phase C) | Capacitive Power (Phase C) |  | powerCapacitivePhaseC | Yes | Yes | No | Number |  |  | kilovolt_ampere_reactive | kilovolt_ampere_reactive | 1 | 1 |  | C | common,power,capacitive,sensor | ATS,BRK,CU,INV,PDU,PFC,PM,PRLY,PV,RECT,RPP,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
capacitorOverloadAlarm | capacitorOverloadAlarm | Capacitor Overload Alarm | Capacitor Overload Alarm |  | capacitorOverloadAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | capacitor,overload,alarm | PFC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
ceilingFanAlarm | ceilingFanAlarm | Ceiling Fan Alarm | Ceiling Fan Alarm |  | ceilingFanAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | ceiling,air,fan,common,alarm | CF | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
ceilingFan | ceilingFan | Ceiling Fan Command | Ceiling Fan Command |  | ceilingFan | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | ceiling,air,fan,status,cmd | CF | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
ceilingFanStatus | ceilingFanStatus | Ceiling Fan Status | Ceiling Fan Status |  | ceilingFanStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | ceiling,air,fan,status,sensor | CF | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
chillerLoad | chillerLoad | Chiller Actual Energy Production | Chiller Actual Energy Production |  | chillerLoad | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | chiller,load,sensor | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
chillerAlarm | chillerAlarm | Chiller Alarm | Chiller Alarm |  | chillerAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | chiller,common,alarm | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
chillerCapacityMaxSp | chillerCapacityMaxSp | Chiller Capacity Max Setpoint | Chiller Capacity Max Setpoint |  | chillerCapacityMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | chiller,demand,max,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
chillerCapacityMaxSpOvr | chillerCapacityMaxSpOvr | Chiller Capacity Max Setpoint Override | Chiller Capacity Max Setpoint Override |  | chillerCapacityMaxSpOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | chiller,demand,max,spOvr | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
chiller | chiller | Chiller Command | Chiller Command |  | chiller | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | chiller,status,common,cmd | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
chillerEfficiency | chillerEfficiency | Chiller Efficiency of Refrigeration | Chiller Efficiency of Refrigeration |  | chillerEfficiency | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | chiller,efficiency,sensor | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
chillerEnable | chillerEnable | Chiller Enable Command | Chiller Enable Command |  | chillerEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | chiller,enable,cmd | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
chillerEnableOvr | chillerEnableOvr | Chiller Enable Override | Chiller Enable Override |  | chillerEnableOvr | No | No | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | chiller,enable,ovr | CLR | 2.14,2.15 (Released),2.16 (Pre-Release)
chillerEnableSp | chillerEnableSp | Chiller Enable Setpoint | Chiller Enable Setpoint |  | chillerEnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | chiller,enable,sp | CLR | 2.14,2.15 (Released),2.16 (Pre-Release)
chillerFault | chillerFault | Chiller Fault | Chiller Fault |  | chillerFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | chiller,fault | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
chillerHandMode | chillerHandMode | Chiller Hand/Auto Mode | Chiller Hand/Auto Mode |  | chillerHandMode | Yes | Yes | No | Bool | Hand/Auto | Hand/Auto | [6 empty] | chiller,handMode,sensor | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
chillerLagEnable | chillerLagEnable | Chiller Lag Enable | Chiller Lag Enable |  | chillerLagEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | chiller,lag,enable,cmd | CWS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
chillerLagReq | chillerLagReq | Chiller Lag Request | Chiller Lag Request |  | chillerLagReq | No | No | No | Bool | Request/No Request | Request/No Request | [6 empty] | chiller,lag,request,cmd | CWS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
chillerLead | chillerLead | Chiller Lead | Chiller Lead |  | chillerLead | Yes | Yes | No | Bool | Lead 1/Lead 2 | Lead 1/Lead 2 | [6 empty] | chiller,lead,sp | CWS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
chillerLeadXor | chillerLeadXor | Chiller Lead Change Over | Chiller Lead Change Over |  | chillerLeadXor | No | No | No | Bool | On/Off | On/Off | [6 empty] | chiller,lead,changeOver,common,cmd | CWS,WS | 2.15 (Released),2.16 (Pre-Release)
chillerLeadXorDay | chillerLeadXorDay | Chiller Lead Change Over Day | Chiller Lead Change Over Day |  | chillerLeadXorDay | No | No | No | Number |  | Sun,Mon,Tue,Wed,Thur,Fri,Sat | day | day | 0 | 0 |  |  | chiller,lead,changeOver,day,cmd | CWS,WS | 2.15 (Released),2.16 (Pre-Release)
chillerLeadXorHour | chillerLeadXorHour | Chiller Lead Change Over Hour | Chiller Lead Change Over Hour |  | chillerLeadXorHour | No | No | No | Number |  |  | hour | hour | 0 | 0 |  |  | chiller,lead,changeOver,hour,cmd | CWS,WS | 2.15 (Released),2.16 (Pre-Release)
chillerLeadXorRuntimeSp | chillerLeadXorRuntimeSp | Chiller Lead Change Over Runtime Setpoint | Chiller Lead Change Over Runtime Setpoint |  | chillerLeadXorRuntimeSp | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | CWS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
chillerMaint | chillerMaint | Chiller Maintenance | Chiller Maintenance |  | chillerMaint | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | chiller,maintenance,cmd | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
chillerOvr | chillerOvr | Chiller Override | Chiller Override |  | chillerOvr | No | No | No | Bool | On/Off | On/Off | [6 empty] | chiller,status,ovr | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
chillerDemand | chillerDemand | Chiller Percent of Max Output | Chiller Percent of Max Output |  | chillerDemand | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | chiller,demand,sensor | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
chillerReq | chillerReq | Chiller Request | Chiller Request |  | chillerReq | No | No | No | Bool | Request/No Request | Request/No Request | [6 empty] | chiller,request,cmd | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
chillerRuntime | chillerRuntime | Chiller Runtime | Chiller Runtime |  | chillerRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | CLR | 2.15 (Released),2.16 (Pre-Release)
chillerStage | chillerStageXXXX | Chiller Stage | Chiller Stage XX |  | chillerStage(\d{0,4}) | Yes | Yes | No | Bool | On/Off | On/Off |  |  |  |  | XX |  | chiller,status,cmd | CLR,CWS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
chillerStageDownDelayOnSp | chillerStageDownDelayOnSp | Chiller Stage Down Delay On Setpoint | Chiller Stage Down Delay On Setpoint |  | chillerStageDownDelayOnSp | No | No | No | Number |  |  | minute | minute | 0 | 0 |  |  | chiller,stageDown,delay,on,sp | CWS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
chillerStageDownSp | chillerStageDownSp | Chiller Stage Down Setpoint | Chiller Stage Down Setpoint |  | chillerStageDownSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | chiller,stageDown,effective,sp | CWS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
chillerStageOffSp | chillerStageXXXXOffSp | Chiller Stage Off Setpoint | Chiller Stage XX Off Setpoint |  | chillerStage(\d{0,4})OffSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 | XX |  | chiller,off,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
chillerStageOnSp | chillerStageXXXXOnSp | Chiller Stage On Setpoint | Chiller Stage XX On Setpoint |  | chillerStage(\d{0,4})OnSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 | XX |  | chiller,on,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
chillerStageUpDelayOnSp | chillerStageUpDelayOnSp | Chiller Stage Up Delay Setpoint | Chiller Stage Up Delay Setpoint |  | chillerStageUpDelayOnSp | No | No | No | Number |  |  | minute | minute | 0 | 0 |  |  | chiller,stageUp,delay,on,sp | CWS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
chillerStageUpSp | chillerStageUpSp | Chiller Stage Up Setpoint | Chiller Stage Up Setpoint |  | chillerStageUpSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | chiller,stageUp,effective,sp | CWS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
chillerStarts | chillerStarts | Chiller Starts | Chiller Starts |  | chillerStarts | Yes | No | No | Number |  |  |  |  | 0 | 0 |  |  | chiller,starts,sensor | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
chillerStatus | chillerStatus | Chiller Status | Chiller Status |  | chillerStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | chiller,status,common,sensor | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
circPumpAlarm | circPumpXXXXAlarm | Circulation Pump Alarm | Circulation Pump XX Alarm |  | circPump(\w{0,4}(?=[A-Z]¦$))Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | circ,water,pump,common,alarm | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
circPumpAlarmReset | circPumpXXXXAlarmReset | Circulation Pump Alarm Reset | Circulation Pump XX Alarm Reset |  | circPump(\w{0,4}(?=[A-Z]¦$))AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | circ,water,pump,reset,alarm | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
circPump | circPumpXXXX | Circulation Pump Command | Circulation Pump XX Command |  | circPump((?:(?!Lead)(?!Ovr)\w){0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | circ,water,pump,status,cmd | BLR | 2.15 (Released),2.16 (Pre-Release)
circPumpCurrent | circPumpXXXXCurrent | Circulation Pump Current | Circulation Pump XX Current |  | circPump(\w{0,4}(?=[A-Z]¦$))Current | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | circ,water,pump,current,sensor | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
circPumpDelayOffSp | circPumpXXXXDelayOffSp | Circulation Pump Delay Off Setpoint | Circulation Pump XX Delay Off Setpoint |  | circPump(\w{0,4}(?=[A-Z]¦$))DelayOffSp | No | No | No | Number |  |  | minute | minute | 0 | 0 |  |  | circ,water,pump,delay,off,sp | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
circPumpEnable | circPumpXXXXEnable | Circulation Pump Enable | Circulation Pump XX Enable |  | circPump(\w{0,4}(?=[A-Z]¦$))Enable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | circ,water,pump,enable,cmd | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
circPumpEnableDb | circPumpXXXXEnableDb | Circulation Pump Enable Deadband | Circulation Pump XX Enable Deadband |  | circPump(\w{0,4}(?=[A-Z]¦$))EnableDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | circ,water,pump,enable,deadband,sp | BLR | 2.15 (Released),2.16 (Pre-Release)
circPumpEnableSp | circPumpXXXXEnableSp | Circulation Pump Enable Setpoint | Circulation Pump XX Enable Setpoint |  | circPump((?:(?!Lag)\w){0,4}(?=[A-Z]¦$))EnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | circ,water,pump,enable,effective,sp | BLR | 2.15 (Released),2.16 (Pre-Release)
circPumpEnteringPressure | circPumpXXXXEnteringPressure | Circulation Pump Entering Pressure | Circulation Pump XX Entering Pressure |  | circPump(\w{0,4}(?=[A-Z]¦$))EnteringPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | circ,water,pump,entering,pressure,sensor | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
circPumpFault | circPumpXXXXFault | Circulation Pump Fault | Circulation Pump XX Fault |  | circPump(\w{0,4}(?=[A-Z]¦$))Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | circ,water,pump,fault,common | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
circPumpLagDisableSp | circPumpXXXXLagDisableSp | Circulation Pump Lag Disable Setpoint | Circulation Pump XX Lag Disable Setpoint |  | circPump(\w{0,4}(?=[A-Z]¦$))LagDisableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | circ,water,pump,lag,disable,sp | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
circPumpLagEnableSp | circPumpXXXXLagEnableSp | Circulation Pump Lag Enable Setpoint | Circulation Pump XX Lag Enable Setpoint |  | circPump(\w{0,4}(?=[A-Z]¦$))LagEnableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | circ,water,pump,lag,enable,sp | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
circPumpLagReq | circPumpXXXXLagReq | Circulation Pump Lag Request | Circulation Pump XX Lag Request |  | circPump(\w{0,4}(?=[A-Z]¦$))LagReq | No | No | No | Bool | Request/No Request | Request/No Request | [6 empty] | circ,water,pump,lag,request,cmd | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
circPumpLead | circPumpLead | Circulation Pump Lead | Circulation Pump Lead |  | circPumpLead | Yes | Yes | No | Bool | Lead 1/Lead 2 | Lead 1/Lead 2 | [6 empty] | circ,water,pump,lead,sp | BLR | 2.15 (Released),2.16 (Pre-Release)
circPumpLeadXor | circPumpLeadXor | Circulation Pump Lead Change Over | Circulation Pump Lead Change Over |  | circPumpLeadXor | No | No | No | Bool | On/Off | On/Off | [6 empty] | circ,water,pump,lead,changeOver,cmd | BLR | 2.15 (Released),2.16 (Pre-Release)
circPumpLeadXorRuntimeSp | circPumpLeadXorRuntimeSp | Circulation Pump Lead Change Over Runtime Setpoint | Circulation Pump Lead Change Over Runtime Setpoint |  | circPumpLeadXorRuntimeSp | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | BLR | 2.15 (Released),2.16 (Pre-Release)
circPumpLeavingPressure | circPumpXXXXLeavingPressure | Circulation Pump Leaving Pressure | Circulation Pump XX Leaving Pressure |  | circPump(\w{0,4}(?=[A-Z]¦$))LeavingPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | circ,water,pump,leaving,pressure,sensor | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
circPumpMaintSwitch | circPumpXXXXMaintSwitch | Circulation Pump Maintenance Switch | Circulation Pump XX Maintenance Switch |  | circPump(\w{0,4}(?=[A-Z]¦$))MaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | circ,water,pump,maintenance,switch,cmd | BLR | 2.15 (Released),2.16 (Pre-Release)
circPumpOvr | circPumpXXXXOvr | Circulation Pump Override | Circulation Pump XX Override |  | circPump(\w{0,4}(?=[A-Z]¦$))Ovr | No | No | No | Bool | On/Off | On/Off | [6 empty] | circ,water,pump,status,ovr | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
circPumpPressureDelta | circPumpXXXXPressureDelta | Circulation Pump Pressure Delta | Circulation Pump XX Pressure Delta |  | circPump(\w{0,4}(?=[A-Z]¦$))PressureDelta | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | circ,water,pump,common,pressure,delta,sensor | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
circPumpPressureHiAlarm | circPumpXXXXPressureHiAlarm | Circulation Pump Pressure High Alarm | Circulation Pump XX Pressure High Alarm |  | circPump(\w{0,4}(?=[A-Z]¦$))PressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | circ,water,pump,pressure,high,alarm | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
circPumpPressureHiSp | circPumpXXXXPressureHiSp | Circulation Pump Pressure High Setpoint | Circulation Pump XX Pressure High Setpoint |  | circPump(\w{0,4}(?=[A-Z]¦$))PressureHiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | circ,water,pump,pressure,high,sp | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
circPumpPressureLoAlarm | circPumpXXXXPressureLoAlarm | Circulation Pump Pressure Low Alarm | Circulation Pump XX Pressure Low Alarm |  | circPump(\w{0,4}(?=[A-Z]¦$))PressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | circ,water,pump,pressure,low,alarm | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
circPumpPressureLoSp | circPumpXXXXPressureLoSp | Circulation Pump Pressure Low Setpoint | Circulation Pump XX Pressure Low Setpoint |  | circPump(\w{0,4}(?=[A-Z]¦$))PressureLoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | circ,water,pump,pressure,low,sp | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
circPumpRuntime | circPumpXXXXRuntime | Circulation Pump Runtime | Circulation Pump XX Runtime |  | circPump(\w{0,4}(?=[A-Z]¦$))Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | BLR | 2.15 (Released),2.16 (Pre-Release)
circPumpSpeed | circPumpXXXXSpeed | Circulation Pump Speed | Circulation Pump XX Speed |  | circPump(\w{0,4}(?=[A-Z]¦$))Speed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | circ,water,pump,speed,cmd | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
circPumpSpeedFb | circPumpXXXXSpeedFb | Circulation Pump Speed Feedback | Circulation Pump XX Speed Feedback |  | circPump(\w{0,4}(?=[A-Z]¦$))SpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | circ,water,pump,speed,sensor | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
circPumpSpeedMaxSp | circPumpXXXXSpeedMaxSp | Circulation Pump Speed Max Setpoint | Circulation Pump XX Speed Max Setpoint |  | circPump(\w{0,4}(?=[A-Z]¦$))SpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | circ,water,pump,speed,max,sp | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
circPumpSpeedMinSp | circPumpXXXXSpeedMinSp | Circulation Pump Speed Min Setpoint | Circulation Pump XX Speed Min Setpoint |  | circPump(\w{0,4}(?=[A-Z]¦$))SpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | circ,water,pump,speed,min,sp | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
circPumpSpeedOvr | circPumpXXXXSpeedOvr | Circulation Pump Speed Override | Circulation Pump XX Speed Override |  | circPump(\w{0,4}(?=[A-Z]¦$))SpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | circ,water,pump,speed,ovr | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
circPumpSpeedSp | circPumpXXXXSpeedSp | Circulation Pump Speed Setpoint | Circulation Pump XX Speed Setpoint |  | circPump(\w{0,4}(?=[A-Z]¦$))SpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | circ,water,pump,speed,effective,sp | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
circPumpStatus | circPumpXXXXStatus | Circulation Pump Status | Circulation Pump XX Status |  | circPump(\w{0,4}(?=[A-Z]¦$))Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | circ,water,pump,status,sensor | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDamper | coldDeckDamperXXXX | Cold Deck Damper Command | Cold Deck Damper XX Command |  | coldDeckDamper(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | coldDeck,air,damper,position,cmd | AHU,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDamperFb | coldDeckDamperXXXXFb | Cold Deck Damper Feedback | Cold Deck Damper XX Feedback |  | coldDeckDamper(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | coldDeck,air,damper,position,sensor | AHU,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDamperOvr | coldDeckDamperXXXXOvr | Cold Deck Damper Override | Cold Deck Damper XX Override |  | coldDeckDamper(\d{0,4})Ovr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | coldDeck,air,damper,position,ovr | AHU,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeDehumidMaxSp | coldDeckDischargeDehumidXXXXMaxSp | Cold Deck Discharge Dehumidification Max Reset Setpoint | Cold Deck Discharge Dehumidification XX Max Reset Setpoint |  | coldDeckDischargeDehumid(\d{0,4})MaxSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | coldDeck,discharge,air,dehumid,max,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeDehumidMinSp | coldDeckDischargeDehumidXXXXMinSp | Cold Deck Discharge Dehumidification Min Reset Setpoint | Cold Deck Discharge Dehumidification XX Min Reset Setpoint |  | coldDeckDischargeDehumid(\d{0,4})MinSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | coldDeck,discharge,air,dehumid,min,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeDehumidSp | coldDeckDischargeDehumidXXXXSp | Cold Deck Discharge Dehumidification Setpoint | Cold Deck Discharge Dehumidification XX Setpoint |  | coldDeckDischargeDehumid(\d{0,4})Sp | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | coldDeck,discharge,air,dehumid,effective,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeEnthalpy | coldDeckDischargeEnthalpyXXXX | Cold Deck Discharge Enthalpy | Cold Deck Discharge Enthalpy XX |  | coldDeckDischargeEnthalpy(\d{0,4}) | Yes | Yes | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | coldDeck,discharge,air,enthalpy,sensor | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeEnthalpyDb | coldDeckDischargeEnthalpyXXXXDb | Cold Deck Discharge Enthalpy Deadband | Cold Deck Discharge Enthalpy XX Deadband |  | coldDeckDischargeEnthalpy(\d{0,4})Db | No | No | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | coldDeck,discharge,air,enthalpy,deadband,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeEnthalpyHiSp | coldDeckDischargeEnthalpyXXXXHiSp | Cold Deck Discharge Enthalpy High Setpoint | Cold Deck Discharge Enthalpy XX High Setpoint |  | coldDeckDischargeEnthalpy(\d{0,4})HiSp | No | No | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | coldDeck,discharge,air,enthalpy,high,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeEnthalpyLoSp | coldDeckDischargeEnthalpyXXXXLoSp | Cold Deck Discharge Enthalpy Low Setpoint | Cold Deck Discharge Enthalpy XX Low Setpoint |  | coldDeckDischargeEnthalpy(\d{0,4})LoSp | No | No | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | coldDeck,discharge,air,enthalpy,low,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeEnthalpyMaxSp | coldDeckDischargeEnthalpyXXXXMaxSp | Cold Deck Discharge Enthalpy Max Reset Setpoint | Cold Deck Discharge Enthalpy XX Max Reset Setpoint |  | coldDeckDischargeEnthalpy(\d{0,4})MaxSp | No | No | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | coldDeck,discharge,air,enthalpy,max,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeEnthalpyMinSp | coldDeckDischargeEnthalpyXXXXMinSp | Cold Deck Discharge Enthalpy Min Reset Setpoint | Cold Deck Discharge Enthalpy XX Min Reset Setpoint |  | coldDeckDischargeEnthalpy(\d{0,4})MinSp | No | No | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | coldDeck,discharge,air,enthalpy,min,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeEnthalpySp | coldDeckDischargeEnthalpyXXXXSp | Cold Deck Discharge Enthalpy Setpoint | Cold Deck Discharge Enthalpy XX Setpoint |  | coldDeckDischargeEnthalpy(\d{0,4})Sp | Yes | Yes | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | coldDeck,discharge,air,enthalpy,effective,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeFlow | coldDeckDischargeFlowXXXX | Cold Deck Discharge Flow | Cold Deck Discharge Flow XX |  | coldDeckDischargeFlow(\d{0,4}) | Yes | Yes | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | coldDeck,discharge,air,flow,sensor | AFMS,AHU,CU,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeFlowDb | coldDeckDischargeFlowXXXXDb | Cold Deck Discharge Flow Deadband | Cold Deck Discharge Flow XX Deadband |  | coldDeckDischargeFlow(\d{0,4})Db | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | coldDeck,discharge,air,flow,deadband,sp | AHU,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeFlowHiSp | coldDeckDischargeFlowXXXXHiSp | Cold Deck Discharge Flow High Setpoint | Cold Deck Discharge Flow XX High Setpoint |  | coldDeckDischargeFlow(\d{0,4})HiSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | coldDeck,discharge,air,flow,high,sp | AHU,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeFlowLoSp | coldDeckDischargeFlowXXXXLoSp | Cold Deck Discharge Flow Low Setpoint | Cold Deck Discharge Flow XX Low Setpoint |  | coldDeckDischargeFlow(\d{0,4})LoSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | coldDeck,discharge,air,flow,low,sp | AHU,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeFlowMaxSp | coldDeckDischargeFlowXXXXMaxSp | Cold Deck Discharge Flow Max Reset Setpoint | Cold Deck Discharge Flow XX Max Reset Setpoint |  | coldDeckDischargeFlow(\d{0,4})MaxSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | coldDeck,discharge,air,flow,max,sp | AHU,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeFlowMinSp | coldDeckDischargeFlowXXXXMinSp | Cold Deck Discharge Flow Min Reset Setpoint | Cold Deck Discharge Flow XX Min Reset Setpoint |  | coldDeckDischargeFlow(\d{0,4})MinSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | coldDeck,discharge,air,flow,min,sp | AHU,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeFlowSp | coldDeckDischargeFlowXXXXSp | Cold Deck Discharge Flow Setpoint | Cold Deck Discharge Flow XX Setpoint |  | coldDeckDischargeFlow(\d{0,4})Sp | Yes | Yes | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | coldDeck,discharge,air,flow,effective,sp | AHU,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeHumidMaxSp | coldDeckDischargeHumidXXXXMaxSp | Cold Deck Discharge Humidification Max Reset Setpoint | Cold Deck Discharge Humidification XX Max Reset Setpoint |  | coldDeckDischargeHumid(\d{0,4})MaxSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | coldDeck,discharge,air,humid,max,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeHumidMinSp | coldDeckDischargeHumidXXXXMinSp | Cold Deck Discharge Humidification Min Reset Setpoint | Cold Deck Discharge Humidification XX Min Reset Setpoint |  | coldDeckDischargeHumid(\d{0,4})MinSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | coldDeck,discharge,air,humid,min,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeHumidSp | coldDeckDischargeHumidXXXXSp | Cold Deck Discharge Humidification Setpoint | Cold Deck Discharge Humidification XX Setpoint |  | coldDeckDischargeHumid(\d{0,4})Sp | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | coldDeck,discharge,air,humid,effective,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeHumidity | coldDeckDischargeHumidityXXXX | Cold Deck Discharge Humidity | Cold Deck Discharge Humidity XX |  | coldDeckDischargeHumidity(\d{0,4}) | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | coldDeck,discharge,air,humidity,sensor | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeHumidityDb | coldDeckDischargeHumidityXXXXDb | Cold Deck Discharge Humidity Deadband | Cold Deck Discharge Humidity XX Deadband |  | coldDeckDischargeHumidity(\d{0,4})Db | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | coldDeck,discharge,air,humidity,deadband,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeHumidityHiSp | coldDeckDischargeHumidityXXXXHiSp | Cold Deck Discharge Humidity High Setpoint | Cold Deck Discharge Humidity XX High Setpoint |  | coldDeckDischargeHumidity(\d{0,4})HiSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | coldDeck,discharge,air,humidity,high,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeHumidityLoSp | coldDeckDischargeHumidityXXXXLoSp | Cold Deck Discharge Humidity Low Setpoint | Cold Deck Discharge Humidity XX Low Setpoint |  | coldDeckDischargeHumidity(\d{0,4})LoSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | coldDeck,discharge,air,humidity,low,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeHumidityMaxSp | coldDeckDischargeHumidityXXXXMaxSp | Cold Deck Discharge Humidity Max Reset Setpoint | Cold Deck Discharge Humidity XX Max Reset Setpoint |  | coldDeckDischargeHumidity(\d{0,4})MaxSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | coldDeck,discharge,air,humidity,max,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeHumidityMinSp | coldDeckDischargeHumidityXXXXMinSp | Cold Deck Discharge Humidity Min Reset Setpoint | Cold Deck Discharge Humidity XX Min Reset Setpoint |  | coldDeckDischargeHumidity(\d{0,4})MinSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | coldDeck,discharge,air,humidity,min,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeHumiditySp | coldDeckDischargeHumidityXXXXSp | Cold Deck Discharge Humidity Setpoint | Cold Deck Discharge Humidity XX Setpoint |  | coldDeckDischargeHumidity(\d{0,4})Sp | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | coldDeck,discharge,air,humidity,effective,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargePressure | coldDeckDischargePressureXXXX | Cold Deck Discharge Pressure | Cold Deck Discharge Pressure XX |  | coldDeckDischargePressure(\d{0,4}) | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | coldDeck,discharge,air,static,pressure,sensor | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargePressureDb | coldDeckDischargePressureXXXXDb | Cold Deck Discharge Pressure Deadband | Cold Deck Discharge Pressure XX Deadband |  | coldDeckDischargePressure(\d{0,4})Db | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | coldDeck,discharge,air,static,pressure,deadband,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargePressureHiAlarm | coldDeckDischargePressureXXXXHiAlarm | Cold Deck Discharge Pressure High Alarm | Cold Deck Discharge Pressure XX High Alarm |  | coldDeckDischargePressure(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | coldDeck,discharge,air,static,pressure,high,alarm | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargePressureHiSp | coldDeckDischargePressureXXXXHiSp | Cold Deck Discharge Pressure High Setpoint | Cold Deck Discharge Pressure XX High Setpoint |  | coldDeckDischargePressure(\d{0,4})HiSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | coldDeck,discharge,air,static,pressure,high,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargePressureLoAlarm | coldDeckDischargePressureXXXXLoAlarm | Cold Deck Discharge Pressure Low Alarm | Cold Deck Discharge Pressure XX Low Alarm |  | coldDeckDischargePressure(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | coldDeck,discharge,air,static,pressure,low,alarm | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargePressureLoSp | coldDeckDischargePressureXXXXLoSp | Cold Deck Discharge Pressure Low Setpoint | Cold Deck Discharge Pressure XX Low Setpoint |  | coldDeckDischargePressure(\d{0,4})LoSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | coldDeck,discharge,air,static,pressure,low,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargePressureMaxSp | coldDeckDischargePressureXXXXMaxSp | Cold Deck Discharge Pressure Max Reset Setpoint | Cold Deck Discharge Pressure XX Max Reset Setpoint |  | coldDeckDischargePressure(\d{0,4})MaxSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | coldDeck,discharge,air,static,pressure,max,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargePressureMinSp | coldDeckDischargePressureXXXXMinSp | Cold Deck Discharge Pressure Min Reset Setpoint | Cold Deck Discharge Pressure XX Min Reset Setpoint |  | coldDeckDischargePressure(\d{0,4})MinSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | coldDeck,discharge,air,static,pressure,min,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargePressureSp | coldDeckDischargePressureXXXXSp | Cold Deck Discharge Pressure Setpoint | Cold Deck Discharge Pressure XX Setpoint |  | coldDeckDischargePressure(\d{0,4})Sp | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | coldDeck,discharge,air,static,pressure,effective,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeTemp | coldDeckDischargeTempXXXX | Cold Deck Discharge Temperature | Cold Deck Discharge Temperature XX |  | coldDeckDischargeTemp(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | coldDeck,discharge,air,temp,sensor | AFMS,AHU,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeTempDb | coldDeckDischargeTempXXXXDb | Cold Deck Discharge Temperature Deadband | Cold Deck Discharge Temperature XX Deadband |  | coldDeckDischargeTemp(\d{0,4})Db | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | coldDeck,discharge,air,temp,deadband,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeTempHiSp | coldDeckDischargeTempXXXXHiSp | Cold Deck Discharge Temperature High Setpoint | Cold Deck Discharge Temperature XX High Setpoint |  | coldDeckDischargeTemp(\d{0,4})HiSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | coldDeck,discharge,air,temp,high,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeTempLoSp | coldDeckDischargeTempXXXXLoSp | Cold Deck Discharge Temperature Low Setpoint | Cold Deck Discharge Temperature XX Low Setpoint |  | coldDeckDischargeTemp(\d{0,4})LoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | coldDeck,discharge,air,temp,low,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeTempMaxSp | coldDeckDischargeTempXXXXMaxSp | Cold Deck Discharge Temperature Max Reset Setpoint | Cold Deck Discharge Temperature XX Max Reset Setpoint |  | coldDeckDischargeTemp(\d{0,4})MaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | coldDeck,discharge,air,temp,max,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeTempMinSp | coldDeckDischargeTempXXXXMinSp | Cold Deck Discharge Temperature Min Reset Setpoint | Cold Deck Discharge Temperature XX Min Reset Setpoint |  | coldDeckDischargeTemp(\d{0,4})MinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | coldDeck,discharge,air,temp,min,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeTempSp | coldDeckDischargeTempXXXXSp | Cold Deck Discharge Temperature Setpoint | Cold Deck Discharge Temperature XX Setpoint |  | coldDeckDischargeTemp(\d{0,4})Sp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | coldDeck,discharge,air,temp,effective,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckDischargeTempSpOvr | coldDeckDischargeTempXXXXSpOvr | Cold Deck Discharge Temperature Setpoint Override | Cold Deck Discharge Temperature XX Setpoint Override |  | coldDeckDischargeTemp(\d{0,4})SpOvr | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | coldDeck,discharge,air,temp,effective,spOvr | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckFanAlarm | coldDeckFanXXXXAlarm | Cold Deck Fan Alarm | Cold Deck Fan XX Alarm |  | coldDeckFan(\w{0,4}(?=[A-Z]¦$))Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | coldDeck,air,fan,general,common,alarm | AHU | 2.15 (Released),2.16 (Pre-Release)
coldDeckFanAlarmReset | coldDeckFanXXXXAlarmReset | Cold Deck Fan Alarm Reset | Cold Deck Fan XX Alarm Reset |  | coldDeckFan(\w{0,4}(?=[A-Z]¦$))AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | coldDeck,air,fan,common,reset,alarm | AHU | 2.15 (Released),2.16 (Pre-Release)
coldDeckFan | coldDeckFanXXXX | Cold Deck Fan Command | Cold Deck Fan XX Command |  | coldDeckFan((?:(?!Ovr)\w){0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | coldDeck,air,fan,status,cmd | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckFanCurrent | coldDeckFanXXXXCurrent | Cold Deck Fan Current | Cold Deck Fan XX Current |  | coldDeckFan(\w{0,4}(?=[A-Z]¦$))Current | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | coldDeck,air,fan,current,sensor | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckFanEnteringPressure | coldDeckFanXXXXEnteringPressure | Cold Deck Fan Entering Pressure | Cold Deck Fan XX Entering Pressure |  | coldDeckFan(\w{0,4}(?=[A-Z]¦$))EnteringPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | coldDeck,air,fan,entering,pressure,sensor | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckFanFault | coldDeckFanXXXXFault | Cold Deck Fan Fault | Cold Deck Fan XX Fault |  | coldDeckFan(\w{0,4}(?=[A-Z]¦$))Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | coldDeck,air,fan,fault | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckFanFilterAlarm | coldDeckFanXXXXFilterAlarm | Cold Deck Fan Filter Alarm | Cold Deck Fan XX Filter Alarm |  | coldDeckFan(\w{0,4}(?=[A-Z]¦$))FilterAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | coldDeck,air,fan,filter,general,alarm | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckFanFilterAlarmReset | coldDeckFanXXXXFilterAlarmReset | Cold Deck Fan Filter Alarm Reset | Cold Deck Fan XX Filter Alarm Reset |  | coldDeckFan(\w{0,4}(?=[A-Z]¦$))FilterAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | coldDeck,air,fan,filter,reset,alarm | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckFanFilterPressureDelta | coldDeckFanXXXXFilterPressureDelta | Cold Deck Fan Filter Pressure Delta | Cold Deck Fan XX Filter Pressure Delta |  | coldDeckFan(\w{0,4}(?=[A-Z]¦$))FilterPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | coldDeck,air,fan,filter,pressure,delta,sensor | AHU | 2.12,2.13,2.14,2.15 (Released)
coldDeckFanFilterRuntime | coldDeckFanXXXXFilterRuntime | Cold Deck Fan Filter Runtime | Cold Deck Fan XX Filter Runtime |  | coldDeckFan(\w{0,4}(?=[A-Z]¦$))FilterRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU | 2.15 (Released),2.16 (Pre-Release)
coldDeckFanLeavingPressure | coldDeckFanXXXXLeavingPressure | Cold Deck Fan Leaving Pressure | Cold Deck Fan XX Leaving Pressure |  | coldDeckFan(\w{0,4}(?=[A-Z]¦$))LeavingPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | coldDeck,air,fan,leaving,pressure,sensor | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckFanMaintSwitch | coldDeckFanXXXXMaintSwitch | Cold Deck Fan Maintenance Switch | Cold Deck Fan XX Maintenance Switch |  | coldDeckFan(\w{0,4}(?=[A-Z]¦$))MaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | maintenance,switch,cmd,fan,air,coldDeck | AHU | 2.15 (Released),2.16 (Pre-Release)
coldDeckFanOvr | coldDeckFanXXXXOvr | Cold Deck Fan Override | Cold Deck Fan XX Override |  | coldDeckFan(\w{0,4}(?=[A-Z]¦$))Ovr | No | No | No | Bool | On/Off | On/Off | [6 empty] | coldDeck,air,fan,status,ovr | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckFanPressureDelta | coldDeckFanXXXXPressureDelta | Cold Deck Fan Pressure Delta | Cold Deck Fan XX Pressure Delta |  | coldDeckFan(\w{0,4}(?=[A-Z]¦$))PressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | coldDeck,air,fan,common,pressure,delta,sensor | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckFanPressureHiAlarm | coldDeckFanXXXXPressureHiAlarm | Cold Deck Fan Pressure High Alarm | Cold Deck Fan XX Pressure High Alarm |  | coldDeckFan(\w{0,4}(?=[A-Z]¦$))PressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | coldDeck,air,fan,pressure,high,alarm | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckFanPressureHiSp | coldDeckFanXXXXPressureHiSp | Cold Deck Fan Pressure High Setpoint | Cold Deck Fan XX Pressure High Setpoint |  | coldDeckFan(\w{0,4}(?=[A-Z]¦$))PressureHiSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | coldDeck,air,fan,pressure,high,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckFanPressureLoAlarm | coldDeckFanXXXXPressureLoAlarm | Cold Deck Fan Pressure Low Alarm | Cold Deck Fan XX Pressure Low Alarm |  | coldDeckFan(\w{0,4}(?=[A-Z]¦$))PressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | coldDeck,air,fan,pressure,low,alarm | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckFanPressureLoSp | coldDeckFanXXXXPressureLoSp | Cold Deck Fan Pressure Low Setpoint | Cold Deck Fan XX Pressure Low Setpoint |  | coldDeckFan(\w{0,4}(?=[A-Z]¦$))PressureLoSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | coldDeck,air,fan,pressure,low,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckFanRuntime | coldDeckFanXXXXRuntime | Cold Deck Fan Runtime | Cold Deck Fan XX Runtime |  | coldDeckFan(\w{0,4}(?=[A-Z]¦$))Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU | 2.15 (Released),2.16 (Pre-Release)
coldDeckFanSpeed | coldDeckFanXXXXSpeed | Cold Deck Fan Speed | Cold Deck Fan XX Speed |  | coldDeckFan(\w{0,4}(?=[A-Z]¦$))Speed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | coldDeck,air,fan,speed,cmd | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckFanSpeedFb | coldDeckFanXXXXSpeedFb | Cold Deck Fan Speed Feedback | Cold Deck Fan XX Speed Feedback |  | coldDeckFan(\w{0,4}(?=[A-Z]¦$))SpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | coldDeck,air,fan,speed,sensor | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckFanSpeedMaxSp | coldDeckFanXXXXSpeedMaxSp | Cold Deck Fan Speed Max Setpoint | Cold Deck Fan XX Speed Max Setpoint |  | coldDeckFan(\w{0,4}(?=[A-Z]¦$))SpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | coldDeck,air,fan,speed,max,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckFanSpeedMinSp | coldDeckFanXXXXSpeedMinSp | Cold Deck Fan Speed Min Setpoint | Cold Deck Fan XX Speed Min Setpoint |  | coldDeckFan(\w{0,4}(?=[A-Z]¦$))SpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | coldDeck,air,fan,speed,min,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckFanSpeedOvr | coldDeckFanXXXXSpeedOvr | Cold Deck Fan Speed Override | Cold Deck Fan XX Speed Override |  | coldDeckFan(\w{0,4}(?=[A-Z]¦$))SpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | coldDeck,air,fan,speed,ovr | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckFanSpeedSp | coldDeckFanXXXXSpeedSp | Cold Deck Fan Speed Setpoint | Cold Deck Fan XX Speed Setpoint |  | coldDeckFan(\w{0,4}(?=[A-Z]¦$))SpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | coldDeck,air,fan,speed,effective,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coldDeckFanStatus | coldDeckFanXXXXStatus | Cold Deck Fan Status | Cold Deck Fan XX Status |  | coldDeckFan(\w{0,4}(?=[A-Z]¦$))Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | coldDeck,air,fan,status,sensor | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
combustionAlarm | combustionAlarm | Combustion Alarm | Combustion Alarm |  | combustionAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | combustion,common,alarm | HWS,MSC,SMS,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
combustionDamperAlarm | combustionDamperAlarm | Combustion Damper Alarm | Combustion Damper Alarm |  | combustionDamperAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | combustion,air,damper,position,alarm | HWS,MSC,SMS,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
combustionDamper | combustionDamper | Combustion Damper Command | Combustion Damper Command |  | combustionDamper | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | combustion,air,damper,position,cmd | HWS,MSC,SMS,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
combustionDamperFb | combustionDamperFb | Combustion Damper Feedback | Combustion Damper Feedback |  | combustionDamperFb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | combustion,air,damper,position,sensor | HWS,MSC,SMS,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
combustionFan | combustionFan | Combustion Fan Command | Combustion Fan Command |  | combustionFan | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | combustion,air,fan,status,cmd | BLR,WH | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
combustionFanMotorSpeed | combustionFanMotorSpeed | Combustion Fan Motor Speed Command | Combustion Fan Motor Speed Command |  | combustionFanMotorSpeed | Yes | Yes | No | Number |  |  | revolutions_per_minute | revolutions_per_minute | 0 | 0 |  |  | combustion,air,fan,motorSpeed,sensor | BLR,WH | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
combustionFanMotorSpeedSp | combustionFanMotorSpeedSp | Combustion Fan Motor Speed Setpoint | Combustion Fan Motor Speed Setpoint |  | combustionFanMotorSpeedSp | Yes | Yes | No | Number |  |  | revolutions_per_minute | revolutions_per_minute | 0 | 0 |  |  | combustion,air,fan,motorSpeed,sp | BLR,WH | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
commAlarm | commAlarm | Communication Alarm | Communication Alarm |  | commAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | comm,alarm | AC,AFMS,AHU,ATS,ATU,BATT,BLND,BLR,BRK,BTU,CF,CLR,CM,CMP,CRAC,CRAH,CU,CUH,CWS,DAC,DCU,DCWS,DH,DHU,DHWS,DOAS,DOOR,DRY,EC,EF,ELV,ENC,ERU,FC,FCU,FDS,FEXT,FP,FPB,FSD,FSEP,FSS,GBL,GDS,GEN,GEO,GINT,GM,HDS,HP,HRU,HT,HUM,HVHS,HVLS,HWS,INV,LDS,LS,LTGE,LTGI,MAU,MMS,MSC,NC,OF,PDU,PFC,PH,PINT,PIU,PM,PMP,PRLY,PV,PWS,REC,RECT,RF,RFG,ROS,RP,RPC,RPF,RPP,RRS,RTU,SCRB,SEC,SKYL,SM,SMEX,SMP,SMS,STS,SUP,TF,TNK,TRN,TVS,TWR,UH,UPS,UV,VAV,VBTU,VFD,VGM,VPM,VRF,VWM,WH,WM,WNDW,WS,WSS,WTHR,WTS,XFMR,ZD,ZN,CDA,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
compAlarm | compXXXXAlarm | Compressor Alarm | Compressor XX Alarm |  | comp(\w{0,4}(?=[A-Z]¦$))Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | compressor,common,alarm | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compAlarmCode | compXXXXAlarmCode | Compressor Alarm Code | Compressor XX Alarm Code |  | comp(\w{0,4}(?=[A-Z]¦$))AlarmCode | Yes | Yes | No | Str | [8 empty] | compressor,alarm,code | AHU,ATU,CLR,CMP,CRAC,CRAH,CU,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released)
compBypass | compXXXXBypass | Compressor Bypass | Compressor XX Bypass |  | comp(\w{0,4}(?=[A-Z]¦$))Bypass | Yes | Yes | No | Bool | Bypass/Normal | Bypass/Normal | [6 empty] | compressor,bypass,sensor | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
comp | compXXXX | Compressor Command | Compressor XX Command |  | comp((?:(?!Lead)(?!Mod)(?!Mode)(?!Ovr)(?!Temp)\w){0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | compressor,status,cmd | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compCurrent | compXXXXCurrent | Compressor Current | Compressor XX Current |  | comp(\w{0,4}(?=[A-Z]¦$))Current | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | compressor,current,sensor | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compDCVoltage | compXXXXDCVoltage | Compressor DC Voltage | Compressor XX DC Voltage |  | comp(\w{0,4}(?=[A-Z]¦$))DCVoltage | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  |  | compressor,dcVolt,sensor | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compDefrost | compXXXXDefrost | Compressor Defrost | Compressor XX Defrost |  | comp(\w{0,4}(?=[A-Z]¦$))Defrost | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | compressor,defrost,cmd | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compDemand | compXXXXDemand | Compressor Demand | Compressor XX Demand |  | comp(\w{0,4}(?=[A-Z]¦$))Demand | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | compressor,demand,sensor | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compDischargePressureHiSp | compXXXXDischargePressureHiSp | Compressor Discharge High Pressure Setpoint | Compressor XX Discharge High Pressure Setpoint |  | comp(\w{0,4}(?=[A-Z]¦$))DischargePressureHiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | compressor,discharge,pressure,high,sp | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compDischargePressure | compXXXXDischargePressure | Compressor Discharge Pressure | Compressor XX Discharge Pressure |  | comp(\w{0,4}(?=[A-Z]¦$))DischargePressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | compressor,discharge,pressure,sensor | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compDischargePressureFault | compXXXXDischargePressureFault | Compressor Discharge Pressure Fault | Compressor XX Discharge Pressure Fault |  | comp(\w{0,4}(?=[A-Z]¦$))DischargePressureFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | compressor,discharge,pressure,fault | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compDischargePressureHiAlarm | compXXXXDischargePressureHiAlarm | Compressor Discharge Pressure High Alarm | Compressor XX Discharge Pressure High Alarm |  | comp(\w{0,4}(?=[A-Z]¦$))DischargePressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | compressor,discharge,pressure,high,alarm | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compDischargePressureLoAlarm | compXXXXDischargePressureLoAlarm | Compressor Discharge Pressure Low Alarm | Compressor XX Discharge Pressure Low Alarm |  | comp(\w{0,4}(?=[A-Z]¦$))DischargePressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | compressor,discharge,pressure,low,alarm | AHU,ATU,CLR,CMP,CRAC,CRAH,CU,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compDischargeSatTemp | compXXXXDischargeSatTemp | Compressor Discharge Saturation Temperature | Compressor XX Discharge Saturation Temperature |  | comp(\w{0,4}(?=[A-Z]¦$))DischargeSatTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | compressor,discharge,saturation,temp,sensor | AHU,ATU,CLR,CMP,CRAC,CRAH,CU,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compDischargeTemp | compXXXXDischargeTemp | Compressor Discharge Temperature | Compressor XX Discharge Temperature |  | comp(\w{0,4}(?=[A-Z]¦$))DischargeTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | compressor,discharge,common,temp,sensor | AHU,ATU,CLR,CMP,CRAC,CRAH,CU,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compEnable | compXXXXEnable | Compressor Enable | Compressor XX Enable |  | comp(\w{0,4}(?=[A-Z]¦$))Enable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | compressor,enable,cmd | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compEnableSp | compXXXXEnableSp | Compressor Enable Setpoint | Compressor XX Enable Setpoint |  | comp(\w{0,4}(?=[A-Z]¦$))EnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | compressor,enable,sp | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compEnergy | compXXXXEnergy | Compressor Energy | Compressor XX Energy |  | comp(\w{0,4}(?=[A-Z]¦$))Energy | Yes | Yes | No | Number |  |  | kilowatt_hour | kilowatt_hour | 0 | 0 |  |  | compressor,energy,sensor | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compEnteringPressure | compXXXXEnteringPressure | Compressor Entering Pressure | Compressor XX Entering Pressure |  | comp(\w{0,4}(?=[A-Z]¦$))EnteringPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | compressor,entering,pressure,sensor | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compEnteringTemp | compXXXXEnteringTemp | Compressor Entering Temperature | Compressor XX Entering Temperature |  | comp(\w{0,4}(?=[A-Z]¦$))EnteringTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | compressor,entering,temp,sensor | AHU,ATU,CLR,CMP,CRAC,CRAH,CU,DHU,DOAS,EC,HP,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compFault | compXXXXFault | Compressor Fault | Compressor XX Fault |  | comp(\w{0,4}(?=[A-Z]¦$))Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | compressor,common,fault | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compFrequency | compXXXXFrequency | Compressor Frequency | Compressor XX Frequency |  | comp(\w{0,4}(?=[A-Z]¦$))Frequency | Yes | Yes | No | Number |  |  | hertz | hertz | 1 | 1 |  |  | compressor,freq,cmd | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compHandMode | compXXXXHandMode | Compressor Hand/Auto Mode | Compressor XX Hand/Auto Mode |  | comp(\w{0,4}(?=[A-Z]¦$))HandMode | Yes | Yes | No | Bool | Hand/Auto | Hand/Auto | [6 empty] | compressor,handMode,sensor | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compLead | compXXXXLead | Compressor Lead | Compressor XX Lead |  | comp(\w{0,4}(?=[A-Z]¦$))Lead | Yes | Yes | No | Bool | Lead 1/Lead 2 | Lead 1/Lead 2 | [6 empty] | compressor,lead,sp | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compLeadXor | compLeadXor | Compressor Lead Change Over | Compressor Lead Change Over |  | compLeadXor | No | No | No | Bool | On/Off | On/Off | [6 empty] | compressor,lead,changeOver,cmd | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compLeadXorRuntimeSp | compLeadXorRuntimeSp | Compressor Lead Change Over Runtime Setpoint | Compressor Lead Change Over Runtime Setpoint |  | compLeadXorRuntimeSp | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compLeavingPressure | compXXXXLeavingPressure | Compressor Leaving Pressure | Compressor XX Leaving Pressure |  | comp(\w{0,4}(?=[A-Z]¦$))LeavingPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | compressor,leaving,pressure,sensor | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compLeavingTemp | compXXXXLeavingTemp | Compressor Leaving Temp | Compressor XX Leaving Temp |  | comp(\w{0,4}(?=[A-Z]¦$))LeavingTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | compressor,leaving,temp,sensor | AHU,ATU,CLR,CMP,CRAC,CRAH,CU,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compLiquidLineTemp | compXXXXLiquidLineTemp | Compressor Liquid Line Temperature | Compressor XX Liquid Line Temperature |  | comp(\w{0,4}(?=[A-Z]¦$))LiquidLineTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | compressor,liquidLine,temp,sensor | AHU,ATU,CLR,CMP,CRAC,CRAH,CU,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compMaint | compXXXXMaint | Compressor Maintenance | Compressor XX Maintenance |  | comp(\w{0,4}(?=[A-Z]¦$))Maint | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | compressor,maintenance,common,cmd | AHU,ATU,CLR,CMP,CRAC,CRAH,CU,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compMaintSwitch | compXXXXMaintSwitch | Compressor Maintenance Switch | Compressor XX Maintenance Switch |  | comp(\w{0,4}(?=[A-Z]¦$))MaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | compressor,maintenance,switch,cmd | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compMode | compXXXXMode | Compressor Mode | Compressor XX Mode |  | comp((?:(?!Hand)\w){0,4}(?=[A-Z]¦$))Mode | Yes | No | No | Bool | Load/Unload | Load/Unload | [6 empty] | compressor,mode,sp | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compMod | compXXXXMod | Compressor Modulation Command | Compressor XX Modulation Command |  | comp(\w{0,4}(?=[A-Z]¦$))Mod | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | compressor,modulation,cmd | AHU,ATU,CLR,CMP,CRAC,CRAH,CU,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compMotorSpeed | compXXXXMotorSpeed | Compressor Motor Speed | Compressor XX Motor Speed |  | comp(\w{0,4}(?=[A-Z]¦$))MotorSpeed | Yes | Yes | No | Number |  |  | revolutions_per_minute | revolutions_per_minute | 0 | 0 |  |  | compressor,motorSpeed,sensor | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compMotorTemp | compXXXXMotorTemp | Compressor Motor Temperature | Compressor XX Motor Temperature |  | comp(\w{0,4}(?=[A-Z]¦$))MotorTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | compressor,motorTemp,sensor | AHU,ATU,CLR,CMP,CRAC,CRAH,CU,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compMotorTempHiAlarm | compXXXXMotorTempHiAlarm | Compressor Motor Temperature High Alarm | Compressor XX Motor Temperature High Alarm |  | comp(\w{0,4}(?=[A-Z]¦$))MotorTempHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | compressor,motorTemp,high,alarm | AHU,ATU,CLR,CMP,CRAC,CRAH,CU,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compOilPressure | compXXXXOilPressure | Compressor Oil Pressure | Compressor XX Oil Pressure |  | comp(\w{0,4}(?=[A-Z]¦$))OilPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | compressor,oil,pressure,sensor | AHU,ATU,CLR,CMP,CRAC,CRAH,CU,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compOilTemp | compXXXXOilTemp | Compressor Oil Temperature | Compressor XX Oil Temperature |  | comp(\w{0,4}(?=[A-Z]¦$))OilTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | compressor,oil,temp,sensor | AHU,ATU,CLR,CMP,CRAC,CRAH,CU,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compOverloadAlarm | compXXXXOverloadAlarm | Compressor Overload Alarm | Compressor XX Overload Alarm |  | comp(\w{0,4}(?=[A-Z]¦$))OverloadAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | compressor,overload,alarm | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compOvr | compXXXXOvr | Compressor Override | Compressor XX Override |  | comp(\w{0,4}(?=[A-Z]¦$))Ovr | No | No | No | Bool | On/Off | On/Off | [6 empty] | compressor,status,ovr | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compPowerReal | compXXXXPowerReal | Compressor Real Power | Compressor XX Real Power |  | comp(\w{0,4}(?=[A-Z]¦$))PowerReal | Yes | Yes | No | Number |  |  | kilowatt | kilowatt | 1 | 1 |  | N | compressor,power,real,sensor | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compRuntime | compXXXXRuntime | Compressor Runtime | Compressor XX Runtime |  | comp(\w{0,4}(?=[A-Z]¦$))Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compSpeed | compXXXXSpeed | Compressor Speed | Compressor XX Speed |  | comp(\w{0,4}(?=[A-Z]¦$))Speed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | compressor,speed,cmd | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compSpeedFb | compXXXXSpeedFb | Compressor Speed Feedback | Compressor XX Speed Feedback |  | comp(\w{0,4}(?=[A-Z]¦$))SpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | compressor,speed,sensor | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compSpeedMaxSp | compXXXXSpeedMaxSp | Compressor Speed Max Setpoint | Compressor XX Speed Max Setpoint |  | comp(\w{0,4}(?=[A-Z]¦$))SpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | compressor,speed,max,sp | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compSpeedMinSp | compXXXXSpeedMinSp | Compressor Speed Min Setpoint | Compressor XX Speed Min Setpoint |  | comp(\w{0,4}(?=[A-Z]¦$))SpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | compressor,speed,min,sp | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compSpeedSp | compXXXXSpeedSp | Compressor Speed Setpoint | Compressor XX Speed Setpoint |  | comp(\w{0,4}(?=[A-Z]¦$))SpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | compressor,speed,effective,sp | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compStarts | compXXXXStarts | Compressor Starts | Compressor XX Starts |  | comp(\w{0,4}(?=[A-Z]¦$))Starts | Yes | No | No | Number |  |  |  |  | 0 | 0 |  |  | compressor,starts,sensor | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compStatus | compXXXXStatus | Compressor Status | Compressor XX Status |  | comp(\w{0,4}(?=[A-Z]¦$))Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | compressor,status,sensor | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compSuctionPressure | compXXXXSuctionPressure | Compressor Suction Pressure | Compressor XX Suction Pressure |  | comp(\w{0,4}(?=[A-Z]¦$))SuctionPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | compressor,suction,pressure,sensor | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compSuctionPressureFault | compXXXXSuctionPressureFault | Compressor Suction Pressure Fault | Compressor XX Suction Pressure Fault |  | comp(\w{0,4}(?=[A-Z]¦$))SuctionPressureFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | compressor,suction,pressure,fault | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compSuctionPressureHiAlarm | compXXXXSuctionPressureHiAlarm | Compressor Suction Pressure High Alarm | Compressor XX Suction Pressure High Alarm |  | comp(\w{0,4}(?=[A-Z]¦$))SuctionPressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | compressor,suction,pressure,high,alarm | AHU,ATU,CLR,CMP,CRAC,CRAH,CU,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compSuctionPressureLoAlarm | compXXXXSuctionPressureLoAlarm | Compressor Suction Pressure Low Alarm | Compressor XX Suction Pressure Low Alarm |  | comp(\w{0,4}(?=[A-Z]¦$))SuctionPressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | compressor,suction,pressure,low,alarm | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compSuctionPressureLoSp | compXXXXSuctionPressureLoSp | Compressor Suction Pressure Low Setpoint | Compressor XX Suction Pressure Low Setpoint |  | comp(\w{0,4}(?=[A-Z]¦$))SuctionPressureLoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | compressor,suction,pressure,low,sp | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compSuctionSatTemp | compXXXXSuctionSatTemp | Compressor Suction Saturation Temperature | Compressor XX Suction Saturation Temperature |  | comp(\w{0,4}(?=[A-Z]¦$))SuctionSatTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | compressor,suction,saturation,temp,sensor | AHU,ATU,CLR,CMP,CRAC,CRAH,CU,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compSuctionTemp | compXXXXSuctionTemp | Compressor Suction Temperature | Compressor XX Suction Temperature |  | comp(\w{0,4}(?=[A-Z]¦$))SuctionTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | compressor,suction,common,temp,sensor | AHU,ATU,CLR,CMP,CRAC,CRAH,CU,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compSuctionTempLoAlarm | compXXXXSuctionTempLoAlarm | Compressor Suction Temperature Low Alarm | Compressor XX Suction Temperature Low Alarm |  | comp(\w{0,4}(?=[A-Z]¦$))SuctionTempLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | compressor,suction,temp,low,alarm | AHU,ATU,CLR,CMP,CRAC,CRAH,CU,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compSuperheatTemp | compXXXXSuperheatTemp | Compressor Superheat Temperature | Compressor XX Superheat Temperature |  | comp(\w{0,4}(?=[A-Z]¦$))SuperheatTemp | Yes | Yes | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | compressor,superheat,temp,sensor | AHU,ATU,CLR,CMP,CRAC,CRAH,CU,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compTemp | compXXXXTemp | Compressor Temperature | Compressor XX Temperature | The temperature of the compressor itself. | comp((?:(?!Oil)\w){0,4}(?=[A-Z]¦$))Temp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | compressor,general,temp,sensor | AHU,ATU,CLR,CMP,CRAC,CRAH,CU,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compTempHiAlarm | compXXXXTempHiAlarm | Compressor Temperature High Alarm | Compressor XX Temperature High Alarm |  | comp((?:(?!Oil)\w){0,4}(?=[A-Z]¦$))TempHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | compressor,general,temp,high,alarm | AHU,ATU,CLR,CMP,CRAC,CRAH,CU,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compTempLoAlarm | compXXXXTempLoAlarm | Compressor Temperature Low Alarm | Compressor XX Temperature Low Alarm |  | comp((?:(?!Oil)\w){0,4}(?=[A-Z]¦$))TempLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | compressor,general,temp,low,alarm | AHU,ATU,CLR,CMP,CRAC,CRAH,CU,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compTorque | compXXXXTorque | Compressor Torque | Compressor XX Torque |  | comp(\w{0,4}(?=[A-Z]¦$))Torque | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | compressor,torque,sensor | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compVoltage | compXXXXVoltage | Compressor Voltage | Compressor XX Voltage |  | comp((?:(?!DC)\w){0,4}(?=[A-Z]¦$))Voltage | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  | N | compressor,volt,sensor | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
compWarning | compXXXXWarning | Compressor Warning | Compressor XX Warning |  | comp(\w{0,4}(?=[A-Z]¦$))Warning | Yes | Yes | No | Bool | Warning/Normal | Warning/Normal | [6 empty] | compressor,warning | AHU,ATU,CLR,CMP,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
condensateAlarm | condensateAlarmXXXX | Condensate Alarm | Condensate Alarm XX |  | condensateAlarm(\d{0,4}) | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | condensate,water,alarm | AHU,CLR,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condensateTemp | condensateTempXXXX | Condensate Temperature | Condensate Temperature XX |  | condensateTemp(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | condensate,water,temp,sensor | AHU,CLR,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condAlarm | condXXXXAlarm | Condenser Alarm | Condenser XX Alarm |  | cond(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | condensed,common,alarm | AHU,CLR,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condBypassFlow | condBypassFlowXXXX | Condenser Bypass Flow | Condenser Bypass Flow XX |  | condBypassFlow(\d{0,4}) | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,bypass,flow,sensor | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condBypassFlowDb | condBypassFlowXXXXDb | Condenser Bypass Flow Deadband | Condenser Bypass Flow XX Deadband |  | condBypassFlow(\d{0,4})Db | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,bypass,flow,deadband,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condBypassFlowHiSp | condBypassFlowXXXXHiSp | Condenser Bypass Flow High Setpoint | Condenser Bypass Flow XX High Setpoint |  | condBypassFlow(\d{0,4})HiSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,bypass,flow,high,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condBypassFlowLoSp | condBypassFlowXXXXLoSp | Condenser Bypass Flow Low Setpoint | Condenser Bypass Flow XX Low Setpoint |  | condBypassFlow(\d{0,4})LoSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,bypass,flow,low,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condBypassFlowMaxSp | condBypassFlowXXXXMaxSp | Condenser Bypass Flow Max Setpoint | Condenser Bypass Flow XX Max Setpoint |  | condBypassFlow(\d{0,4})MaxSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,bypass,flow,max,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condBypassFlowMinSp | condBypassFlowXXXXMinSp | Condenser Bypass Flow Min Setpoint | Condenser Bypass Flow XX Min Setpoint |  | condBypassFlow(\d{0,4})MinSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,bypass,flow,min,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condBypassFlowSp | condBypassFlowXXXXSp | Condenser Bypass Flow Setpoint | Condenser Bypass Flow XX Setpoint |  | condBypassFlow(\d{0,4})Sp | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,bypass,flow,effective,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condBypassTemp | condBypassTempXXXX | Condenser Bypass Temperature | Condenser Bypass Temperature XX |  | condBypassTemp(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | condensed,water,bypass,temp,sensor | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condBypassValve | condBypassValveXXXX | Condenser Bypass Valve Command | Condenser Bypass Valve XX Command |  | condBypassValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | condensed,water,bypass,valve,position,cmd | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condBypassValveFb | condBypassValveXXXXFb | Condenser Bypass Valve Feedback | Condenser Bypass Valve XX Feedback |  | condBypassValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | condensed,water,bypass,valve,position,sensor | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condBypassValveMinSp | condBypassValveXXXXMinSp | Condenser Bypass Valve Minimum Setpoint | Condenser Bypass Valve XX Minimum Setpoint |  | condBypassValve(\d{0,4})MinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | condensed,water,bypass,valve,position,min,sp | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
cond | condXXXX | Condenser Command | Condenser XX Command |  | cond(\d{0,4}) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | condensed,common,status,cmd | AHU,CLR,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condEnergy | condEnergy | Condenser Energy | Condenser Energy |  | condEnergy | Yes | Yes | No | Number |  |  | kilobtu | kilobtu | 0 | 0 |  |  | condensed,water,energy,common,sensor | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condEnteringBypassValve | condEnteringBypassValveXXXX | Condenser Entering Bypass Valve Command | Condenser Entering Bypass Valve XX Command |  | condEnteringBypassValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | water,valve,position,cmd,entering,condBypass | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condEnteringBypassValveFb | condEnteringBypassValveXXXXFb | Condenser Entering Bypass Valve Feedback | Condenser Entering Bypass Valve XX Feedback |  | condEnteringBypassValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | water,valve,position,sensor,entering,condBypass | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condEnteringFlow | condEnteringFlowXXXX | Condenser Entering Flow | Condenser Entering Flow XX |  | condEnteringFlow(\d{0,4}) | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,entering,flow,sensor | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condEnteringFlowDb | condEnteringFlowXXXXDb | Condenser Entering Flow Deadband | Condenser Entering Flow XX Deadband |  | condEnteringFlow(\d{0,4})Db | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,entering,flow,deadband,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condEnteringFlowHiSp | condEnteringFlowXXXXHiSp | Condenser Entering Flow High Setpoint | Condenser Entering Flow XX High Setpoint |  | condEnteringFlow(\d{0,4})HiSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,entering,flow,high,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condEnteringFlowLoSp | condEnteringFlowXXXXLoSp | Condenser Entering Flow Low Setpoint | Condenser Entering Flow XX Low Setpoint |  | condEnteringFlow(\d{0,4})LoSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,entering,flow,low,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condEnteringFlowMaxSp | condEnteringFlowXXXXMaxSp | Condenser Entering Flow Max Setpoint | Condenser Entering Flow XX Max Setpoint |  | condEnteringFlow(\d{0,4})MaxSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,entering,flow,max,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condEnteringFlowMinSp | condEnteringFlowXXXXMinSp | Condenser Entering Flow Min Setpoint | Condenser Entering Flow XX Min Setpoint |  | condEnteringFlow(\d{0,4})MinSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,entering,flow,min,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condEnteringFlowSp | condEnteringFlowXXXXSp | Condenser Entering Flow Setpoint | Condenser Entering Flow XX Setpoint |  | condEnteringFlow(\d{0,4})Sp | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,entering,flow,effective,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condEnteringFlowTotalizer | condEnteringFlowTotalizer | Condenser Entering Flow Totalizer | Condenser Entering Flow Totalizer |  | condEnteringFlowTotalizer | Yes | Yes | Yes | Number |  |  | gallon | liter | 0 | 0 |  |  | condensed,water,entering,flowConsumption,sensor | CLR,CWS,GEO,WS | 2.15 (Released),2.16 (Pre-Release)
condEnteringIsoValve | condEnteringIsoValveXXXX | Condenser Entering Isolation Valve Command | Condenser Entering Isolation Valve XX Command |  | condEnteringIsoValve(\d{0,4}) | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | condensed,water,entering,iso,valve,position,cmd | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condEnteringIsoValveFb | condEnteringIsoValveXXXXFb | Condenser Entering Isolation Valve Feedback | Condenser Entering Isolation Valve XX Feedback |  | condEnteringIsoValve(\d{0,4})Fb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | condensed,water,entering,iso,valve,position,sensor | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condEnteringIsoValveOvr | condEnteringIsoValveXXXXOvr | Condenser Entering Isolation Valve Override | Condenser Entering Isolation Valve XX Override |  | condEnteringIsoValve(\d{0,4})Ovr | No | No | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | condensed,water,entering,iso,valve,position,ovr | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condEnteringPressure | condEnteringPressureXXXX | Condenser Entering Pressure | Condenser Entering Pressure XX |  | condEnteringPressure(\d{0,4}) | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | condensed,water,entering,pressure,general,sensor | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condEnteringTemp | condEnteringTempXXXX | Condenser Entering Temperature | Condenser Entering Temperature XX |  | condEnteringTemp(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | condensed,water,entering,temp,sensor | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condEnteringTempDb | condEnteringTempXXXXDb | Condenser Entering Temperature Deadband | Condenser Entering Temperature XX Deadband |  | condEnteringTemp(\d{0,4})Db | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | condensed,water,entering,temp,deadband,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condEnteringTempHiAlarm | condEnteringTempXXXXHiAlarm | Condenser Entering Temperature High Alarm | Condenser Entering Temperature XX High Alarm |  | condEnteringTemp(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | condensed,water,entering,temp,high,alarm | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condEnteringTempHiSp | condEnteringTempXXXXHiSp | Condenser Entering Temperature High Setpoint | Condenser Entering Temperature XX High Setpoint |  | condEnteringTemp(\d{0,4})HiSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | condensed,water,entering,temp,high,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condEnteringTempLoAlarm | condEnteringTempXXXXLoAlarm | Condenser Entering Temperature Low Alarm | Condenser Entering Temperature XX Low Alarm |  | condEnteringTemp(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | condensed,water,entering,temp,low,alarm | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condEnteringTempLoSp | condEnteringTempXXXXLoSp | Condenser Entering Temperature Low Setpoint | Condenser Entering Temperature XX Low Setpoint |  | condEnteringTemp(\d{0,4})LoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | condensed,water,entering,temp,low,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condEnteringTempMaxSp | condEnteringTempXXXXMaxSp | Condenser Entering Temperature Max Setpoint | Condenser Entering Temperature XX Max Setpoint |  | condEnteringTemp(\d{0,4})MaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | condensed,water,entering,temp,max,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condEnteringTempMinSp | condEnteringTempXXXXMinSp | Condenser Entering Temperature Min Setpoint | Condenser Entering Temperature XX Min Setpoint |  | condEnteringTemp(\d{0,4})MinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | condensed,water,entering,temp,min,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condEnteringTempSp | condEnteringTempXXXXSp | Condenser Entering Temperature Setpoint | Condenser Entering Temperature XX Setpoint |  | condEnteringTemp(\d{0,4})Sp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | condensed,water,entering,temp,effective,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condEnteringTempSummerSp | condEnteringTempSummerSp | Condenser Entering Temperature Summer Setpoint | Condenser Entering Temperature Summer Setpoint |  | condEnteringTempSummerSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | condensed,water,entering,temp,summer,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condEnteringTempWinterSp | condEnteringTempWinterSp | Condenser Entering Temperature Winter Setpoint | Condenser Entering Temperature Winter Setpoint |  | condEnteringTempWinterSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | condensed,water,entering,temp,winter,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condEnteringValve | condEnteringValveXXXX | Condenser Entering Valve Command | Condenser Entering Valve XX Command |  | condEnteringValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | condensed,water,entering,common,valve,position,cmd | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condEnteringValveFb | condEnteringValveXXXXFb | Condenser Entering Valve Feedback | Condenser Entering Valve XX Feedback |  | condEnteringValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | condensed,water,entering,common,valve,position,sensor | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condFanAlarm | condXXXXFanYYYYAlarm | Condenser Fan Alarm | Condenser XX Fan YY Alarm |  | cond((?:(?!Fan)\w){0,4}(?=[A-Z]¦$))Fan(\w{0,4}(?=[A-Z]¦$))Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | condenser,air,fan,common,alarm | AHU,CLR,RTU,ODU | 2.15 (Released),2.16 (Pre-Release)
condFanAlarmReset | condXXXXFanYYYYAlarmReset | Condenser Fan Alarm Reset | Condenser XX Fan YY Alarm Reset |  | cond((?:(?!Fan)\w){0,4}(?=[A-Z]¦$))Fan(\w{0,4}(?=[A-Z]¦$))AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | condenser,air,fan,alarm,reset | AHU,CLR,RTU,ODU | 2.15 (Released),2.16 (Pre-Release)
condFan | condXXXXFanYYYY | Condenser Fan Command | Condenser XX Fan YY Command |  | cond((?:(?!Fan)\w){0,4}(?=[A-Z]¦$))Fan((?:(?!Ovr)\w){0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | condenser,air,fan,status,cmd | AHU,CLR,RTU,ODU | 2.15 (Released),2.16 (Pre-Release)
condFanCurrent | condXXXXFanYYYYCurrent | Condenser Fan Current | Condenser XX Fan YY Current |  | cond((?:(?!Fan)\w){0,4}(?=[A-Z]¦$))Fan(\w{0,4}(?=[A-Z]¦$))Current | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | condenser,air,fan,current,sensor | AHU,CLR,RTU,ODU | 2.15 (Released),2.16 (Pre-Release)
condFanDirection | condXXXXFanYYYYDirection | Condenser Fan Direction | Condenser XX Fan YY Direction |  | cond((?:(?!Fan)\w){0,4}(?=[A-Z]¦$))Fan(\w{0,4}(?=[A-Z]¦$))Direction | Yes | Yes | No | Bool | Forward/Reverse | Forward/Reverse | [6 empty] | condenser,air,fan,direction,cmd | AHU,CLR,RTU,ODU | 2.15 (Released),2.16 (Pre-Release)
condFanDirectionOvr | condXXXXFanYYYYDirectionOvr | Condenser Fan Direction Override | Condenser XX Fan YY Direction Override |  | cond((?:(?!Fan)\w){0,4}(?=[A-Z]¦$))Fan(\w{0,4}(?=[A-Z]¦$))DirectionOvr | Yes | Yes | No | Bool | Forward/Reverse | Forward/Reverse | [6 empty] | condenser,air,fan,direction,ovr | AHU,CLR,RTU,ODU | 2.15 (Released),2.16 (Pre-Release)
condFanDirectionStatus | condXXXXFanYYYYDirectionStatus | Condenser Fan Direction Status | Condenser XX Fan YY Direction Status |  | cond((?:(?!Fan)\w){0,4}(?=[A-Z]¦$))Fan(\w{0,4}(?=[A-Z]¦$))DirectionStatus | Yes | Yes | No | Bool | Forward/Reverse | Forward/Reverse | [6 empty] | condenser,air,fan,direction,sensor | AHU,CLR,RTU,ODU | 2.15 (Released),2.16 (Pre-Release)
condFanFault | condXXXXFanYYYYFault | Condenser Fan Fault | Condenser XX Fan YY Fault |  | cond((?:(?!Fan)\w){0,4}(?=[A-Z]¦$))Fan(\w{0,4}(?=[A-Z]¦$))Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | condenser,air,fan,fault | AHU,CLR,RTU,ODU | 2.15 (Released),2.16 (Pre-Release)
condFanMaintSwitch | condXXXXFanYYYYMaintSwitch | Condenser Fan Maintenance Switch | Condenser XX Fan YY Maintenance Switch |  | cond((?:(?!Fan)\w){0,4}(?=[A-Z]¦$))Fan(\w{0,4}(?=[A-Z]¦$))MaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | maintenance,switch,cmd,fan,air,condenser | AHU,CLR,RTU,ODU | 2.15 (Released),2.16 (Pre-Release)
condFanOvr | condXXXXFanYYYYOvr | Condenser Fan Override | Condenser XX Fan YY Override |  | cond((?:(?!Fan)\w){0,4}(?=[A-Z]¦$))Fan(\w{0,4}(?=[A-Z]¦$))Ovr | No | No | No | Bool | On/Off | On/Off | [6 empty] | condenser,air,fan,status,ovr | AHU,CLR,RTU,ODU | 2.15 (Released),2.16 (Pre-Release)
condFanRuntime | condXXXXFanYYYYRuntime | Condenser Fan Runtime | Condenser XX Fan YY Runtime |  | cond((?:(?!Fan)\w){0,4}(?=[A-Z]¦$))Fan(\w{0,4}(?=[A-Z]¦$))Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CLR,RTU,ODU | 2.15 (Released),2.16 (Pre-Release)
condFanSpeed | condXXXXFanYYYYSpeed | Condenser Fan Speed | Condenser XX Fan YY Speed |  | cond((?:(?!Fan)\w){0,4}(?=[A-Z]¦$))Fan(\w{0,4}(?=[A-Z]¦$))Speed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | condenser,air,fan,speed,cmd | AHU,CLR,RTU,ODU | 2.15 (Released),2.16 (Pre-Release)
condFanSpeedFb | condXXXXFanYYYYSpeedFb | Condenser Fan Speed Feedback | Condenser XX Fan YY Speed Feedback |  | cond((?:(?!Fan)\w){0,4}(?=[A-Z]¦$))Fan(\w{0,4}(?=[A-Z]¦$))SpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | condenser,air,fan,speed,sensor | AHU,CLR,RTU,ODU | 2.15 (Released),2.16 (Pre-Release)
condFanSpeedMaxSp | condXXXXFanYYYYSpeedMaxSp | Condenser Fan Speed Max Setpoint | Condenser XX Fan YY Speed Max Setpoint |  | cond((?:(?!Fan)\w){0,4}(?=[A-Z]¦$))Fan(\w{0,4}(?=[A-Z]¦$))SpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | condenser,air,fan,speed,max,sp | AHU,CLR,RTU,ODU | 2.15 (Released),2.16 (Pre-Release)
condFanSpeedMinSp | condXXXXFanYYYYSpeedMinSp | Condenser Fan Speed Min Setpoint | Condenser XX Fan YY Speed Min Setpoint |  | cond((?:(?!Fan)\w){0,4}(?=[A-Z]¦$))Fan(\w{0,4}(?=[A-Z]¦$))SpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | condenser,air,fan,speed,min,sp | AHU,CLR,RTU,ODU | 2.15 (Released),2.16 (Pre-Release)
condFanSpeedOvr | condXXXXFanYYYYSpeedOvr | Condenser Fan Speed Override | Condenser XX Fan YY Speed Override |  | cond((?:(?!Fan)\w){0,4}(?=[A-Z]¦$))Fan(\w{0,4}(?=[A-Z]¦$))SpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | condenser,air,fan,speed,ovr | AHU,CLR,RTU,ODU | 2.15 (Released),2.16 (Pre-Release)
condFanSpeedSp | condXXXXFanYYYYSpeedSp | Condenser Fan Speed Setpoint | Condenser XX Fan YY Speed Setpoint |  | cond((?:(?!Fan)\w){0,4}(?=[A-Z]¦$))Fan(\w{0,4}(?=[A-Z]¦$))SpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | condenser,air,fan,speed,effective,sp | AHU,CLR,RTU,ODU | 2.15 (Released),2.16 (Pre-Release)
condFanStatus | condXXXXFanYYYYStatus | Condenser Fan Status | Condenser XX Fan YY Status |  | cond((?:(?!Fan)\w){0,4}(?=[A-Z]¦$))Fan(\w{0,4}(?=[A-Z]¦$))Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | condenser,air,fan,status,sensor | AHU,CLR,RTU,ODU | 2.15 (Released),2.16 (Pre-Release)
condFilterAlarm | condFilterXXXXAlarm | Condenser Filter Alarm | Condenser Filter XX Alarm |  | condFilter(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | condensed,water,filter,general,alarm | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condFilterAlarmReset | condFilterXXXXAlarmReset | Condenser Filter Alarm Reset | Condenser Filter XX Alarm Reset |  | condFilter(\d{0,4})AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | condensed,water,filter,reset,alarm | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condFilterEnable | condFilterXXXXEnable | Condenser Filter Enable | Condenser Filter XX Enable |  | condFilter(\d{0,4})Enable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | condensed,water,filter,enable,cmd | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condFilterPressureDelta | condFilterXXXXPressureDelta | Condenser Filter Pressure Delta | Condenser Filter XX Pressure Delta |  | condFilter(\d{0,4})PressureDelta | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | condensed,water,filter,pressure,delta,sensor | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condFilterPump | condFilterXXXXPump | Condenser Filter Pump Command | Condenser Filter XX Pump Command |  | condFilter(\d{0,4})Pump | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | condensed,water,filter,pump,status,cmd | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condFilterPumpStatus | condFilterXXXXPumpStatus | Condenser Filter Pump Status | Condenser Filter XX Pump Status |  | condFilter(\d{0,4})PumpStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | condensed,water,filter,pump,status,sensor | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condFlowFault | condFlowXXXXFault | Condenser Flow Fault | Condenser Flow XX Fault |  | condFlow(\d{0,4})Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | condensed,water,flow,fault | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condFlowStatus | condFlowXXXXStatus | Condenser Flow Status | Condenser Flow XX Status |  | condFlow(\d{0,4})Status | Yes | Yes | No | Bool | Flow/No Flow | Flow/No Flow | [6 empty] | condensed,water,status,flow,sensor | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condLeavingBypassValve | condLeavingBypassValveXXXX | Condenser Leaving Bypass Valve Command | Condenser Leaving Bypass Valve XX Command |  | condLeavingBypassValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | water,bypass,valve,position,cmd,leaving,condBypass | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condLeavingBypassValveFb | condLeavingBypassValveXXXXFb | Condenser Leaving Bypass Valve Feedback | Condenser Leaving Bypass Valve XX Feedback |  | condLeavingBypassValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | water,bypass,valve,position,sensor,leaving,condBypass | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condLeavingFlow | condLeavingFlowXXXX | Condenser Leaving Flow | Condenser Leaving Flow XX |  | condLeavingFlow(\d{0,4}) | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,leaving,flow,sensor | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condLeavingFlowDb | condLeavingFlowXXXXDb | Condenser Leaving Flow Deadband | Condenser Leaving Flow XX Deadband |  | condLeavingFlow(\d{0,4})Db | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,leaving,flow,deadband,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condLeavingFlowHiSp | condLeavingFlowXXXXHiSp | Condenser Leaving Flow High Setpoint | Condenser Leaving Flow XX High Setpoint |  | condLeavingFlow(\d{0,4})HiSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,leaving,flow,high,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condLeavingFlowLoSp | condLeavingFlowXXXXLoSp | Condenser Leaving Flow Low Setpoint | Condenser Leaving Flow XX Low Setpoint |  | condLeavingFlow(\d{0,4})LoSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,leaving,flow,low,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condLeavingFlowMaxSp | condLeavingFlowXXXXMaxSp | Condenser Leaving Flow Max Setpoint | Condenser Leaving Flow XX Max Setpoint |  | condLeavingFlow(\d{0,4})MaxSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,leaving,flow,max,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condLeavingFlowMinSp | condLeavingFlowXXXXMinSp | Condenser Leaving Flow Min Setpoint | Condenser Leaving Flow XX Min Setpoint |  | condLeavingFlow(\d{0,4})MinSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,leaving,flow,min,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condLeavingFlowSp | condLeavingFlowXXXXSp | Condenser Leaving Flow Setpoint | Condenser Leaving Flow XX Setpoint |  | condLeavingFlow(\d{0,4})Sp | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,leaving,flow,effective,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condLeavingFlowTotalizer | condLeavingFlowTotalizer | Condenser Leaving Flow Totalizer | Condenser Leaving Flow Totalizer |  | condLeavingFlowTotalizer | Yes | Yes | Yes | Number |  |  | gallon | liter | 0 | 0 |  |  | condensed,water,leaving,flowConsumption,sensor | CLR,CWS,GEO,WS | 2.15 (Released),2.16 (Pre-Release)
condLeavingIsoValve | condLeavingIsoValveXXXX | Condenser Leaving Isolation Valve Command | Condenser Leaving Isolation Valve XX Command |  | condLeavingIsoValve(\d{0,4}) | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | condensed,water,leaving,iso,valve,position,cmd | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condLeavingIsoValveFb | condLeavingIsoValveXXXXFb | Condenser Leaving Isolation Valve Feedback | Condenser Leaving Isolation Valve XX Feedback |  | condLeavingIsoValve(\d{0,4})Fb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | condensed,water,leaving,iso,valve,position,sensor | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condLeavingIsoValveOvr | condLeavingIsoValveXXXXOvr | Condenser Leaving Isolation Valve Override | Condenser Leaving Isolation Valve XX Override |  | condLeavingIsoValve(\d{0,4})Ovr | No | No | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | condensed,water,leaving,iso,valve,position,ovr | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condLeavingPressure | condLeavingPressureXXXX | Condenser Leaving Pressure | Condenser Leaving Pressure XX |  | condLeavingPressure(\d{0,4}) | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | condensed,water,leaving,pressure,general,sensor | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condLeavingTemp | condLeavingTempXXXX | Condenser Leaving Temperature | Condenser Leaving Temperature XX |  | condLeavingTemp(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | condensed,water,leaving,temp,sensor | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condLeavingTempDb | condLeavingTempXXXXDb | Condenser Leaving Temperature Deadband | Condenser Leaving Temperature XX Deadband |  | condLeavingTemp(\d{0,4})Db | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | condensed,water,leaving,temp,deadband,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condLeavingTempHiSp | condLeavingTempXXXXHiSp | Condenser Leaving Temperature High Setpoint | Condenser Leaving Temperature XX High Setpoint |  | condLeavingTemp(\d{0,4})HiSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | condensed,water,leaving,temp,high,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condLeavingTempLoSp | condLeavingTempXXXXLoSp | Condenser Leaving Temperature Low Setpoint | Condenser Leaving Temperature XX Low Setpoint |  | condLeavingTemp(\d{0,4})LoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | condensed,water,leaving,temp,low,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condLeavingTempMaxSp | condLeavingTempXXXXMaxSp | Condenser Leaving Temperature Max Setpoint | Condenser Leaving Temperature XX Max Setpoint |  | condLeavingTemp(\d{0,4})MaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | condensed,water,leaving,temp,max,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condLeavingTempMinSp | condLeavingTempXXXXMinSp | Condenser Leaving Temperature Min Setpoint | Condenser Leaving Temperature XX Min Setpoint |  | condLeavingTemp(\d{0,4})MinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | condensed,water,leaving,temp,min,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condLeavingTempSp | condLeavingTempXXXXSp | Condenser Leaving Temperature Setpoint | Condenser Leaving Temperature XX Setpoint |  | condLeavingTemp(\d{0,4})Sp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | condensed,water,leaving,temp,effective,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condLeavingTempSummerSp | condLeavingTempSummerSp | Condenser Leaving Temperature Summer Setpoint | Condenser Leaving Temperature Summer Setpoint |  | condLeavingTempSummerSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | condensed,water,leaving,temp,summer,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condLeavingTempWinterSp | condLeavingTempWinterSp | Condenser Leaving Temperature Winter Setpoint | Condenser Leaving Temperature Winter Setpoint |  | condLeavingTempWinterSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | condensed,water,leaving,temp,winter,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condLeavingValve | condLeavingValveXXXX | Condenser Leaving Valve Command | Condenser Leaving Valve XX Command |  | condLeavingValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | condensed,water,leaving,common,valve,position,cmd | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condLeavingValveFb | condLeavingValveXXXXFb | Condenser Leaving Valve Feedback | Condenser Leaving Valve XX Feedback |  | condLeavingValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | condensed,water,leaving,common,valve,position,sensor | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condLoad | condXXXXLoad | Condenser Load | Condenser XX Load |  | cond(\d{0,4})Load | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | condensed,load,sensor | AHU,CLR,CWS,GEO,RTU,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condPower | condPower | Condenser Power | Condenser Power |  | condPower | Yes | Yes | No | Number |  |  | kilobtus_per_hour | kilobtus_per_hour | 1 | 1 |  |  | condensed,water,power,common,sensor | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condPressureDelta | condPressureDelta | Condenser Pressure Differential | Condenser Pressure Differential |  | condPressureDelta | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | condensed,water,common,delta,pressure,general,sensor | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condPressureDeltaDb | condPressureDeltaDb | Condenser Pressure Differential Deadband | Condenser Pressure Differential Deadband |  | condPressureDeltaDb | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | condensed,water,common,delta,pressure,deadband,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condPressureDeltaHiSp | condPressureDeltaHiSp | Condenser Pressure Differential High Setpoint | Condenser Pressure Differential High Setpoint |  | condPressureDeltaHiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | condensed,water,common,delta,pressure,high,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condPressureDeltaLoSp | condPressureDeltaLoSp | Condenser Pressure Differential Low Setpoint | Condenser Pressure Differential Low Setpoint |  | condPressureDeltaLoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | condensed,water,common,delta,pressure,low,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condPressureDeltaMaxSp | condPressureDeltaMaxSp | Condenser Pressure Differential Max Setpoint | Condenser Pressure Differential Max Setpoint |  | condPressureDeltaMaxSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | condensed,water,common,delta,pressure,max,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condPressureDeltaMinSp | condPressureDeltaMinSp | Condenser Pressure Differential Min Setpoint | Condenser Pressure Differential Min Setpoint |  | condPressureDeltaMinSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | condensed,water,common,delta,pressure,min,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condPressureDeltaSp | condPressureDeltaSp | Condenser Pressure Differential Setpoint | Condenser Pressure Differential Setpoint |  | condPressureDeltaSp | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | condensed,water,common,delta,pressure,effective,sp | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condPumpAlarm | condPumpXXXXAlarm | Condenser Pump Alarm | Condenser Pump XX Alarm |  | condPump(\w{0,4}(?=[A-Z]¦$))Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | condenser,water,pump,common,alarm | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condPumpAlarmReset | condPumpXXXXAlarmReset | Condenser Pump Alarm Reset | Condenser Pump XX Alarm Reset |  | condPump(\w{0,4}(?=[A-Z]¦$))AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | condenser,water,pump,reset,alarm | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condPump | condPumpXXXX | Condenser Pump Command | Condenser Pump XX Command |  | condPump((?:(?!Lead)(?!Ovr)\w){0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | condenser,water,pump,status,cmd | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condPumpCurrent | condPumpXXXXCurrent | Condenser Pump Current | Condenser Pump XX Current |  | condPump(\w{0,4}(?=[A-Z]¦$))Current | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | condenser,water,pump,current,sensor | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condPumpDirectionOvr | condPumpXXXXDirectionOvr | Condenser Pump Direction Override | Condenser Pump XX Direction Override |  | condPump(\w{0,4}(?=[A-Z]¦$))DirectionOvr | Yes | Yes | No | Bool | Forward/Reverse | Forward/Reverse | [6 empty] | condenser,water,pump,direction,cmd | CLR,CWS,GEO,WS | 2.15 (Released)
condPumpDirectionStatus | condPumpXXXXDirectionStatus | Condenser Pump Direction Status | Condenser Pump XX Direction Status |  | condPump(\w{0,4}(?=[A-Z]¦$))DirectionStatus | Yes | Yes | No | Bool | Forward/Reverse | Forward/Reverse | [6 empty] | condenser,water,pump,direction,sensor | CLR,CWS,GEO,WS | 2.15 (Released)
condPumpEnable | condPumpXXXXEnable | Condenser Pump Enable | Condenser Pump XX Enable |  | condPump(\w{0,4}(?=[A-Z]¦$))Enable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | condenser,water,pump,enable,cmd | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condPumpEnableDb | condPumpXXXXEnableDb | Condenser Pump Enable Deadband | Condenser Pump XX Enable Deadband |  | condPump(\w{0,4}(?=[A-Z]¦$))EnableDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | condenser,water,pump,enable,deadband,sp | CLR,CWS,GEO,WS | 2.15 (Released),2.16 (Pre-Release)
condPumpEnableSp | condPumpXXXXEnableSp | Condenser Pump Enable Setpoint | Condenser Pump XX Enable Setpoint |  | condPump((?:(?!Lag)\w){0,4}(?=[A-Z]¦$))EnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | condenser,water,pump,enable,effective,sp | CLR,CWS,GEO,WS | 2.15 (Released),2.16 (Pre-Release)
condPumpEnteringPressure | condPumpXXXXEnteringPressure | Condenser Pump Entering Pressure | Condenser Pump XX Entering Pressure |  | condPump(\w{0,4}(?=[A-Z]¦$))EnteringPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | condenser,water,pump,entering,pressure,sensor | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condPumpFault | condPumpXXXXFault | Condenser Pump Fault | Condenser Pump XX Fault |  | condPump(\w{0,4}(?=[A-Z]¦$))Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | condenser,water,pump,fault,common | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condPumpLagDisableSp | condPumpXXXXLagDisableSp | Condenser Pump Lag Disable Setpoint | Condenser Pump XX Lag Disable Setpoint |  | condPump(\w{0,4}(?=[A-Z]¦$))LagDisableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | condenser,water,pump,lag,disable,sp | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condPumpLagEnableSp | condPumpXXXXLagEnableSp | Condenser Pump Lag Enable Setpoint | Condenser Pump XX Lag Enable Setpoint |  | condPump(\w{0,4}(?=[A-Z]¦$))LagEnableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | condenser,water,pump,lag,enable,sp | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condPumpLagReq | condPumpXXXXLagReq | Condenser Pump Lag Request | Condenser Pump XX Lag Request |  | condPump(\w{0,4}(?=[A-Z]¦$))LagReq | No | No | No | Bool | Request/No Request | Request/No Request | [6 empty] | condenser,water,pump,lag,request,cmd | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condPumpLead | condPumpLead | Condenser Pump Lead | Condenser Pump Lead |  | condPumpLead | Yes | Yes | No | Bool | Lead 1/Lead 2 | Lead 1/Lead 2 | [6 empty] | condenser,water,pump,lead,sp | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condPumpLeadXor | condPumpLeadXor | Condenser Pump Lead Change Over | Condenser Pump Lead Change Over |  | condPumpLeadXor | No | No | No | Bool | On/Off | On/Off | [6 empty] | condenser,water,pump,lead,changeOver,common,cmd | CLR,CWS,GEO,WS | 2.15 (Released),2.16 (Pre-Release)
condPumpLeadXorDay | condPumpLeadXorDay | Condenser Pump Lead Change Over Day | Condenser Pump Lead Change Over Day |  | condPumpLeadXorDay | No | No | No | Number |  | Sun,Mon,Tue,Wed,Thur,Fri,Sat | day | day | 0 | 0 |  |  | condenser,water,pump,lead,changeOver,day,cmd | CLR,CWS,GEO,WS | 2.15 (Released),2.16 (Pre-Release)
condPumpLeadXorHour | condPumpLeadXorHour | Condenser Pump Lead Change Over Hour | Condenser Pump Lead Change Over Hour |  | condPumpLeadXorHour | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | condenser,water,pump,lead,changeOver,hour,cmd | CLR,CWS,GEO,WS | 2.15 (Released),2.16 (Pre-Release)
condPumpLeadXorMode | condPumpLeadXorMode | Condenser Pump Lead Change Over Mode | Condenser Pump Lead Change Over Mode |  | condPumpLeadXorMode | No | No | No | Str |  | 1Week/2Week/3Week/4Week | [6 empty] | condenser,water,pump,lead,changeOver,mode,cmd | CLR,CWS,GEO,WS | 2.15 (Released),2.16 (Pre-Release)
condPumpLeadXorRuntimeSp | condPumpLeadXorRuntimeSp | Condenser Pump Lead Change Over Runtime Setpoint | Condenser Pump Lead Change Over Runtime Setpoint |  | condPumpLeadXorRuntimeSp | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condPumpLeavingPressure | condPumpXXXXLeavingPressure | Condenser Pump Leaving Pressure | Condenser Pump XX Leaving Pressure |  | condPump(\w{0,4}(?=[A-Z]¦$))LeavingPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | condenser,water,pump,leaving,pressure,sensor | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condPumpMaintSwitch | condPumpXXXXMaintSwitch | Condenser Pump Maintenance Switch | Condenser Pump XX Maintenance Switch |  | condPump(\w{0,4}(?=[A-Z]¦$))MaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | condensed,water,pump,maintenance,switch,cmd | CLR,CWS,GEO,WS | 2.15 (Released),2.16 (Pre-Release)
condPumpOvr | condPumpXXXXOvr | Condenser Pump Override | Condenser Pump XX Override |  | condPump(\w{0,4}(?=[A-Z]¦$))Ovr | No | No | No | Bool | On/Off | On/Off | [6 empty] | condenser,water,pump,status,ovr | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condPumpPressureDelta | condPumpXXXXPressureDelta | Condenser Pump Pressure Delta | Condenser Pump XX Pressure Delta |  | condPump(\w{0,4}(?=[A-Z]¦$))PressureDelta | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | condenser,water,pump,common,pressure,delta,sensor | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condPumpPressureHiAlarm | condPumpXXXXPressureHiAlarm | Condenser Pump Pressure High Alarm | Condenser Pump XX Pressure High Alarm |  | condPump(\w{0,4}(?=[A-Z]¦$))PressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | condenser,water,pump,pressure,high,alarm | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condPumpPressureHiSp | condPumpXXXXPressureHiSp | Condenser Pump Pressure High Setpoint | Condenser Pump XX Pressure High Setpoint |  | condPump(\w{0,4}(?=[A-Z]¦$))PressureHiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | condenser,water,pump,pressure,high,sp | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condPumpPressureLoAlarm | condPumpXXXXPressureLoAlarm | Condenser Pump Pressure Low Alarm | Condenser Pump XX Pressure Low Alarm |  | condPump(\w{0,4}(?=[A-Z]¦$))PressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | condenser,water,pump,pressure,low,alarm | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condPumpPressureLoSp | condPumpXXXXPressureLoSp | Condenser Pump Pressure Low Setpoint | Condenser Pump XX Pressure Low Setpoint |  | condPump(\w{0,4}(?=[A-Z]¦$))PressureLoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | condenser,water,pump,pressure,low,sp | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condPumpRuntime | condPumpXXXXRuntime | Condenser Pump Runtime | Condenser Pump XX Runtime |  | condPump(\w{0,4}(?=[A-Z]¦$))Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | CLR,CWS,GEO,WS | 2.15 (Released),2.16 (Pre-Release)
condPumpSpeed | condPumpXXXXSpeed | Condenser Pump Speed | Condenser Pump XX Speed |  | condPump(\w{0,4}(?=[A-Z]¦$))Speed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | condenser,water,pump,speed,cmd | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condPumpSpeedFb | condPumpXXXXSpeedFb | Condenser Pump Speed Feedback | Condenser Pump XX Speed Feedback |  | condPump(\w{0,4}(?=[A-Z]¦$))SpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | condenser,water,pump,speed,sensor | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condPumpSpeedMaxSp | condPumpXXXXSpeedMaxSp | Condenser Pump Speed Max Setpoint | Condenser Pump XX Speed Max Setpoint |  | condPump(\w{0,4}(?=[A-Z]¦$))SpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | condenser,water,pump,speed,max,sp | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condPumpSpeedMinSp | condPumpXXXXSpeedMinSp | Condenser Pump Speed Min Setpoint | Condenser Pump XX Speed Min Setpoint |  | condPump(\w{0,4}(?=[A-Z]¦$))SpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | condenser,water,pump,speed,min,sp | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condPumpSpeedOvr | condPumpXXXXSpeedOvr | Condenser Pump Speed Override | Condenser Pump XX Speed Override |  | condPump(\w{0,4}(?=[A-Z]¦$))SpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | condenser,water,pump,speed,ovr | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condPumpSpeedSp | condPumpXXXXSpeedSp | Condenser Pump Speed Setpoint | Condenser Pump XX Speed Setpoint |  | condPump(\w{0,4}(?=[A-Z]¦$))SpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | condenser,water,pump,speed,effective,sp | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condPumpStageDownDelayOnSp | condPumpStageDownDelayOnSp | Condenser Pump Stage Down Delay On Setpoint | Condenser Pump Stage Down Delay On Setpoint |  | condPumpStageDownDelayOnSp | No | No | No | Number |  |  | minute | minute | 0 | 0 |  |  | condenser,water,pump,stageDown,delay,on,sp | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condPumpStageDownSp | condPumpStageDownSp | Condenser Pump Stage Down Setpoint | Condenser Pump Stage Down Setpoint |  | condPumpStageDownSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | condenser,water,pump,stageDown,effective,sp | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condPumpStageUpDelayOnSp | condPumpStageUpDelayOnSp | Condenser Pump Stage Up Delay On Setpoint | Condenser Pump Stage Up Delay On Setpoint |  | condPumpStageUpDelayOnSp | No | No | No | Number |  |  | minute | minute | 0 | 0 |  |  | condenser,water,pump,stageUp,delay,on,sp | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condPumpStageUpSp | condPumpStageUpSp | Condenser Pump Stage Up Setpoint | Condenser Pump Stage Up Setpoint |  | condPumpStageUpSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | condenser,water,pump,stageUp,effective,sp | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condPumpStatus | condPumpXXXXStatus | Condenser Pump Status | Condenser Pump XX Status |  | condPump(\w{0,4}(?=[A-Z]¦$))Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | condenser,water,pump,status,sensor | CLR,CWS,GEO,WS | 2.14,2.15 (Released),2.16 (Pre-Release)
condStatus | condXXXXStatus | Condenser Status | Condenser XX Status |  | cond(\d{0,4})Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | condensed,common,status,sensor | AHU,CLR,CWS,GEO,RTU,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condStrainerAlarm | condXXXXStrainerAlarm | Condenser Strainer Alarm | Condenser XX Strainer Alarm |  | cond(\d{0,4})StrainerAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | condensed,water,strainer,alarm | AHU,CLR,CWS,GEO,RTU,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condStrainerEnable | condXXXXStrainerEnable | Condenser Strainer Enable | Condenser XX Strainer Enable |  | cond(\d{0,4})StrainerEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | condensed,water,strainer,enable,cmd | AHU,CLR,CWS,GEO,RTU,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
condTempDelta | condTempDelta | Condenser Temperature Delta | Condenser Temperature Delta |  | condTempDelta | Yes | Yes | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | condensed,water,delta,temp,sensor | CLR,CWS,GEO,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
contaminantThicknessAlarm | contaminantThicknessAlarm | Contaminant Thickness Alarm | Contaminant Thickness Alarm |  | contaminantThicknessAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | contaminant,thickness,alarm | FSEP,GINT,PINT | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
controlDamperSource | controlDamperSource | Control Damper Source | Control Damper Source |  | controlDamperSource | No | No | No | Str |  | Manual/Pressure | [6 empty] | blacklist | AC,AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,ERU,FCU,FPB,HP,HRU,MAU,RTU,UV,VAV,VRF,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
controlHumiditySource | controlHumiditySource | Control Humidity Source | Control Humidity Source |  | controlHumiditySource | No | No | No | Str | Return/Zone | Return/Zone | [6 empty] | blacklist | AC,AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,ERU,FCU,FPB,HP,HRU,MAU,RTU,UV,VAV,VRF,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
controlHvacModeSource | controlHvacModeSource | Control HVAC Mode Source | Control HVAC Mode Source |  | controlHvacModeSource | No | No | No | Bool | BAS/Local | BAS/Local | [6 empty] | blacklist | AC,AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,ERU,FCU,FPB,HP,HRU,MAU,RTU,UV,VAV,VRF,FCU,HP | 2.14,2.15 (Released),2.16 (Pre-Release)
controlOccSource | controlOccSource | Control Occupancy Source | Control Occupancy Source |  | controlOccSource | No | No | No | Str | BAS/Local | BAS/Local | [6 empty] | blacklist | AC,AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,ERU,FCU,FPB,HP,HRU,MAU,RTU,UV,VAV,VRF,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
controlPressureSource | controlPressureSource | Control Pressure Source | Control Pressure Source |  | controlPressureSource | No | No | No | Str | BAS/Local | BAS/Local | [6 empty] | blacklist | AC,AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,ERU,FCU,FPB,HP,HRU,MAU,RTU,UV,VAV,VRF,FCU,HP | 2.14,2.15 (Released),2.16 (Pre-Release)
controlPressureSourceOvr | controlPressureSourceOvr | Control Pressure Source Override | Control Pressure Source Override |  | controlPressureSourceOvr | No | No | No | Str | BAS/Local | BAS/Local | [6 empty] | blacklist | AC,AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,ERU,FCU,FPB,HP,HRU,MAU,RTU,UV,VAV,VRF,FCU,HP | 2.14,2.15 (Released),2.16 (Pre-Release)
controlSpeedSource | controlSpeedSource | Control Speed Source | Control Speed Source |  | controlSpeedSource | No | No | No | Str | BAS/Local | BAS/Local | [6 empty] | blacklist | AC,AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,ERU,FCU,FPB,HP,HRU,MAU,RTU,UV,VAV,VRF,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
controlTemp | controlTemp | Control Temperature | Control Temperature |  | controlTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | blacklist | AC,AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,ERU,FCU,FPB,HP,HRU,MAU,RTU,UV,VAV,VRF,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
controlTempSpSource | controlTempSpSource | Control Temperature Setpoint Source | Control Temperature Setpoint Source |  | controlTempSpSource | No | No | No | Str | BAS/Local | BAS/Local | [6 empty] | blacklist | AC,AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,ERU,FCU,FPB,HP,HRU,MAU,RTU,UV,VAV,VRF,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
controlTempSource | controlTempSource | Control Temperature Source | Control Temperature Source |  | controlTempSource | No | No | No | Str | Return/Zone | Return/Zone | [6 empty] | blacklist | AC,AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,ERU,FCU,FPB,HP,HRU,MAU,RTU,UV,VAV,VRF,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
controlUnitEnableSource | controlUnitEnableSource | Control Unit Enable Source | Control Unit Enable Source |  | controlUnitEnableSource | No | No | No | Bool | BAS/Local | BAS/Local | [6 empty] | blacklist | AC,AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,ERU,FCU,FPB,HP,HRU,MAU,RTU,UV,VAV,VRF,FCU,HP | 2.14,2.15 (Released),2.16 (Pre-Release)
coolantFilterPressureDelta | coolantFilterPressureDelta | Coolant Filter Pressure Differential | Coolant Filter Pressure Differential |  | coolantFilterPressureDelta | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | coolant,filter,pressure,delta,sensor | CMP,GEN | 2.12,2.13,2.14,2.15 (Released)
coolantLevel | coolantLevel | Coolant Level | Coolant Level |  | coolantLevel | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | coolant,level,sensor | CMP,GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolantLevelLoAlarm | coolantLevelLoAlarm | Coolant Level Low Alarm | Coolant Level Low Alarm |  | coolantLevelLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | coolant,level,low,alarm | CMP,GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolantTemp | coolantTemp | Coolant Temperature | Coolant Temperature |  | coolantTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | coolant,temp,sensor | CMP,GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolantTempFault | coolantTempFault | Coolant Temperature Fault | Coolant Temperature Fault |  | coolantTempFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | coolant,temp,fault | CMP,GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolantTempHiAlarm | coolantTempHiAlarm | Coolant Temperature High Alarm | Coolant Temperature High Alarm |  | coolantTempHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | coolant,temp,high,alarm | CMP,GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolantTempLoAlarm | coolantTempLoAlarm | Coolant Temperature Low Alarm | Coolant Temperature Low Alarm |  | coolantTempLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | coolant,temp,low,alarm | CMP,GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolerEnteringPressure | coolerEnteringPressure | Cooler Entering Pressure | Cooler Entering Pressure |  | coolerEnteringPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | cooler,entering,pressure,sensor | CMP,GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolerEnteringTemp | coolerEnteringTemp | Cooler Entering Temperature | Cooler Entering Temperature |  | coolerEnteringTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | cooler,entering,temp,sensor | CMP,GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolerLeavingPressure | coolerLeavingPressure | Cooler Leaving Pressure | Cooler Leaving Pressure |  | coolerLeavingPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | cooler,leaving,pressure,sensor | CMP,GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolerLeavingTemp | coolerLeavingTemp | Cooler Leaving Temperature | Cooler Leaving Temperature |  | coolerLeavingTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | cooler,leaving,temp,sensor | CMP,GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCapacityMaxSp | coolingCapacityMaxSp | Cooling Capacity Max Setpoint | Cooling Capacity Max Setpoint |  | coolingCapacityMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | cool,demand,max,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilDischargeHumidity | coolingCoilXXXXDischargeHumidity | Cooling Coil Discharge Humidity | Cooling Coil XX Discharge Humidity |  | coolingCoil(\d{0,4})DischargeHumidity | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | cool,coil,air,discharge,humidity,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilDischargeTemp | coolingCoilXXXXDischargeTemp | Cooling Coil Discharge Temperature | Cooling Coil XX Discharge Temperature |  | coolingCoil(\d{0,4})DischargeTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | cool,coil,air,discharge,temp,sensor | AFMS,AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilDischargeTempDb | coolingCoilXXXXDischargeTempDb | Cooling Coil Discharge Temperature Deadband | Cooling Coil XX Discharge Temperature Deadband |  | coolingCoil(\d{0,4})DischargeTempDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | cool,coil,air,discharge,temp,deadband,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilDischargeTempHiSp | coolingCoilXXXXDischargeTempHiSp | Cooling Coil Discharge Temperature High Setpoint | Cooling Coil XX Discharge Temperature High Setpoint |  | coolingCoil(\d{0,4})DischargeTempHiSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | cool,coil,air,discharge,temp,high,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilDischargeTempLoSp | coolingCoilXXXXDischargeTempLoSp | Cooling Coil Discharge Temperature Low Setpoint | Cooling Coil XX Discharge Temperature Low Setpoint |  | coolingCoil(\d{0,4})DischargeTempLoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | cool,coil,air,discharge,temp,low,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilDischargeTempMaxSp | coolingCoilXXXXDischargeTempMaxSp | Cooling Coil Discharge Temperature Max Setpoint | Cooling Coil XX Discharge Temperature Max Setpoint |  | coolingCoil(\d{0,4})DischargeTempMaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | cool,coil,air,discharge,temp,max,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilDischargeTempMinSp | coolingCoilXXXXDischargeTempMinSp | Cooling Coil Discharge Temperature Min Setpoint | Cooling Coil XX Discharge Temperature Min Setpoint |  | coolingCoil(\d{0,4})DischargeTempMinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | cool,coil,air,discharge,temp,min,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilDischargeTempSp | coolingCoilXXXXDischargeTempSp | Cooling Coil Discharge Temperature Setpoint | Cooling Coil XX Discharge Temperature Setpoint |  | coolingCoil(\d{0,4})DischargeTempSp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | cool,coil,air,discharge,temp,effective,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilEnergy | coolingCoilXXXXEnergy | Cooling Coil Energy | Cooling Coil XX Energy |  | coolingCoil(\d{0,4})Energy | Yes | Yes | No | Number |  |  | tons_refrigeration_hour | tons_refrigeration_hour | 0 | 0 |  |  | cool,coil,water,energy,common,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilEnteringPressure | coolingCoilXXXXEnteringPressure | Cooling Coil Entering Pressure | Cooling Coil XX Entering Pressure |  | coolingCoil(\d{0,4})EnteringPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | cool,coil,water,entering,pressure,general,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilEnteringTemp | coolingCoilXXXXEnteringTemp | Cooling Coil Entering Temperature | Cooling Coil XX Entering Temperature |  | coolingCoil(\d{0,4})EnteringTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | cool,coil,water,entering,temp,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilFilterAlarm | coolingCoilXXXXFilterAlarm | Cooling Coil Filter Alarm | Cooling Coil XX Filter Alarm |  | coolingCoil(\d{0,4})FilterAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | cool,coil,air,filter,general,alarm | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilFilterAlarmReset | coolingCoilXXXXFilterAlarmReset | Cooling Coil Filter Alarm Reset | Cooling Coil XX Filter Alarm Reset |  | coolingCoil(\d{0,4})FilterAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | cool,coil,air,filter,reset,alarm | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilFilterPressureDelta | coolingCoilXXXXFilterPressureDelta | Cooling Coil Filter Pressure Delta | Cooling Coil XX Filter Pressure Delta |  | coolingCoil(\d{0,4})FilterPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | cool,coil,air,filter,pressure,delta,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released)
coolingCoilFilterRuntime | coolingCoilXXXXFilterRuntime | Cooling Coil Filter Runtime | Cooling Coil XX Filter Runtime |  | coolingCoil(\d{0,4})FilterRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.15 (Released),2.16 (Pre-Release)
coolingCoilFlow | coolingCoilXXXXFlow | Cooling Coil Flow | Cooling Coil XX Flow |  | coolingCoil(\d{0,4})Flow | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | cool,coil,water,flow,status,cmd | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilFlowStatus | coolingCoilXXXXFlowStatus | Cooling Coil Flow Status | Cooling Coil XX Flow Status |  | coolingCoil(\d{0,4})FlowStatus | Yes | Yes | No | Bool | Flow/No Flow | Flow/No Flow | [6 empty] | cool,coil,water,flow,status,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilLeavingPressure | coolingCoilXXXXLeavingPressure | Cooling Coil Leaving Pressure | Cooling Coil XX Leaving Pressure |  | coolingCoil(\d{0,4})LeavingPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | cool,coil,water,leaving,pressure,general,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilLeavingTemp | coolingCoilXXXXLeavingTemp | Cooling Coil Leaving Temperature | Cooling Coil XX Leaving Temperature |  | coolingCoil(\d{0,4})LeavingTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | cool,coil,water,leaving,temp,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilPower | coolingCoilXXXXPower | Cooling Coil Power | Cooling Coil XX Power |  | coolingCoil(\d{0,4})Power | Yes | Yes | No | Number |  |  | tons_refrigeration | tons_refrigeration | 1 | 1 |  |  | cool,coil,water,power,common,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilPumpAlarm | coolingCoilXXXXPumpAlarm | Cooling Coil Pump Alarm | Cooling Coil XX Pump Alarm |  | coolingCoil(\d{0,4})PumpAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | cool,coil,water,pump,common,alarm | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilPumpAlarmReset | coolingCoilXXXXPumpAlarmReset | Cooling Coil Pump Alarm Reset | Cooling Coil XX Pump Alarm Reset |  | coolingCoil(\d{0,4})PumpAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | cool,coil,water,pump,reset,alarm | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilPump | coolingCoilXXXXPump | Cooling Coil Pump Command | Cooling Coil XX Pump Command |  | coolingCoil(\d{0,4})Pump | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | cool,coil,water,pump,status,cmd | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilPumpCurrent | coolingCoilXXXXPumpCurrent | Cooling Coil Pump Current | Cooling Coil XX Pump Current |  | coolingCoil(\d{0,4})PumpCurrent | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | cool,coil,water,pump,current,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilPumpEnable | coolingCoilXXXXPumpEnable | Cooling Coil Pump Enable | Cooling Coil XX Pump Enable |  | coolingCoil(\d{0,4})PumpEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | cool,coil,water,pump,enable,cmd | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilPumpEnableDb | coolingCoilXXXXPumpEnableDb | Cooling Coil Pump Enable Deadband | Cooling Coil XX Pump Enable Deadband |  | coolingCoil(\d{0,4})PumpEnableDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | cool,coil,water,pump,enable,deadband,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.15 (Released),2.16 (Pre-Release)
coolingCoilPumpEnableSp | coolingCoilXXXXPumpEnableSp | Cooling Coil Pump Enable Setpoint | Cooling Coil XX Pump Enable Setpoint |  | coolingCoil(\d{0,4})PumpEnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | cool,coil,water,pump,enable,effective,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.15 (Released),2.16 (Pre-Release)
coolingCoilPumpEnteringPressure | coolingCoilXXXXPumpEnteringPressure | Cooling Coil Pump Entering Pressure | Cooling Coil XX Pump Entering Pressure |  | coolingCoil(\d{0,4})PumpEnteringPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | cool,coil,water,pump,entering,pressure,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilPumpFault | coolingCoilXXXXPumpFault | Cooling Coil Pump Fault | Cooling Coil XX Pump Fault |  | coolingCoil(\d{0,4})PumpFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | cool,coil,water,pump,fault,common | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilPumpLagDisableSp | coolingCoilXXXXPumpLagDisableSp | Cooling Coil Pump Lag Disable Setpoint | Cooling Coil XX Pump Lag Disable Setpoint |  | coolingCoil(\d{0,4})PumpLagDisableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | cool,coil,water,pump,lag,disable,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilPumpLagEnableSp | coolingCoilXXXXPumpLagEnableSp | Cooling Coil Pump Lag Enable Setpoint | Cooling Coil XX Pump Lag Enable Setpoint |  | coolingCoil(\d{0,4})PumpLagEnableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | cool,coil,water,pump,lag,enable,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilPumpLagReq | coolingCoilXXXXPumpLagReq | Cooling Coil Pump Lag Request | Cooling Coil XX Pump Lag Request |  | coolingCoil(\d{0,4})PumpLagReq | No | No | No | Bool | Request/No Request | Request/No Request | [6 empty] | cool,coil,water,pump,lag,request,cmd | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilPumpLead | coolingCoilPumpLead | Cooling Coil Pump Lead | Cooling Coil Pump Lead |  | coolingCoilPumpLead | Yes | Yes | No | Bool | Lead 1/Lead 2 | Lead 1/Lead 2 | [6 empty] | cool,coil,water,pump,lead,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.15 (Released),2.16 (Pre-Release)
coolingCoilPumpLeadXor | coolingCoilPumpLeadXor | Cooling Coil Pump Lead Change Over | Cooling Coil Pump Lead Change Over |  | coolingCoilPumpLeadXor | No | No | No | Bool | On/Off | On/Off | [6 empty] | cool,coil,water,pump,lead,changeOver,cmd | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.15 (Released),2.16 (Pre-Release)
coolingCoilPumpLeadXorRuntimeSp | coolingCoilPumpLeadXorRuntimeSp | Cooling Coil Pump Lead Change Over Runtime Setpoint | Cooling Coil Pump Lead Change Over Runtime Setpoint |  | coolingCoilPumpLeadXorRuntimeSp | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.15 (Released),2.16 (Pre-Release)
coolingCoilPumpLeavingPressure | coolingCoilXXXXPumpLeavingPressure | Cooling Coil Pump Leaving Pressure | Cooling Coil XX Pump Leaving Pressure |  | coolingCoil(\d{0,4})PumpLeavingPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | cool,coil,water,pump,leaving,pressure,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilPumpMaintSwitch | coolingCoilXXXXPumpMaintSwitch | Cooling Coil Pump Maintenance Switch | Cooling Coil XX Pump Maintenance Switch |  | coolingCoil(\d{0,4})PumpMaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | cool,coil,water,pump,maintenance,switch,cmd | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.15 (Released),2.16 (Pre-Release)
coolingCoilPumpOvr | coolingCoilXXXXPumpOvr | Cooling Coil Pump Override | Cooling Coil XX Pump Override |  | coolingCoil(\d{0,4})PumpOvr | No | No | No | Bool | On/Off | On/Off | [6 empty] | cool,coil,water,pump,status,ovr | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilPumpPressureDelta | coolingCoilXXXXPumpPressureDelta | Cooling Coil Pump Pressure Delta | Cooling Coil XX Pump Pressure Delta |  | coolingCoil(\d{0,4})PumpPressureDelta | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | cool,coil,water,pump,common,pressure,delta,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilPumpPressureHiAlarm | coolingCoilXXXXPumpPressureHiAlarm | Cooling Coil Pump Pressure High Alarm | Cooling Coil XX Pump Pressure High Alarm |  | coolingCoil(\d{0,4})PumpPressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | cool,coil,water,pump,pressure,high,alarm | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilPumpPressureHiSp | coolingCoilXXXXPumpPressureHiSp | Cooling Coil Pump Pressure High Setpoint | Cooling Coil XX Pump Pressure High Setpoint |  | coolingCoil(\d{0,4})PumpPressureHiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | cool,coil,water,pump,pressure,high,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilPumpPressureLoAlarm | coolingCoilXXXXPumpPressureLoAlarm | Cooling Coil Pump Pressure Low Alarm | Cooling Coil XX Pump Pressure Low Alarm |  | coolingCoil(\d{0,4})PumpPressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | cool,coil,water,pump,pressure,low,alarm | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilPumpPressureLoSp | coolingCoilXXXXPumpPressureLoSp | Cooling Coil Pump Pressure Low Setpoint | Cooling Coil XX Pump Pressure Low Setpoint |  | coolingCoil(\d{0,4})PumpPressureLoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | cool,coil,water,pump,pressure,low,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilPumpRuntime | coolingCoilXXXXPumpRuntime | Cooling Coil Pump Runtime | Cooling Coil XX Pump Runtime |  | coolingCoil(\d{0,4})PumpRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.15 (Released),2.16 (Pre-Release)
coolingCoilPumpSpeed | coolingCoilXXXXPumpSpeed | Cooling Coil Pump Speed | Cooling Coil XX Pump Speed |  | coolingCoil(\d{0,4})PumpSpeed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | cool,coil,water,pump,speed,cmd | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilPumpSpeedFb | coolingCoilXXXXPumpSpeedFb | Cooling Coil Pump Speed Feedback | Cooling Coil XX Pump Speed Feedback |  | coolingCoil(\d{0,4})PumpSpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | cool,coil,water,pump,speed,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilPumpSpeedMaxSp | coolingCoilXXXXPumpSpeedMaxSp | Cooling Coil Pump Speed Max Setpoint | Cooling Coil XX Pump Speed Max Setpoint |  | coolingCoil(\d{0,4})PumpSpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | cool,coil,water,pump,speed,max,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilPumpSpeedMinSp | coolingCoilXXXXPumpSpeedMinSp | Cooling Coil Pump Speed Min Setpoint | Cooling Coil XX Pump Speed Min Setpoint |  | coolingCoil(\d{0,4})PumpSpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | cool,coil,water,pump,speed,min,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilPumpSpeedOvr | coolingCoilXXXXPumpSpeedOvr | Cooling Coil Pump Speed Override | Cooling Coil XX Pump Speed Override |  | coolingCoil(\d{0,4})PumpSpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | cool,coil,water,pump,speed,ovr | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilPumpSpeedSp | coolingCoilXXXXPumpSpeedSp | Cooling Coil Pump Speed Setpoint | Cooling Coil XX Pump Speed Setpoint |  | coolingCoil(\d{0,4})PumpSpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | cool,coil,water,pump,speed,effective,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilPumpStatus | coolingCoilXXXXPumpStatus | Cooling Coil Pump Status | Cooling Coil XX Pump Status |  | coolingCoil(\d{0,4})PumpStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | cool,coil,water,pump,status,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilStrainerAlarm | coolingCoilXXXXStrainerAlarm | Cooling Coil Strainer Alarm | Cooling Coil XX Strainer Alarm |  | coolingCoil(\d{0,4})StrainerAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | cool,coil,water,strainer,alarm | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingCoilStrainerEnable | coolingCoilXXXXStrainerEnable | Cooling Coil Strainer Enable | Cooling Coil XX Strainer Enable |  | coolingCoil(\d{0,4})StrainerEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | cool,coil,water,strainer,enable,cmd | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingDemand | coolingDemand | Cooling Demand | Cooling Demand |  | coolingDemand | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | cool,common,load,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RP,RPC,RPF,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingEnable | coolingEnable | Cooling Enable Command | Cooling Enable Command |  | coolingEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | cool,enable,common,cmd | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RP,RPC,RPF,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingEnableDb | coolingEnableDb | Cooling Enable Deadband | Cooling Enable Deadband |  | coolingEnableDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | cool,enable,deadband,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RP,RPC,RPF,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingEnableSp | coolingEnableSp | Cooling Enable Setpoint | Cooling Enable Setpoint |  | coolingEnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | cool,enable,effective,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RP,RPC,RPF,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingStageAlarm | coolingStageXXXXAlarm | Cooling Stage Alarm | Cooling Stage XX Alarm |  | coolingStage(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal |  |  |  |  | XX |  | cool,status,alarm | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingStage | coolingStageXXXX | Cooling Stage Command | Cooling Stage XX Command |  | coolingStage(\d{0,4}) | Yes | Yes | No | Bool | On/Off | On/Off |  |  |  |  | XX |  | cool,status,cmd | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingStageDisable | coolingStageXXXXDisable | Cooling Stage Disable | Cooling Stage XX Disable |  | coolingStage(\d{0,4})Disable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled |  |  |  |  | XX |  | cool,disable,cmd | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingStageEnable | coolingStageXXXXEnable | Cooling Stage Enable | Cooling Stage XX Enable |  | coolingStage(\d{0,4})Enable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled |  |  |  |  | XX |  | cool,enable,cmd | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingStageEnableSp | coolingStageXXXXEnableSp | Cooling Stage Enable Setpoint | Cooling Stage XX Enable Setpoint |  | coolingStage(\d{0,4})EnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 | XX |  | cool,enable,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingStageMinOffSp | coolingStageXXXXMinOffSp | Cooling Stage Min Off Time Setpoint | Cooling Stage XX Min Off Time Setpoint |  | coolingStage(\d{0,4})MinOffSp | No | No | No | Number |  |  | second | second | 0 | 0 | XX |  | cool,min,off,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingStageMinOnSp | coolingStageXXXXMinOnSp | Cooling Stage Min On Time Setpoint | Cooling Stage XX Min On Time Setpoint |  | coolingStage(\d{0,4})MinOnSp | No | No | No | Number |  |  | second | second | 0 | 0 | XX |  | cool,min,on,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingStageMod | coolingStageXXXXMod | Cooling Stage Modulation | Cooling Stage XX Modulation |  | coolingStage(\d{0,4})Mod | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 | XX |  | cool,modulation,cmd | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingStageOvr | coolingStageXXXXOvr | Cooling Stage Override | Cooling Stage XX Override |  | coolingStage(\d{0,4})Ovr | No | No | No | Bool | On/Off | On/Off |  |  |  |  | XX |  | cool,status,ovr | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingStageRuntime | coolingStageXXXXRuntime | Cooling Stage Runtime | Cooling Stage XX Runtime |  | coolingStage(\d{0,4})Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 | XX |  | blacklist | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.15 (Released),2.16 (Pre-Release)
coolingStageStatus | coolingStageXXXXStatus | Cooling Stage Status | Cooling Stage XX Status |  | coolingStage(\d{0,4})Status | Yes | Yes | No | Bool | On/Off | On/Off |  |  |  |  | XX |  | cool,status,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingValveOneThird | coolingValveOneThird | Cooling Valve 1/3 Command | Cooling Valve 1/3 Command |  | coolingValveOneThird | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | cool,valve,position,oneThird,cmd | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingValveOneThirdFb | coolingValveOneThirdFb | Cooling Valve 1/3 Feedback | Cooling Valve 1/3 Feedback |  | coolingValveOneThirdFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | cool,valve,position,oneThird,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingValveOneThirdOvr | coolingValveOneThirdOvr | Cooling Valve 1/3 Override | Cooling Valve 1/3 Override |  | coolingValveOneThirdOvr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | cool,valve,position,oneThird,ovr | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingValveTwoThird | coolingValveTwoThird | Cooling Valve 2/3 Command | Cooling Valve 2/3 Command |  | coolingValveTwoThird | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | cool,valve,position,twoThird,cmd | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingValveTwoThirdFb | coolingValveTwoThirdFb | Cooling Valve 2/3 Feedback | Cooling Valve 2/3 Feedback |  | coolingValveTwoThirdFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | cool,valve,position,twoThird,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingValveTwoThirdOvr | coolingValveTwoThirdOvr | Cooling Valve 2/3 Override | Cooling Valve 2/3 Override |  | coolingValveTwoThirdOvr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | cool,valve,position,twoThird,ovr | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingValve | coolingValveXXXX | Cooling Valve Command | Cooling Valve XX Command |  | coolingValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 | XX |  | cool,valve,position,cmd | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingValveFb | coolingValveXXXXFb | Cooling Valve Feedback | Cooling Valve XX Feedback |  | coolingValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 | XX |  | cool,valve,position,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
coolingValveOvr | coolingValveXXXXOvr | Cooling Valve Override | Cooling Valve XX Override |  | coolingValve(\d{0,4})Ovr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 | XX |  | cool,valve,position,ovr | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
currentPhaseA | currentPhaseA | Current (Phase A) | Current (Phase A) |  | currentPhaseA | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | A | common,current,sensor | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CU,CUH,DAC,DH,DHU,DOAS,EC,EF,FCU,FPB,HP,HUM,INV,MAU,PDU,PFC,PM,PRLY,PV,RECT,RPP,RTU,TWR,UV,VAV,VPM,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
currentPhaseAMax | currentPhaseAMax | Current (Phase A) Maximum | Current (Phase A) Maximum |  | currentPhaseAMax | Yes | No | No | Number |  |  | ampere | ampere | 1 | 1 |  | A | common,current,max,calc | PRLY | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
currentPhaseB | currentPhaseB | Current (Phase B) | Current (Phase B) |  | currentPhaseB | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | B | common,current,sensor | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CU,CUH,DAC,DH,DHU,DOAS,EC,EF,FCU,FPB,HP,HUM,INV,MAU,PDU,PFC,PM,PRLY,PV,RECT,RPP,RTU,TWR,UV,VAV,VPM,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
currentPhaseBMax | currentPhaseBMax | Current (Phase B) Maximum | Current (Phase B) Maximum |  | currentPhaseBMax | Yes | No | No | Number |  |  | ampere | ampere | 1 | 1 |  | B | common,current,max,calc | PRLY | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
currentPhaseC | currentPhaseC | Current (Phase C) | Current (Phase C) |  | currentPhaseC | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | C | common,current,sensor | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CU,CUH,DAC,DH,DHU,DOAS,EC,EF,FCU,FPB,HP,HUM,INV,MAU,PDU,PFC,PM,PRLY,PV,RECT,RPP,RTU,TWR,UV,VAV,VPM,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
currentPhaseCMax | currentPhaseCMax | Current (Phase C) Maximum | Current (Phase C) Maximum |  | currentPhaseCMax | Yes | No | No | Number |  |  | ampere | ampere | 1 | 1 |  | C | common,current,max,calc | PRLY | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
currentPhaseG | currentPhaseG | Current (Phase G) | Current (Phase G) |  | currentPhaseG | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | G | common,current,sensor | PRLY | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
currentPhaseGMax | currentPhaseGMax | Current (Phase G) Maximum | Current (Phase G) Maximum |  | currentPhaseGMax | Yes | No | No | Number |  |  | ampere | ampere | 1 | 1 |  | G | common,current,max,calc | PRLY | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
currentPhaseN | currentPhaseN | Current (Phase N) | Current (Phase N) |  | currentPhaseN | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | common,current,sensor | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CU,CUH,DAC,DH,DHU,DOAS,EC,EF,FCU,FPB,HP,HUM,INV,MAU,PDU,PFC,PM,PRLY,PV,RECT,RPP,RTU,TWR,UV,VAV,VPM,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
currentPhaseNMax | currentPhaseNMax | Current (Phase N) Maximum | Current (Phase N) Maximum |  | currentPhaseNMax | Yes | No | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | common,current,max,calc | PRLY | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
current | current | Current Average | Current Average |  | current | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  |  | common,current,avg,calc | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CU,CUH,DAC,DH,DHU,DOAS,EC,EF,FCU,FPB,HP,HUM,INV,MAU,PDU,PFC,PM,PRLY,PV,RECT,RPP,RTU,TWR,UV,VAV,VPM,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
currentDirectionAlarm | currentDirectionAlarm | Current Direction Alarm | Current Direction Alarm |  | currentDirectionAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | common,current,direction,alarm | BRK,CU,DHU,EC,INV,PDU,PFC,PM,PRLY,PV,RECT,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
currentHiAlarm | currentHiAlarm | Current High Alarm | Current High Alarm |  | currentHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | common,current,high,alarm | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CU,CUH,DAC,DH,DHU,DOAS,EC,EF,FCU,FPB,HP,HUM,INV,MAU,PDU,PFC,PM,PRLY,PV,RECT,RPP,RTU,TWR,UV,VAV,VPM,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
currentImbalance | currentImbalance | Current Imbalance | Current Imbalance |  | currentImbalance | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | common,current,imbalance,sensor | PRLY | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
currentLoAlarm | currentLoAlarm | Current Low Alarm | Current Low Alarm |  | currentLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | common,current,low,alarm | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CU,CUH,DAC,DH,DHU,DOAS,EC,EF,FCU,FPB,HP,HUM,INV,MAU,PDU,PFC,PM,PRLY,PV,RECT,RPP,RTU,TWR,UV,VAV,VPM,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
currentSeqNeg | currentSeqNeg | Current Sequence Negtive | Current Sequence Negtive |  | currentSeqNeg | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  |  | common,current,seqNeg,sensor | PRLY | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
currentToleranceAlarm | currentToleranceAlarm | Current Tolerance Alarm | Current Tolerance Alarm |  | currentToleranceAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | common,current,tolerance,alarm | BRK,INV,PDU,PFC,PM,PRLY,PV,RECT,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
daytimeWarmUp | daytimeWarmUp | Daytime Warm Up Command | Daytime Warm Up Command |  | daytimeWarmUp | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | daytime,warmUp,cmd | AHU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
daytimeWarmUpDb | daytimeWarmUpDb | Daytime Warm Up Deadband | Daytime Warm Up Deadband |  | daytimeWarmUpDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | daytime,warmUp,deadband,sp | AHU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
daytimeWarmUpSp | daytimeWarmUpSp | Daytime Warm Up Setpoint | Daytime Warm Up Setpoint |  | daytimeWarmUpSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | daytime,warmUp,effective,sp | AHU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
currentDC | currentDC | DC Current | DC Current |  | currentDC | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  |  | current,dc,sensor | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CU,CUH,DAC,DH,DHU,DOAS,EC,EF,FCU,FPB,HP,HUM,INV,MAU,PDU,PFC,PM,PRLY,PV,RECT,RPP,RTU,TWR,UV,VAV,VPM,FCU,HP | 2.15 (Released),2.16 (Pre-Release)
powerRealDC | powerRealDC | DC Real Power | DC Real Power |  | powerRealDC | Yes | Yes | No | Number |  |  | kilowatt | kilowatt | 1 | 1 |  |  | power,real,dc,sensor | AC,AHU,ATS,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CU,CUH,CWS,DAC,DH,DHU,DOAS,EC,EF,FCU,FPB,GEO,HP,HUM,HWS,INV,MAU,PDU,PFC,PM,PRLY,PV,RECT,RPP,RTU,SMS,STS,TVS,TWR,UPS,UV,VAV,VPM,WS,FCU,HP | 2.15 (Released),2.16 (Pre-Release)
voltageDC | voltageDC | DC Voltage | DC Voltage |  | voltageDC | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  |  | volt,dc,sensor | ATS,BRK,CU,INV,PFC,PM,PRLY,PV,RECT,STS,TVS,UPS,VPM | 2.15 (Released),2.16 (Pre-Release)
decouplerFlow | decouplerFlow | Decoupler Water Flow | Decoupler Water Flow |  | decouplerFlow | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | decoupler,water,flow,sensor | CWS,HWS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
decouplerTemp | decouplerTemp | Decoupler Water Temperature | Decoupler Water Temperature |  | decouplerTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | decoupler,water,temp,sensor | CWS,HWS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dehumidDemand | dehumidDemand | Dehumidification Demand | Dehumidification Demand |  | dehumidDemand | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | dehumid,load,cmd | AHU,ATU,CRAC,CRAH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dehumidEnable | dehumidEnable | Dehumidification Enable | Dehumidification Enable |  | dehumidEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | dehumid,enable,cmd | AHU,ATU,CRAC,CRAH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dehumidEnableOvr | dehumidEnableOvr | Dehumidification Enable Override | Dehumidification Enable Override |  | dehumidEnableOvr | No | No | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | dehumid,enable,ovr | AHU,ATU,CRAC,CRAH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dehumidEnableSp | dehumidEnableSp | Dehumidification Enable Setpoint | Dehumidification Enable Setpoint |  | dehumidEnableSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | dehumid,enable,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dehumidMode | dehumidMode | Dehumidification Mode | Dehumidification Mode |  | dehumidMode | Yes | No | No | Bool | On/Off | On/Off | [6 empty] | dehumid,mode,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dehumidifierAlarm | dehumidifierXXXXAlarm | Dehumidifier Alarm | Dehumidifier XX Alarm |  | dehumidifier(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | dehumidifier,common,alarm | AHU,ATU,CRAC,CRAH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dehumidifier | dehumidifierXXXX | Dehumidifier Command | Dehumidifier XX Command |  | dehumidifier(\d{0,4}) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | dehumidifier,status,cmd | AHU,ATU,CRAC,CRAH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dehumidifierDemand | dehumidifierXXXXDemand | Dehumidifier Demand | Dehumidifier XX Demand |  | dehumidifier(\d{0,4})Demand | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | dehumidifier,load,cmd | AHU,ATU,CRAC,CRAH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dehumidifierEnable | dehumidifierXXXXEnable | Dehumidifier Enable Command | Dehumidifier XX Enable Command |  | dehumidifier(\d{0,4})Enable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | dehumidifier,enable,cmd | AHU,ATU,CRAC,CRAH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dehumidifierEnableSp | dehumidifierXXXXEnableSp | Dehumidifier Enable Setpoint | Dehumidifier XX Enable Setpoint |  | dehumidifier(\d{0,4})EnableSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | dehumidifier,enable,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dehumidifierFault | dehumidifierXXXXFault | Dehumidifier Fault | Dehumidifier XX Fault |  | dehumidifier(\d{0,4})Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | dehumidifier,fault | AHU,ATU,CRAC,CRAH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dehumidifierRuntime | dehumidifierXXXXRuntime | Dehumidifier Runtime | Dehumidifier XX Runtime |  | dehumidifier(\d{0,4})Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,ATU,CRAC,CRAH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.15 (Released),2.16 (Pre-Release)
dehumidifierStatus | dehumidifierXXXXStatus | Dehumidifier Status | Dehumidifier XX Status |  | dehumidifier(\d{0,4})Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | dehumidifier,status,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dcvDemand | dcvDemand | Demand Ventilation Demand | Demand Ventilation Demand |  | dcvDemand | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | demand,ventilation,common,cmd | AHU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dcvEnable | dcvEnable | Demand Ventilation Enable | Demand Ventilation Enable |  | dcvEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | demand,ventilation,enable,cmd | AHU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dcvMode | dcvMode | Demand Ventilation Mode | Demand Ventilation Mode |  | dcvMode | Yes | No | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | demand,ventilation,mode,cmd | AHU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
diffuserDirection | diffuserDirection | Diffuser Direction | Diffuser Direction |  | diffuserDirection | Yes | Yes | No | Str |  | Horizontal/Down 60%/Down 80%/Down 100%/Swing | [6 empty] | diffuser,direction,common,cmd | AC,FCU,UV,VRF,FCU | 2.14,2.15 (Released),2.16 (Pre-Release)
diffuserDirectionBAS | diffuserDirectionBAS | Diffuser Direction BAS | Diffuser Direction BAS |  | diffuserDirectionBAS | No | No | No | Str |  | Horizontal/Down 60%/Down 80%/Down 100%/Swing | [6 empty] | diffuser,direction,bas,cmd | AC,FCU,UV,VRF,FCU | 2.14,2.15 (Released),2.16 (Pre-Release)
diffuserDirectionOvr | diffuserDirectionOvr | Diffuser Direction Override | Diffuser Direction Override |  | diffuserDirectionOvr | No | No | No | Str |  | Horizontal/Down 60%/Down 80%/Down 100%/Swing | [6 empty] | diffuser,direction,ovr | AC,FCU,UV,VRF,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFlow | dischargeFlowXXXX | Discharge Airflow | Discharge Airflow XX |  | dischargeFlow(\d{0,4}) | Yes | Yes | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | discharge,air,flow,common,sensor | AFMS,AHU,ATU,CRAC,CRAH,CU,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFlowAlarm | dischargeFlowXXXXAlarm | Discharge Airflow Alarm | Discharge Airflow XX Alarm |  | dischargeFlow(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | discharge,air,flow,common,alarm | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFlowCO2MaxSp | dischargeFlowXXXXCO2MaxSp | Discharge Airflow CO2 Max Reset Setpoint | Discharge Airflow XX CO2 Max Reset Setpoint |  | dischargeFlow(\d{0,4})CO2MaxSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | discharge,air,flow,co2,max,sp | FPB,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFlowCO2MinSp | dischargeFlowXXXXCO2MinSp | Discharge Airflow CO2 Min Reset Setpoint | Discharge Airflow XX CO2 Min Reset Setpoint |  | dischargeFlow(\d{0,4})CO2MinSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | discharge,air,flow,co2,min,sp | FPB,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFlowCoolMaxSp | dischargeFlowXXXXCoolMaxSp | Discharge Airflow Cool Max Reset Setpoint | Discharge Airflow XX Cool Max Reset Setpoint |  | dischargeFlow(\d{0,4})CoolMaxSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | discharge,air,flow,cool,max,sp | FPB,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFlowCoolMinSp | dischargeFlowXXXXCoolMinSp | Discharge Airflow Cool Min Reset Setpoint | Discharge Airflow XX Cool Min Reset Setpoint |  | dischargeFlow(\d{0,4})CoolMinSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | discharge,air,flow,cool,min,sp | FPB,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFlowDb | dischargeFlowXXXXDb | Discharge Airflow Deadband | Discharge Airflow XX Deadband |  | dischargeFlow(\d{0,4})Db | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | discharge,air,flow,common,deadband,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFlowFault | dischargeFlowXXXXFault | Discharge Airflow Fault | Discharge Airflow XX Fault |  | dischargeFlow(\d{0,4})Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | discharge,air,flow,fault | AFMS,AHU,ATU,CRAC,CRAH,CU,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFlowHeatMaxSp | dischargeFlowXXXXHeatMaxSp | Discharge Airflow Heat Max Reset Setpoint | Discharge Airflow XX Heat Max Reset Setpoint |  | dischargeFlow(\d{0,4})HeatMaxSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | discharge,air,flow,heat,max,sp | FPB,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFlowHeatMinSp | dischargeFlowXXXXHeatMinSp | Discharge Airflow Heat Min Reset Setpoint | Discharge Airflow XX Heat Min Reset Setpoint |  | dischargeFlow(\d{0,4})HeatMinSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | discharge,air,flow,heat,min,sp | FPB,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFlowHiAlarm | dischargeFlowXXXXHiAlarm | Discharge Airflow High Alarm | Discharge Airflow XX High Alarm |  | dischargeFlow(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | discharge,air,flow,high,alarm | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFlowHiSp | dischargeFlowXXXXHiSp | Discharge Airflow High Setpoint | Discharge Airflow XX High Setpoint |  | dischargeFlow(\d{0,4})HiSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | discharge,air,flow,common,high,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFlowLoAlarm | dischargeFlowXXXXLoAlarm | Discharge Airflow Low Alarm | Discharge Airflow XX Low Alarm |  | dischargeFlow(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | discharge,air,flow,low,alarm | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFlowLoSp | dischargeFlowXXXXLoSp | Discharge Airflow Low Setpoint | Discharge Airflow XX Low Setpoint |  | dischargeFlow(\d{0,4})LoSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | discharge,air,flow,common,low,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFlowMaxSp | dischargeFlowXXXXMaxSp | Discharge Airflow Max Reset Setpoint | Discharge Airflow XX Max Reset Setpoint |  | dischargeFlow(\d{0,4})MaxSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | discharge,air,flow,common,max,sp | AHU,ATU,CRAC,CRAH,DOAS,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFlowMinSp | dischargeFlowXXXXMinSp | Discharge Airflow Min Reset Setpoint | Discharge Airflow XX Min Reset Setpoint |  | dischargeFlow(\d{0,4})MinSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | discharge,air,flow,common,min,sp | AHU,ATU,CRAC,CRAH,DOAS,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFlowOccSp | dischargeFlowXXXXOccSp | Discharge Airflow Occupied Setpoint | Discharge Airflow XX Occupied Setpoint |  | dischargeFlow(\d{0,4})OccSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | discharge,air,flow,occupied,effective,sp | AHU,ATU,CRAC,CRAH,DOAS,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFlowReHeatMaxSp | dischargeFlowXXXXReHeatMaxSp | Discharge Airflow Re-Heat Max Reset Setpoint | Discharge Airflow XX Re-Heat Max Reset Setpoint |  | dischargeFlow(\d{0,4})ReHeatMaxSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | discharge,air,flow,reheat,max,sp | FPB,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFlowReHeatMinSp | dischargeFlowXXXXReHeatMinSp | Discharge Airflow Re-Heat Min Reset Setpoint | Discharge Airflow XX Re-Heat Min Reset Setpoint |  | dischargeFlow(\d{0,4})ReHeatMinSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | discharge,air,flow,reheat,min,sp | FPB,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFlowSp | dischargeFlowXXXXSp | Discharge Airflow Setpoint | Discharge Airflow XX Setpoint |  | dischargeFlow(\d{0,4})Sp | Yes | Yes | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | discharge,air,flow,common,effective,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFlowSpOvr | dischargeFlowXXXXSpOvr | Discharge Airflow Setpoint Override | Discharge Airflow XX Setpoint Override |  | dischargeFlow(\d{0,4})SpOvr | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | discharge,air,flow,common,effective,spOvr | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,VAV,ZD,FCU,HP | 2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFlowStandbyCoolSp | dischargeFlowXXXXStandbyCoolSp | Discharge Airflow Standby Cool Setpoint | Discharge Airflow XX Standby Cool Setpoint |  | dischargeFlow(\d{0,4})StandbyCoolSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | discharge,air,flow,standby,cool,sp | FPB,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFlowStandbyHeatSp | dischargeFlowXXXXStandbyHeatSp | Discharge Airflow Standby Heat Setpoint | Discharge Airflow XX Standby Heat Setpoint |  | dischargeFlow(\d{0,4})StandbyHeatSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | discharge,air,flow,standby,heat,sp | FPB,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFlowStandbySp | dischargeFlowXXXXStandbySp | Discharge Airflow Standby Setpoint | Discharge Airflow XX Standby Setpoint |  | dischargeFlow(\d{0,4})StandbySp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | discharge,air,flow,standby,effective,sp | ATU,FPB,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFlowStatus | dischargeFlowXXXXStatus | Discharge Airflow Status | Discharge Airflow XX Status |  | dischargeFlow(\d{0,4})Status | Yes | Yes | No | Bool | Flow/No Flow | Flow/No Flow | [6 empty] | discharge,air,flow,status,sensor | AHU,ATU,CRAC,CRAH,DH,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFlowTotalizer | dischargeFlowTotalizer | Discharge Airflow Totalizer | Discharge Airflow Totalizer |  | dischargeFlowTotalizer | Yes | Yes | Yes | Number |  |  | cubic_foot | liter | 0 | 0 |  |  | discharge,air,flow,flowConsumption,sensor | AFMS,AHU,ATU,CRAC,CRAH,CU,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.15 (Released),2.16 (Pre-Release)
dischargeFlowTotalizerReset | dischargeFlowTotalizerReset | Discharge Airflow Totalizer Reset | Discharge Airflow Totalizer Reset |  | dischargeFlowTotalizerReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | discharge,air,flow,flowConsumption,reset | AFMS,AHU,ATU,CRAC,CRAH,CU,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.15 (Released),2.16 (Pre-Release)
dischargeFlowUnoccCoolSp | dischargeFlowXXXXUnoccCoolSp | Discharge Airflow Unoccupied Cool Setpoint | Discharge Airflow XX Unoccupied Cool Setpoint |  | dischargeFlow(\d{0,4})UnoccCoolSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | discharge,air,flow,unoccupied,cool,sp | FPB,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFlowUnoccHeatSp | dischargeFlowXXXXUnoccHeatSp | Discharge Airflow Unoccupied Heat Setpoint | Discharge Airflow XX Unoccupied Heat Setpoint |  | dischargeFlow(\d{0,4})UnoccHeatSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | discharge,air,flow,unoccupied,heat,sp | FPB,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFlowUnoccSp | dischargeFlowXXXXUnoccSp | Discharge Airflow Unoccupied Setpoint | Discharge Airflow XX Unoccupied Setpoint |  | dischargeFlow(\d{0,4})UnoccSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | discharge,air,flow,unoccupied,effective,sp | AHU,ATU,CRAC,CRAH,DOAS,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeCO2 | dischargeCO2XXXX | Discharge CO2 | Discharge CO2 XX |  | dischargeCO2(\d{0,4}) | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | discharge,air,co2,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeDamperAlarm | dischargeDamperXXXXAlarm | Discharge Damper Alarm | Discharge Damper XX Alarm |  | dischargeDamper(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | discharge,air,damper,common,alarm | FPB,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeDamper | dischargeDamperXXXX | Discharge Damper Command | Discharge Damper XX Command |  | dischargeDamper(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | discharge,air,damper,position,cmd | FPB,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeDamperCoolMaxSp | dischargeDamperXXXXCoolMaxSp | Discharge Damper Cool Max Reset Setpoint | Discharge Damper XX Cool Max Reset Setpoint |  | dischargeDamper(\d{0,4})CoolMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | discharge,air,damper,cool,max,sp | FPB,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeDamperCoolMinSp | dischargeDamperXXXXCoolMinSp | Discharge Damper Cool Min Reset Setpoint | Discharge Damper XX Cool Min Reset Setpoint |  | dischargeDamper(\d{0,4})CoolMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | discharge,air,damper,cool,min,sp | FPB,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeDamperDb | dischargeDamperXXXXDb | Discharge Damper Deadband | Discharge Damper XX Deadband |  | dischargeDamper(\d{0,4})Db | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | discharge,air,damper,common,deadband,sp | FPB,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeDamperDirection | dischargeDamperXXXXDirection | Discharge Damper Direction | Discharge Damper XX Direction |  | dischargeDamper(\d{0,4})Direction | Yes | Yes | No | Bool | CW/CCW | CW/CCW | [6 empty] | discharge,air,damper,direction,cmd | FPB,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeDamperFb | dischargeDamperXXXXFb | Discharge Damper Feedback | Discharge Damper XX Feedback |  | dischargeDamper(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | discharge,air,damper,position,sensor | FPB,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeDamperHeatMaxSp | dischargeDamperXXXXHeatMaxSp | Discharge Damper Heat Max Reset Setpoint | Discharge Damper XX Heat Max Reset Setpoint |  | dischargeDamper(\d{0,4})HeatMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | discharge,air,damper,heat,max,sp | FPB,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeDamperHeatMinSp | dischargeDamperXXXXHeatMinSp | Discharge Damper Heat Min Reset Setpoint | Discharge Damper XX Heat Min Reset Setpoint |  | dischargeDamper(\d{0,4})HeatMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | discharge,air,damper,heat,min,sp | FPB,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeDamperMaxSp | dischargeDamperXXXXMaxSp | Discharge Damper Max Setpoint | Discharge Damper XX Max Setpoint |  | dischargeDamper(\d{0,4})MaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | discharge,air,damper,common,max,sp | FPB,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeDamperMinSp | dischargeDamperXXXXMinSp | Discharge Damper Min Setpoint | Discharge Damper XX Min Setpoint |  | dischargeDamper(\d{0,4})MinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | discharge,air,damper,common,min,sp | FPB,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeDamperOvr | dischargeDamperXXXXOvr | Discharge Damper Override | Discharge Damper XX Override |  | dischargeDamper(\d{0,4})Ovr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | discharge,air,damper,position,ovr | FPB,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeDamperSp | dischargeDamperXXXXSp | Discharge Damper Setpoint | Discharge Damper XX Setpoint |  | dischargeDamper(\d{0,4})Sp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | discharge,air,damper,effective,sp | FPB,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeDehumidMaxSp | dischargeDehumidXXXXMaxSp | Discharge Dehumidification Max Reset Setpoint | Discharge Dehumidification XX Max Reset Setpoint |  | dischargeDehumid(\d{0,4})MaxSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | common,discharge,air,dehumid,max,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeDehumidMinSp | dischargeDehumidXXXXMinSp | Discharge Dehumidification Min Reset Setpoint | Discharge Dehumidification XX Min Reset Setpoint |  | dischargeDehumid(\d{0,4})MinSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | common,discharge,air,dehumid,min,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeDehumidSp | dischargeDehumidXXXXSp | Discharge Dehumidification Setpoint | Discharge Dehumidification XX Setpoint |  | dischargeDehumid(\d{0,4})Sp | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | common,discharge,air,dehumid,effective,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeDewpoint | dischargeDewpointXXXX | Discharge Dewpoint | Discharge Dewpoint XX |  | dischargeDewpoint(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | discharge,air,dewpoint,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeDewpointDb | dischargeDewpointXXXXDb | Discharge Dewpoint Deadband | Discharge Dewpoint XX Deadband |  | dischargeDewpoint(\d{0,4})Db | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | discharge,air,dewpoint,deadband,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeDewpointHiAlarm | dischargeDewpointXXXXHiAlarm | Discharge Dewpoint High Alarm | Discharge Dewpoint XX High Alarm |  | dischargeDewpoint(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | discharge,air,dewpoint,high,alarm | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeDewpointHiSp | dischargeDewpointXXXXHiSp | Discharge Dewpoint High Setpoint | Discharge Dewpoint XX High Setpoint |  | dischargeDewpoint(\d{0,4})HiSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | discharge,air,dewpoint,high,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeDewpointLoSp | dischargeDewpointXXXXLoSp | Discharge Dewpoint Low Setpoint | Discharge Dewpoint XX Low Setpoint |  | dischargeDewpoint(\d{0,4})LoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | discharge,air,dewpoint,low,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeDewpointMaxSp | dischargeDewpointXXXXMaxSp | Discharge Dewpoint Max Reset Setpoint | Discharge Dewpoint XX Max Reset Setpoint |  | dischargeDewpoint(\d{0,4})MaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | discharge,air,dewpoint,max,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeDewpointMinSp | dischargeDewpointXXXXMinSp | Discharge Dewpoint Min Reset Setpoint | Discharge Dewpoint XX Min Reset Setpoint |  | dischargeDewpoint(\d{0,4})MinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | discharge,air,dewpoint,min,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeDewpointSp | dischargeDewpointXXXXSp | Discharge Dewpoint Setpoint | Discharge Dewpoint XX Setpoint |  | dischargeDewpoint(\d{0,4})Sp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | discharge,air,dewpoint,effective,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeEnthalpy | dischargeEnthalpyXXXX | Discharge Enthalpy | Discharge Enthalpy XX |  | dischargeEnthalpy(\d{0,4}) | Yes | Yes | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | discharge,air,enthalpy,common,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeEnthalpyDb | dischargeEnthalpyXXXXDb | Discharge Enthalpy Deadband | Discharge Enthalpy XX Deadband |  | dischargeEnthalpy(\d{0,4})Db | No | No | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | discharge,air,enthalpy,common,deadband,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeEnthalpyHiSp | dischargeEnthalpyXXXXHiSp | Discharge Enthalpy High Setpoint | Discharge Enthalpy XX High Setpoint |  | dischargeEnthalpy(\d{0,4})HiSp | No | No | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | discharge,air,enthalpy,common,high,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeEnthalpyLoSp | dischargeEnthalpyXXXXLoSp | Discharge Enthalpy Low Setpoint | Discharge Enthalpy XX Low Setpoint |  | dischargeEnthalpy(\d{0,4})LoSp | No | No | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | discharge,air,enthalpy,common,low,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeEnthalpyMaxSp | dischargeEnthalpyXXXXMaxSp | Discharge Enthalpy Max Setpoint | Discharge Enthalpy XX Max Setpoint |  | dischargeEnthalpy(\d{0,4})MaxSp | No | No | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | discharge,air,enthalpy,common,max,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeEnthalpyMinSp | dischargeEnthalpyXXXXMinSp | Discharge Enthalpy Min Setpoint | Discharge Enthalpy XX Min Setpoint |  | dischargeEnthalpy(\d{0,4})MinSp | No | No | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | discharge,air,enthalpy,common,min,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeEnthalpySp | dischargeEnthalpyXXXXSp | Discharge Enthalpy Setpoint | Discharge Enthalpy XX Setpoint |  | dischargeEnthalpy(\d{0,4})Sp | Yes | Yes | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | discharge,air,enthalpy,common,effective,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanAlarm | dischargeFanXXXXAlarm | Discharge Fan Alarm | Discharge Fan XX Alarm |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | discharge,air,fan,general,common,alarm | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanAlarmReset | dischargeFanXXXXAlarmReset | Discharge Fan Alarm Reset | Discharge Fan XX Alarm Reset |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | discharge,air,fan,general,reset,alarm | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFan | dischargeFanXXXX | Discharge Fan Command | Discharge Fan XX Command |  | dischargeFan((?:(?!Ovr)(?!Mode)\w){0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | discharge,air,fan,status,cmd,common | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanCurrent | dischargeFanXXXXCurrent | Discharge Fan Current | Discharge Fan XX Current |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))Current | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | discharge,air,fan,current,sensor | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanDischargeTemp | dischargeFanXXXXDischargeTemp | Discharge Fan Discharge Temperature | Discharge Fan XX Discharge Temperature |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))DischargeTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | discharge,air,fan,leaving,temp,sensor | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.15 (Released),2.16 (Pre-Release)
dischargeFanEnteringPressure | dischargeFanXXXXEnteringPressure | Discharge Fan Entering Pressure | Discharge Fan XX Entering Pressure |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))EnteringPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | discharge,air,fan,entering,pressure,sensor | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanFault | dischargeFanXXXXFault | Discharge Fan Fault | Discharge Fan XX Fault |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | discharge,air,fan,fault,common | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanFilterAlarm | dischargeFanXXXXFilterAlarm | Discharge Fan Filter Alarm | Discharge Fan XX Filter Alarm |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))FilterAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | discharge,air,fan,filter,common,alarm | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanFilterAlarmReset | dischargeFanXXXXFilterAlarmReset | Discharge Fan Filter Alarm Reset | Discharge Fan XX Filter Alarm Reset |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))FilterAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | discharge,air,fan,filter,reset,alarm | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanFilterPressureDelta | dischargeFanXXXXFilterYYYYPressureDelta | Discharge Fan Filter Pressure Delta | Discharge Fan XX Filter YY Pressure Delta |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))Filter(\d{0,4})PressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | discharge,air,fan,filter,pressure,delta,sensor | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanFilterRuntime | dischargeFanXXXXFilterRuntime | Discharge Fan Filter Runtime | Discharge Fan XX Filter Runtime |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))FilterRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.15 (Released),2.16 (Pre-Release)
dischargeFanLeavingPressure | dischargeFanXXXXLeavingPressure | Discharge Fan Leaving Pressure | Discharge Fan XX Leaving Pressure |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))LeavingPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | discharge,air,fan,leaving,pressure,sensor | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanMaintSwitch | dischargeFanXXXXMaintSwitch | Discharge Fan Maintenance Switch | Discharge Fan XX Maintenance Switch |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))MaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | discharge,air,fan,maintenance,switch,cmd | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanMode | dischargeFanXXXXMode | Discharge Fan Mode | Discharge Fan XX Mode |  | dischargeFan((?:(?!Hand)\w){0,4}(?=[A-Z]¦$))Mode | Yes | No | No | Str | Continuous/Cycling | Continuous/Cycling | [6 empty] | blacklist | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanModeOvr | dischargeFanXXXXModeOvr | Discharge Fan Mode Override | Discharge Fan XX Mode Override |  | dischargeFan((?:(?!Hand)\w){0,4}(?=[A-Z]¦$))ModeOvr | No | No | No | Str | Continuous/Cycling | Continuous/Cycling | [6 empty] | discharge,air,fan,mode,ovr | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanOvr | dischargeFanXXXXOvr | Discharge Fan Override | Discharge Fan XX Override |  | dischargeFan((?:(?!Mode)\w){0,4}(?=[A-Z]¦$))Ovr | No | No | No | Bool | On/Off | On/Off | [6 empty] | discharge,air,fan,status,ovr | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanPressureDelta | dischargeFanXXXXPressureDelta | Discharge Fan Pressure Delta | Discharge Fan XX Pressure Delta |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))PressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | discharge,air,fan,common,pressure,delta,sensor | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanPressureHiAlarm | dischargeFanXXXXPressureHiAlarm | Discharge Fan Pressure High Alarm | Discharge Fan XX Pressure High Alarm |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))PressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | discharge,air,fan,pressure,high,alarm | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanPressureHiSp | dischargeFanXXXXPressureHiSp | Discharge Fan Pressure High Setpoint | Discharge Fan XX Pressure High Setpoint |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))PressureHiSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | discharge,air,fan,pressure,high,sp | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanPressureLoAlarm | dischargeFanXXXXPressureLoAlarm | Discharge Fan Pressure Low Alarm | Discharge Fan XX Pressure Low Alarm |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))PressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | discharge,air,fan,pressure,low,alarm | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanPressureLoSp | dischargeFanXXXXPressureLoSp | Discharge Fan Pressure Low Setpoint | Discharge Fan XX Pressure Low Setpoint |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))PressureLoSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | discharge,air,fan,pressure,low,sp | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanRuntime | dischargeFanXXXXRuntime | Discharge Fan Runtime | Discharge Fan XX Runtime |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.15 (Released),2.16 (Pre-Release)
dischargeFanShutdownSwitch | dischargeFanXXXXShutdownSwitch | Discharge Fan Shutdown Switch | Discharge Fan XX Shutdown Switch |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))ShutdownSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | discharge,air,fan,shutdown,switch,cmd | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanSpeed | dischargeFanXXXXSpeed | Discharge Fan Speed | Discharge Fan XX Speed |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))Speed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | discharge,air,fan,speed,common,cmd | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanSpeedBAS | dischargeFanXXXXSpeedBAS | Discharge Fan Speed BAS | Discharge Fan XX Speed BAS |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))SpeedBAS | No | No | No | Number |  | Low/Medium/High | percent | percent | 1 | 1 |  |  | discharge,air,fan,speed,bas,cmd | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanSpeedFb | dischargeFanXXXXSpeedFb | Discharge Fan Speed Feedback | Discharge Fan XX Speed Feedback |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))SpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | discharge,air,fan,speed,sensor | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanSpeedMaxSp | dischargeFanXXXXSpeedMaxSp | Discharge Fan Speed Max Setpoint | Discharge Fan XX Speed Max Setpoint |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))SpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | discharge,air,fan,speed,max,sp | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanSpeedMinSp | dischargeFanXXXXSpeedMinSp | Discharge Fan Speed Min Setpoint | Discharge Fan XX Speed Min Setpoint |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))SpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | discharge,air,fan,speed,min,sp | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanSpeedMode | dischargeFanXXXXSpeedMode | Discharge Fan Speed Mode | Discharge Fan XX Speed Mode |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))SpeedMode | Yes | No | No | Str |  | Constant Volume/Fixed Variable Speed/Pressure Controlled | [6 empty] | discharge,air,fan,speed,mode,sp | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanSpeedOccSp | dischargeFanXXXXSpeedOccSp | Discharge Fan Speed Occupied Setpoint | Discharge Fan XX Speed Occupied Setpoint |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))SpeedOccSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | discharge,air,fan,speed,occupied,sp | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanSpeedOvr | dischargeFanXXXXSpeedOvr | Discharge Fan Speed Override | Discharge Fan XX Speed Override |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))SpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | discharge,air,fan,speed,ovr | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanSpeedSp | dischargeFanXXXXSpeedSp | Discharge Fan Speed Setpoint | Discharge Fan XX Speed Setpoint |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))SpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | discharge,air,fan,speed,effective,sp | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanSpeedStage | dischargeFanXXXXSpeedStage | Discharge Fan Speed Stage | Discharge Fan XX Speed Stage |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))SpeedStage | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | discharge,air,fan,speed,stage | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanSpeedSummerSp | dischargeFanXXXXSpeedSummerSp | Discharge Fan Speed Summer Setpoint | Discharge Fan XX Speed Summer Setpoint |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))SpeedSummerSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | discharge,air,fan,speed,summer,sp | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanSpeedUnoccSp | dischargeFanXXXXSpeedUnoccSp | Discharge Fan Speed Unoccupied Setpoint | Discharge Fan XX Speed Unoccupied Setpoint |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))SpeedUnoccSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | discharge,air,fan,speed,unoccupied,sp | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanSpeedWinterSp | dischargeFanXXXXSpeedWinterSp | Discharge Fan Speed Winter Setpoint | Discharge Fan XX Speed Winter Setpoint |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))SpeedWinterSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | discharge,air,fan,speed,winter,sp | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanStageSp | dischargeFanXXXXStageYYYYSp | Discharge Fan Stage Setpoint | Discharge Fan XX Stage YY Setpoint |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))Stage(\d{0,4})Sp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 | YY |  | discharge,air,fan,sp | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFanStatus | dischargeFanXXXXStatus | Discharge Fan Status | Discharge Fan XX Status |  | dischargeFan(\w{0,4}(?=[A-Z]¦$))Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | discharge,air,fan,status,sensor,common | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFilterAlarm | dischargeFilterXXXXAlarm | Discharge Filter Alarm | Discharge Filter XX Alarm |  | dischargeFilter(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | discharge,air,filter,general,common,alarm | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFilterAlarmReset | dischargeFilterXXXXAlarmReset | Discharge Filter Alarm Reset | Discharge Filter XX Alarm Reset |  | dischargeFilter(\d{0,4})AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | discharge,air,filter,general,reset,alarm | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeFilterPressureDelta | dischargeFilterXXXXPressureDelta | Discharge Filter Pressure Differential | Discharge Filter XX Pressure Differential |  | dischargeFilter(\d{0,4})PressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | discharge,air,filter,general,pressure,delta,sensor | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeHumidMaxSp | dischargeHumidXXXXMaxSp | Discharge Humidification Max Reset Setpoint | Discharge Humidification XX Max Reset Setpoint |  | dischargeHumid(\d{0,4})MaxSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | common,discharge,air,humid,max,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeHumidMinSp | dischargeHumidXXXXMinSp | Discharge Humidification Min Reset Setpoint | Discharge Humidification XX Min Reset Setpoint |  | dischargeHumid(\d{0,4})MinSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | common,discharge,air,humid,min,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeHumidSp | dischargeHumidXXXXSp | Discharge Humidification Setpoint | Discharge Humidification XX Setpoint |  | dischargeHumid(\d{0,4})Sp | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | common,discharge,air,humid,effective,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeHumidity | dischargeHumidityXXXX | Discharge Humidity | Discharge Humidity XX |  | dischargeHumidity(\d{0,4}) | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | common,discharge,air,humidity,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeHumidityDb | dischargeHumidityXXXXDb | Discharge Humidity Deadband | Discharge Humidity XX Deadband |  | dischargeHumidity(\d{0,4})Db | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | common,discharge,air,humidity,deadband,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeHumidityFault | dischargeHumidityXXXXFault | Discharge Humidity Fault | Discharge Humidity XX Fault |  | dischargeHumidity(\d{0,4})Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | common,discharge,air,humidity,fault | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeHumidityHiAlarm | dischargeHumidityXXXXHiAlarm | Discharge Humidity High Alarm | Discharge Humidity XX High Alarm |  | dischargeHumidity(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | common,discharge,air,humidity,high,alarm | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeHumidityHiSp | dischargeHumidityXXXXHiSp | Discharge Humidity High Setpoint | Discharge Humidity XX High Setpoint |  | dischargeHumidity(\d{0,4})HiSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | discharge,air,humidity,common,high,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeHumidityLoAlarm | dischargeHumidityXXXXLoAlarm | Discharge Humidity Low Alarm | Discharge Humidity XX Low Alarm |  | dischargeHumidity(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | common,discharge,air,humidity,low,alarm | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeHumidityLoSp | dischargeHumidityXXXXLoSp | Discharge Humidity Low Setpoint | Discharge Humidity XX Low Setpoint |  | dischargeHumidity(\d{0,4})LoSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | discharge,air,humidity,common,low,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeHumidityMaxSp | dischargeHumidityXXXXMaxSp | Discharge Humidity Max Reset Setpoint | Discharge Humidity XX Max Reset Setpoint |  | dischargeHumidity(\d{0,4})MaxSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | discharge,air,humidity,common,max,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeHumidityMinSp | dischargeHumidityXXXXMinSp | Discharge Humidity Min Reset Setpoint | Discharge Humidity XX Min Reset Setpoint |  | dischargeHumidity(\d{0,4})MinSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | discharge,air,humidity,common,min,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeHumiditySp | dischargeHumidityXXXXSp | Discharge Humidity Setpoint | Discharge Humidity XX Setpoint |  | dischargeHumidity(\d{0,4})Sp | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | common,discharge,air,humidity,effective,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeIsoDamper | dischargeIsoDamperXXXX | Discharge Isolation Damper Command | Discharge Isolation Damper XX Command |  | dischargeIsoDamper(\d{0,4}) | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | common,discharge,iso,air,damper,status,cmd | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeIsoDamperFb | dischargeIsoDamperXXXXFb | Discharge Isolation Damper Feedback | Discharge Isolation Damper XX Feedback |  | dischargeIsoDamper(\d{0,4})Fb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | common,discharge,iso,air,damper,status,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeIsoDamperOvr | dischargeIsoDamperXXXXOvr | Discharge Isolation Damper Override | Discharge Isolation Damper XX Override |  | dischargeIsoDamper(\d{0,4})Ovr | No | No | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | common,discharge,iso,air,damper,status,ovr | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargePressure | dischargePressureXXXX | Discharge Pressure | Discharge Pressure XX |  | dischargePressure(\d{0,4}) | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | common,discharge,air,static,pressure,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargePressureDb | dischargePressureXXXXDb | Discharge Pressure Deadband | Discharge Pressure XX Deadband |  | dischargePressure(\d{0,4})Db | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | common,discharge,air,static,pressure,deadband,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargePressureHiAlarm | dischargePressureXXXXHiAlarm | Discharge Pressure High Alarm | Discharge Pressure XX High Alarm |  | dischargePressure(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | common,discharge,air,static,pressure,high,general,alarm | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargePressureHiAlarmReset | dischargePressureXXXXHiAlarmReset | Discharge Pressure High Alarm Reset | Discharge Pressure XX High Alarm Reset |  | dischargePressure(\d{0,4})HiAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | common,discharge,air,static,pressure,high,reset,alarm | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargePressureHiSp | dischargePressureXXXXHiSp | Discharge Pressure High Setpoint | Discharge Pressure XX High Setpoint |  | dischargePressure(\d{0,4})HiSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | common,discharge,air,static,pressure,high,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargePressureLoAlarm | dischargePressureXXXXLoAlarm | Discharge Pressure Low Alarm | Discharge Pressure XX Low Alarm |  | dischargePressure(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | common,discharge,air,static,pressure,low,general,alarm | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargePressureLoAlarmReset | dischargePressureXXXXLoAlarmReset | Discharge Pressure Low Alarm Reset | Discharge Pressure XX Low Alarm Reset |  | dischargePressure(\d{0,4})LoAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | common,discharge,air,static,pressure,low,reset,alarm | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargePressureLoSp | dischargePressureXXXXLoSp | Discharge Pressure Low Setpoint | Discharge Pressure XX Low Setpoint |  | dischargePressure(\d{0,4})LoSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | common,discharge,air,static,pressure,low,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargePressureMaxSp | dischargePressureXXXXMaxSp | Discharge Pressure Max Reset Setpoint | Discharge Pressure XX Max Reset Setpoint |  | dischargePressure(\d{0,4})MaxSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | common,discharge,air,static,pressure,max,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargePressureMinSp | dischargePressureXXXXMinSp | Discharge Pressure Min Reset Setpoint | Discharge Pressure XX Min Reset Setpoint |  | dischargePressure(\d{0,4})MinSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | common,discharge,air,static,pressure,min,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargePressureOccSp | dischargePressureXXXXOccSp | Discharge Pressure Occupied Setpoint | Discharge Pressure XX Occupied Setpoint |  | dischargePressure(\d{0,4})OccSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | common,discharge,air,static,pressure,occupied,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargePressureSp | dischargePressureXXXXSp | Discharge Pressure Setpoint | Discharge Pressure XX Setpoint |  | dischargePressure(\d{0,4})Sp | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | common,discharge,air,static,pressure,effective,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargePressureSpOvr | dischargePressureXXXXSpOvr | Discharge Pressure Setpoint Override | Discharge Pressure XX Setpoint Override |  | dischargePressure(\d{0,4})SpOvr | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | common,discharge,air,static,pressure,effective,ovr | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargePressureUnoccSp | dischargePressureXXXXUnoccSp | Discharge Pressure Unoccupied Setpoint | Discharge Pressure XX Unoccupied Setpoint |  | dischargePressure(\d{0,4})UnoccSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | common,discharge,air,static,pressure,unoccupied,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeSmokeAlarm | dischargeSmokeXXXXAlarm | Discharge Smoke Alarm | Discharge Smoke XX Alarm |  | dischargeSmoke(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | common,discharge,air,smoke,alarm | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeSmokeDamper | dischargeSmokeDamperXXXX | Discharge Smoke Damper Command | Discharge Smoke Damper XX Command |  | dischargeSmokeDamper(\d{0,4}) | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | discharge,air,smoke,damper,status,cmd | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeSmokeDamperFb | dischargeSmokeDamperXXXXFb | Discharge Smoke Damper Feedback | Discharge Smoke Damper XX Feedback |  | dischargeSmokeDamper(\d{0,4})Fb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | discharge,air,smoke,damper,status,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeSmokeFault | dischargeSmokeXXXXFault | Discharge Smoke Fault | Discharge Smoke XX Fault |  | dischargeSmoke(\d{0,4})Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | common,discharge,air,smoke,fault | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTemp | dischargeTempXXXX | Discharge Temperature | Discharge Temperature XX |  | dischargeTemp(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,discharge,air,temp,sensor | AFMS,AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,ERU,FCU,FPB,HP,HRU,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempCoolMaxSp | dischargeTempXXXXCoolMaxSp | Discharge Temperature Cool Max Reset Setpoint | Discharge Temperature XX Cool Max Reset Setpoint |  | dischargeTemp(\d{0,4})CoolMaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,discharge,air,temp,cool,max,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempCoolMinSp | dischargeTempXXXXCoolMinSp | Discharge Temperature Cool Min Reset Setpoint | Discharge Temperature XX Cool Min Reset Setpoint |  | dischargeTemp(\d{0,4})CoolMinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,discharge,air,temp,cool,min,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempCoolSp | dischargeTempXXXXCoolSp | Discharge Temperature Cooling Setpoint | Discharge Temperature XX Cooling Setpoint |  | dischargeTemp(\d{0,4})CoolSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,discharge,air,cool,temp,active,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,FPB,MAU,RTU,UV,VAV,ZD,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempCoolSpOvr | dischargeTempXXXXCoolSpOvr | Discharge Temperature Cooling Setpoint Override | Discharge Temperature XX Cooling Setpoint Override |  | dischargeTemp(\d{0,4})CoolSpOvr | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,discharge,air,cool,temp,active,ovr | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,FPB,MAU,RTU,UV,VAV,ZD,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempDb | dischargeTempXXXXDb | Discharge Temperature Deadband | Discharge Temperature XX Deadband |  | dischargeTemp(\d{0,4})Db | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | common,discharge,air,temp,general,deadband,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,FPB,MAU,RTU,UV,VAV,ZD,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempDehumidSp | dischargeTempXXXXDehumidSp | Discharge Temperature Dehumidification Setpoint | Discharge Temperature XX Dehumidification Setpoint |  | dischargeTemp(\d{0,4})DehumidSp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,discharge,air,temp,dehumid,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempEconMaxSp | dischargeTempXXXXEconMaxSp | Discharge Temperature Economizer Max Setpoint | Discharge Temperature XX Economizer Max Setpoint |  | dischargeTemp(\d{0,4})EconMaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,discharge,air,temp,econ,max,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempEconMinSp | dischargeTempXXXXEconMinSp | Discharge Temperature Economizer Min Setpoint | Discharge Temperature XX Economizer Min Setpoint |  | dischargeTemp(\d{0,4})EconMinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,discharge,air,temp,econ,min,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempEconSp | dischargeTempXXXXEconSp | Discharge Temperature Economizer Setpoint | Discharge Temperature XX Economizer Setpoint |  | dischargeTemp(\d{0,4})EconSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,discharge,air,temp,econ,effective,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempFault | dischargeTempXXXXFault | Discharge Temperature Fault | Discharge Temperature XX Fault |  | dischargeTemp(\d{0,4})Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | discharge,air,temp,fault | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempHeatMaxSp | dischargeTempXXXXHeatMaxSp | Discharge Temperature Heat Max Reset Setpoint | Discharge Temperature XX Heat Max Reset Setpoint |  | dischargeTemp(\d{0,4})HeatMaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,discharge,air,temp,heat,max,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempHeatMinSp | dischargeTempXXXXHeatMinSp | Discharge Temperature Heat Min Reset Setpoint | Discharge Temperature XX Heat Min Reset Setpoint |  | dischargeTemp(\d{0,4})HeatMinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,discharge,air,temp,heat,min,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempHeatSp | dischargeTempXXXXHeatSp | Discharge Temperature Heating Setpoint | Discharge Temperature XX Heating Setpoint |  | dischargeTemp(\d{0,4})HeatSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,discharge,air,heat,temp,active,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,FPB,MAU,RTU,UV,VAV,ZD,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempHiAlarm | dischargeTempXXXXHiAlarm | Discharge Temperature High Alarm | Discharge Temperature XX High Alarm |  | dischargeTemp(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | common,discharge,air,temp,high,alarm | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempHiSp | dischargeTempXXXXHiSp | Discharge Temperature High Setpoint | Discharge Temperature XX High Setpoint |  | dischargeTemp(\d{0,4})HiSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,discharge,air,temp,high,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempLoAlarm | dischargeTempXXXXLoAlarm | Discharge Temperature Low Alarm | Discharge Temperature XX Low Alarm |  | dischargeTemp(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | common,discharge,air,temp,low,alarm | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempLoSp | dischargeTempXXXXLoSp | Discharge Temperature Low Setpoint | Discharge Temperature XX Low Setpoint |  | dischargeTemp(\d{0,4})LoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,discharge,air,temp,low,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempMaxSp | dischargeTempXXXXMaxSp | Discharge Temperature Max Reset Setpoint | Discharge Temperature XX Max Reset Setpoint |  | dischargeTemp(\d{0,4})MaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,discharge,air,temp,max,sp,limit | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempMinSp | dischargeTempXXXXMinSp | Discharge Temperature Min Reset Setpoint | Discharge Temperature XX Min Reset Setpoint |  | dischargeTemp(\d{0,4})MinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,discharge,air,temp,min,sp,limit | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempOccCoolSpOffset | dischargeTempXXXXOccCoolSpOffset | Discharge Temperature Occupied Cool Setpoint Offset | Discharge Temperature XX Occupied Cool Setpoint Offset |  | dischargeTemp(\d{0,4})OccCoolSpOffset | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | discharge,air,temp,cool,offset,occupied,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempOccHeatSpOffset | dischargeTempXXXXOccHeatSpOffset | Discharge Temperature Occupied Heat Setpoint Offset | Discharge Temperature XX Occupied Heat Setpoint Offset |  | dischargeTemp(\d{0,4})OccHeatSpOffset | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | discharge,air,temp,heat,offset,occupied,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempOccSp | dischargeTempXXXXOccSp | Discharge Temperature Occupied Setpoint | Discharge Temperature XX Occupied Setpoint |  | dischargeTemp(\d{0,4})OccSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,discharge,air,temp,occupied,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempResetEnable | dischargeTempResetEnable | Discharge Temperature Reset Enable | Discharge Temperature Reset Enable |  | dischargeTempResetEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | common,discharge,air,temp,reset,enable,cmd | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempSp | dischargeTempXXXXSp | Discharge Temperature Setpoint | Discharge Temperature XX Setpoint |  | dischargeTemp(\d{0,4})Sp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,discharge,air,temp,general,effective,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempSpOffset | dischargeTempXXXXSpOffset | Discharge Temperature Setpoint Offset | Discharge Temperature XX Setpoint Offset |  | dischargeTemp(\d{0,4})SpOffset | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | common,discharge,air,temp,offset,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempSpOffsetMax | dischargeTempXXXXSpOffsetMax | Discharge Temperature Setpoint Offset Max | Discharge Temperature XX Setpoint Offset Max |  | dischargeTemp(\d{0,4})SpOffsetMax | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | discharge,air,temp,offset,max,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempSpOffsetMin | dischargeTempXXXXSpOffsetMin | Discharge Temperature Setpoint Offset Min | Discharge Temperature XX Setpoint Offset Min |  | dischargeTemp(\d{0,4})SpOffsetMin | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | discharge,air,temp,offset,min,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempSpOvr | dischargeTempXXXXSpOvr | Discharge Temperature Setpoint Override | Discharge Temperature XX Setpoint Override |  | dischargeTemp(\d{0,4})SpOvr | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | blacklist | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempSummerDb | dischargeTempSummerDb | Discharge Temperature Summer Deadband | Discharge Temperature Summer Deadband |  | dischargeTempSummerDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | common,discharge,air,temp,summer,deadband,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempSummerMaxSp | dischargeTempSummerMaxSp | Discharge Temperature Summer Max Reset Setpoint | Discharge Temperature Summer Max Reset Setpoint |  | dischargeTempSummerMaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,discharge,air,temp,summer,max,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempSummerMinSp | dischargeTempSummerMinSp | Discharge Temperature Summer Min Reset Setpoint | Discharge Temperature Summer Min Reset Setpoint |  | dischargeTempSummerMinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,discharge,air,temp,summer,min,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempSummerSp | dischargeTempSummerSp | Discharge Temperature Summer Setpoint | Discharge Temperature Summer Setpoint |  | dischargeTempSummerSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,discharge,air,temp,summer,effective,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempUnoccCoolSpOffset | dischargeTempXXXXUnoccCoolSpOffset | Discharge Temperature Unoccupied Cool Setpoint Offset | Discharge Temperature XX Unoccupied Cool Setpoint Offset |  | dischargeTemp(\d{0,4})UnoccCoolSpOffset | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | discharge,air,temp,cool,offset,unoccupied,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempUnoccHeatSpOffset | dischargeTempXXXXUnoccHeatSpOffset | Discharge Temperature Unoccupied Heat Setpoint Offset | Discharge Temperature XX Unoccupied Heat Setpoint Offset |  | dischargeTemp(\d{0,4})UnoccHeatSpOffset | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | discharge,air,temp,heat,offset,unoccupied,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempUnoccSp | dischargeTempXXXXUnoccSp | Discharge Temperature Unoccupied Setpoint | Discharge Temperature XX Unoccupied Setpoint |  | dischargeTemp(\d{0,4})UnoccSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,discharge,air,temp,unoccupied,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempWinterDb | dischargeTempWinterDb | Discharge Temperature Winter Deadband | Discharge Temperature Winter Deadband |  | dischargeTempWinterDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | common,discharge,air,temp,winter,deadband,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempWinterMaxSp | dischargeTempWinterMaxSp | Discharge Temperature Winter Max Reset Setpoint | Discharge Temperature Winter Max Reset Setpoint |  | dischargeTempWinterMaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,discharge,air,temp,winter,max,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempWinterMinSp | dischargeTempWinterMinSp | Discharge Temperature Winter Min Reset Setpoint | Discharge Temperature Winter Min Reset Setpoint |  | dischargeTempWinterMinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,discharge,air,temp,winter,min,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeTempWinterSp | dischargeTempWinterSp | Discharge Temperature Winter Setpoint | Discharge Temperature Winter Setpoint |  | dischargeTempWinterSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,discharge,air,temp,winter,effective,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeVelocity | dischargeVelocityXXXX | Discharge Velocity | Discharge Velocity XX |  | dischargeVelocity(\d{0,4}) | Yes | Yes | No | Number |  |  | feet_per_minute | meters_per_second | 1 | 1 |  |  | common,discharge,air,velocity,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,FPB,RTU,VAV,ZD,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeVelocityPressure | dischargeVelocityXXXXPressure | Discharge Velocity Pressure | Discharge Velocity XX Pressure |  | dischargeVelocity(\d{0,4})Pressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | common,discharge,air,dynamic,pressure,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,FPB,RTU,VAV,ZD,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dischargeVelocityPressureSp | dischargeVelocityXXXXPressureSp | Discharge Velocity Pressure Setpoint | Discharge Velocity XX Pressure Setpoint |  | dischargeVelocity(\d{0,4})PressureSp | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | common,discharge,air,dynamic,pressure,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,FPB,RTU,VAV,ZD,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
divertingValve | divertingValveXXXX | Diverting Valve Command | Diverting Valve XX Command |  | divertingValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | divert,valve,position,cmd | CWS,HWS,TWR,WS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
divertingValveEnableSp | divertingValveXXXXEnableSp | Diverting Valve Enable Setpoint | Diverting Valve XX Enable Setpoint |  | divertingValve(\d{0,4})EnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | divert,valve,enable,sp | CWS,HWS,TWR,WS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
divertingValveFb | divertingValveXXXXFb | Diverting Valve Feedback | Diverting Valve XX Feedback |  | divertingValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | divert,valve,position,sensor | CWS,HWS,TWR,WS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
divertingValveOvr | divertingValveXXXXOvr | Diverting Valve Override | Diverting Valve XX Override |  | divertingValve(\d{0,4})Ovr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | divert,valve,position,ovr | CWS,HWS,TWR,WS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
door | doorXXXX | Door Command | Door XX Command |  | door(\d{0,4}) | Yes | Yes | No | Bool | Open/Closed | Open/Closed | [6 empty] | door,status,cmd | DAC,SEC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
doorEnterReader | doorXXXXEnterReader | Door Enter Reader | Door XX Enter Reader |  | door(\d{0,4})EnterReader | Yes | Yes | No | Bool | Access Granted/Access Denied | Access Granted/Access Denied | [6 empty] | door,enter,reader | DOOR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
doorExitReader | doorXXXXExitReader | Door Exit Reader | Door XX Exit Reader |  | door(\d{0,4})ExitReader | Yes | Yes | No | Bool | Access Granted/Access Denied | Access Granted/Access Denied | [6 empty] | door,exit,reader | DOOR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
doorForcedOpenAlarm | doorXXXXForcedOpenAlarm | Door Forced Open Alarm | Door XX Forced Open Alarm |  | door(\d{0,4})ForcedOpenAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | door,forcedOpen,alarm | DOOR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
doorHeldOpenAlarm | doorXXXXHeldOpenAlarm | Door Held Open Alarm | Door XX Held Open Alarm |  | door(\d{0,4})HeldOpenAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | door,heldOpen,alarm | DOOR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
doorRex | doorXXXXRex | Door Request to Exit | Door XX Request to Exit |  | door(\d{0,4})Rex | Yes | Yes | No | Bool | Request/No Request | Request/No Request | [6 empty] | door,rex | DOOR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
doorStatus | doorXXXXStatus | Door Status | Door XX Status |  | door(\d{0,4})Status | Yes | Yes | No | Bool | Open/Closed | Open/Closed | [6 empty] | door,status,sensor | DAC,DOOR,SEC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
doorStrike | doorXXXXStrike | Door Strike | Door XX Strike |  | door(\d{0,4})Strike | Yes | Yes | No | Bool | Locked/Unlocked | Locked/Unlocked | [6 empty] | door,strike | DOOR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
drainPanAlarm | drainPanAlarm | Drain Pan Alarm | Drain Pan Alarm |  | drainPanAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | drain,pan,alarm | CRAC,CRAH,DHU,DOAS,EC,ERU,HP,HRU,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
drainValve | drainValveXXXX | Drain Valve Command | Drain Valve XX Command |  | drainValve(\d{0,4}) | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | drain,valve,status,cmd | SMP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
drainValveFb | drainValveXXXXFb | Drain Valve Feedback | Drain Valve XX Feedback |  | drainValve(\d{0,4})Fb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | drain,valve,status,sensor | SMP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
driveAlarm | driveAlarm | Drive Alarm | Drive Alarm |  | driveAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | drive,common,alarm | VFD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
driveAlarmCode | driveAlarmCode | Drive Alarm Code | Drive Alarm Code |  | driveAlarmCode | Yes | Yes | No | Str | [8 empty] | drive,alarm,code | VFD | 2.15 (Released)
driveAlarmReset | driveAlarmReset | Drive Alarm Reset | Drive Alarm Reset |  | driveAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | drive,reset,alarm | VFD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
driveBypass | driveBypass | Drive Bypass | Drive Bypass |  | driveBypass | Yes | Yes | No | Bool | Bypass/Normal | Bypass/Normal | [6 empty] | drive,bypass,sensor | VFD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
drive | drive | Drive Command | Drive Command |  | drive | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | drive,status,cmd,common | VFD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
driveCurrent | driveCurrent | Drive Current | Drive Current |  | driveCurrent | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | drive,current,sensor | VFD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
driveDCVoltage | driveDCVoltage | Drive DC Voltage | Drive DC Voltage |  | driveDCVoltage | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  |  | drive,dcVolt,sensor | VFD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
driveDirection | driveDirection | Drive Direction Comamnd | Drive Direction Comamnd |  | driveDirection | Yes | Yes | No | Bool | Forward/Reverse | Forward/Reverse | [6 empty] | drive,direction,cmd | VFD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
driveDirectionStatus | driveDirectionStatus | Drive Direction Status | Drive Direction Status |  | driveDirectionStatus | Yes | Yes | No | Bool | Forward/Reverse | Forward/Reverse | [6 empty] | drive,direction,sensor | VFD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
driveEnergy | driveEnergy | Drive Energy | Drive Energy |  | driveEnergy | Yes | Yes | No | Number |  |  | kilowatt_hour | kilowatt_hour | 0 | 0 |  |  | drive,energy,sensor | VFD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
driveFault | driveFault | Drive Fault | Drive Fault |  | driveFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | drive,fault,common | VFD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
driveFaultCode | driveFaultCode | Drive Fault Code | Drive Fault Code |  | driveFaultCode | Yes | Yes | No | Str | [8 empty] | drive,fault,code | VFD | 2.15 (Released)
driveFaultReset | driveFaultReset | Drive Fault Reset | Drive Fault Reset |  | driveFaultReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | drive,fault,reset | VFD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
driveFrequency | driveFrequency | Drive Frequency | Drive Frequency |  | driveFrequency | Yes | Yes | No | Number |  |  | hertz | hertz | 1 | 1 |  |  | drive,freq,sensor | VFD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
driveHandMode | driveHandMode | Drive Hand/Auto Mode | Drive Hand/Auto Mode |  | driveHandMode | Yes | Yes | No | Bool | Hand/Auto | Hand/Auto | [6 empty] | drive,handMode,sensor | VFD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
driveMotorSpeed | driveMotorSpeed | Drive Motor Speed Command | Drive Motor Speed Command |  | driveMotorSpeed | Yes | Yes | No | Number |  |  | revolutions_per_minute | revolutions_per_minute | 0 | 0 |  |  | drive,motorSpeed,sensor | VFD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
driveMotorTemp | driveMotorTemp | Drive Motor Temperature | Drive Motor Temperature |  | driveMotorTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | drive,motorTemp,sensor | VFD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
drivePowerReal | drivePowerReal | Drive Real Power | Drive Real Power |  | drivePowerReal | Yes | Yes | No | Number |  |  | kilowatt | kilowatt | 1 | 1 |  | N | drive,power,real,sensor | VFD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
driveRuntime | driveRuntime | Drive Runtime | Drive Runtime |  | driveRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | VFD | 2.15 (Released),2.16 (Pre-Release)
driveSpeed | driveSpeed | Drive Speed Command | Drive Speed Command |  | driveSpeed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | drive,speed,cmd | VFD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
driveSpeedFb | driveSpeedFb | Drive Speed Feedback | Drive Speed Feedback |  | driveSpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | drive,speed,sensor | VFD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
driveSpeedMaxSp | driveSpeedMaxSp | Drive Speed Max Setpoint | Drive Speed Max Setpoint |  | driveSpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | drive,speed,max,sp | VFD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
driveSpeedMinSp | driveSpeedMinSp | Drive Speed Min Setpoint | Drive Speed Min Setpoint |  | driveSpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | drive,speed,min,sp | VFD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
driveSpeedOvr | driveSpeedOvr | Drive Speed Override | Drive Speed Override |  | driveSpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | drive,speed,ovr | VFD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
driveStarts | driveStarts | Drive Starts | Drive Starts |  | driveStarts | Yes | No | No | Number |  |  |  |  | 0 | 0 |  |  | drive,starts,sensor | VFD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
driveStatus | driveStatus | Drive Status | Drive Status |  | driveStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | drive,status,sensor | VFD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
driveTemp | driveTemp | Drive Temperature | Drive Temperature |  | driveTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | drive,temp,sensor | VFD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
driveTorque | driveTorque | Drive Torque | Drive Torque |  | driveTorque | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | drive,torque,sensor | VFD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
driveVoltage | driveVoltage | Drive Voltage | Drive Voltage |  | driveVoltage | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  | N | drive,volt,sensor | VFD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
driveWarning | driveWarning | Drive Warning | Drive Warning |  | driveWarning | Yes | Yes | No | Bool | Warning/Normal | Warning/Normal | [6 empty] | drive,warning,common | VFD | 2.14,2.15 (Released),2.16 (Pre-Release)
dryCooler | dryCooler | Dry Cooler | Dry Cooler |  | dryCooler | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | dryCooler,status,cmd | DRY | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dryCoolerFanSpeed | dryCoolerFanXXXXSpeed | Dry Cooler Fan Speed Command | Dry Cooler Fan XX Speed Command |  | dryCoolerFan(\w{0,4}(?=[A-Z]¦$))Speed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | dryCooler,air,fan,speed,cmd | DRY | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dryCoolerFanSpeedFb | dryCoolerFanXXXXSpeedFb | Dry Cooler Fan Speed Feedback | Dry Cooler Fan XX Speed Feedback |  | dryCoolerFan(\w{0,4}(?=[A-Z]¦$))SpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | dryCooler,air,fan,speed,sensor | DRY | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
dryCoolerStatus | dryCoolerStatus | Dry Cooler Status | Dry Cooler Status |  | dryCoolerStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | dryCooler,status,sensor | DRY | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
earthquakeLevelAlarm | earthquakeLevelXXXXAlarm | Earthquake Level Alarm | Earthquake Level XX Alarm |  | earthquakeLevel(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | earthquake,level,alarm | GBL,MSC,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
econDisableHumiditySp | econDisableHumiditySp | Economizer Disable Humidity Setpoint | Economizer Disable Humidity Setpoint |  | econDisableHumiditySp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | econ,disable,humidity,effective,sp | AHU,CRAC,CRAH,DOAS,RTU,UV | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
econDisableSp | econDisableSp | Economizer Disable Temperature Setpoint | Economizer Disable Temperature Setpoint |  | econDisableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | econ,disable,temp,effective,sp | AHU,CRAC,CRAH,DOAS,RTU,UV | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
econEnable | econEnable | Economizer Enable Command | Economizer Enable Command |  | econEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | econ,enable,cmd | AHU,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
econEnableDelayOffSp | econEnableDelayOffSp | Economizer Enable Delay Off Setpoint | Economizer Enable Delay Off Setpoint |  | econEnableDelayOffSp | No | No | No | Number |  |  | minute | minute | 0 | 0 |  |  | econ,enable,delay,off,sp | AHU,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
econEnableDelayOnSp | econEnableDelayOnSp | Economizer Enable Delay On Setpoint | Economizer Enable Delay On Setpoint |  | econEnableDelayOnSp | No | No | No | Number |  |  | minute | minute | 0 | 0 |  |  | econ,enable,delay,on,sp | AHU,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
econEnableDelayOnOffSp | econEnableDelayOnOffSp | Economizer Enable Delay On-Off Setpoint | Economizer Enable Delay On-Off Setpoint |  | econEnableDelayOnOffSp | No | No | No | Number |  |  | minute | minute | 0 | 0 |  |  | econ,enable,delay,onOff,sp | AHU,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
econEnableDewpointSp | econEnableDewpointSp | Economizer Enable Dewpoint Setpoint | Economizer Enable Dewpoint Setpoint |  | econEnableDewpointSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | econ,enable,dewpoint,sp | AHU,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
econEnableDeltaSp | econEnableDeltaSp | Economizer Enable Differential Setpoint | Economizer Enable Differential Setpoint |  | econEnableDeltaSp | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | econ,enable,temp,delta,sp | AHU,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
econEnableEnthalpyDb | econEnableEnthalpyDb | Economizer Enable Enthalpy Deadband | Economizer Enable Enthalpy Deadband |  | econEnableEnthalpyDb | No | No | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | econ,enable,enthalpy,deadband,sp | AHU,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
econEnableEnthalpyDeltaSp | econEnableEnthalpyDeltaSp | Economizer Enable Enthalpy Delta Setpoint | Economizer Enable Enthalpy Delta Setpoint |  | econEnableEnthalpyDeltaSp | No | No | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | econ,enable,enthalpy,delta,sp | AHU,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
econEnableEnthalpySp | econEnableEnthalpySp | Economizer Enable Enthalpy Setpoint | Economizer Enable Enthalpy Setpoint |  | econEnableEnthalpySp | No | No | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | econ,enable,enthalpy,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
econEnableHumidityDb | econEnableHumidityDb | Economizer Enable Humidity Deadband | Economizer Enable Humidity Deadband |  | econEnableHumidityDb | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | econ,enable,humidity,deadband,sp | AHU,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
econEnableHumidityDeltaSp | econEnableHumidityDeltaSp | Economizer Enable Humidity Differential Setpoint | Economizer Enable Humidity Differential Setpoint |  | econEnableHumidityDeltaSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | econ,enable,humidity,delta,sp | AHU,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
econEnableHumiditySp | econEnableHumiditySp | Economizer Enable Humidity Setpoint | Economizer Enable Humidity Setpoint |  | econEnableHumiditySp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | econ,enable,humidity,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
econEnableOvr | econEnableOvr | Economizer Enable Override | Economizer Enable Override |  | econEnableOvr | No | No | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | econ,enable,ovr | AHU,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
econEnableDb | econEnableDb | Economizer Enable Temperature Deadband | Economizer Enable Temperature Deadband |  | econEnableDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | econ,enable,temp,deadband,sp | AHU,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
econEnableLoSp | econEnableLoSp | Economizer Enable Temperature Low Setpoint | Economizer Enable Temperature Low Setpoint |  | econEnableLoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | econ,enable,temp,low,sp | AHU,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,UV,HP | 2.14,2.15 (Released),2.16 (Pre-Release)
econEnableSp | econEnableSp | Economizer Enable Temperature Setpoint | Economizer Enable Temperature Setpoint |  | econEnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | econ,enable,temp,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
econMode | econMode | Economizer Mode | Economizer Mode |  | econMode | Yes | No | No | Str |  | DryBulb/SingleEnthalpy/DualEnthalpy/Off | [6 empty] | econ,mode,sp | AHU,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
electronicExpansionValve | electronicExpansionValve | Electronic Expansion Valve | Electronic Expansion Valve |  | electronicExpansionValve | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | electronic,expansion,valve,status,cmd | AC,AHU,ATU,CLR,CMP,FCU,HP,RTU,UV,VRF,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
shutdownMode | shutdownMode | Emergency Shutdown Mode | Emergency Shutdown Mode |  | shutdownMode | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | shutdown,mode,cmd | AHU,ATU,BLR,CLR,CRAC,CRAH,CUH,CWS,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,GEO,HP,HRU,HWS,MAU,RTU,SMS,TWR,UV,VAV,WS,FCU,HP,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
shutdownModeOvr | shutdownModeOvr | Emergency Shutdown Mode Override | Emergency Shutdown Mode Override |  | shutdownModeOvr | No | No | No | Bool | On/Off | On/Off | [6 empty] | shutdown,mode,ovr | AHU,ATU,BLR,CLR,CRAC,CRAH,CUH,CWS,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,GEO,HP,HRU,HWS,MAU,RTU,SMS,TWR,UV,VAV,WS,FCU,HP,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
emergencyStop | emergencyStop | Emergency Stop | Emergency Stop |  | emergencyStop | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | emergencyStop,status,cmd | AHU,CRAC,CRAH,CU,DHU,DOAS,EC,MAU,MSC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
energy | energy | Energy | Energy |  | energy | Yes | Yes | Yes | Number |  |  | kilowatt_hour | kilowatt_hour | 0 | 0 |  | N | common,energy,general,sensor | AHU,ATS,ATU,BLR,BRK,CLR,CRAC,CRAH,CU,CUH,CWS,DH,DHU,DOAS,EC,EF,FCU,FPB,GEO,HP,HWS,MAU,PDU,PM,PRLY,PV,RPP,RTU,SMS,STS,TVS,TWR,UPS,UV,VAV,VPM,FCU,HP,HX | 2.15 (Released),2.16 (Pre-Release)
energyRealPhaseA | energyRealPhaseA | Energy (Phase A) | Energy (Phase A) |  | energyRealPhaseA | Yes | Yes | Yes | Number |  |  | kilowatt_hour | kilowatt_hour | 0 | 0 |  | A | common,energy,general,sensor | ATS,BRK,INV,PDU,PFC,PM,RECT,RPP,STS,TVS,UPS | 2.15 (Released),2.16 (Pre-Release)
energyRealPhaseB | energyRealPhaseB | Energy (Phase B) | Energy (Phase B) |  | energyRealPhaseB | Yes | Yes | Yes | Number |  |  | kilowatt_hour | kilowatt_hour | 0 | 0 |  | B | common,energy,general,sensor | ATS,BRK,INV,PDU,PFC,PM,RECT,RPP,STS,TVS,UPS | 2.15 (Released),2.16 (Pre-Release)
energyRealPhaseC | energyRealPhaseC | Energy (Phase C) | Energy (Phase C) |  | energyRealPhaseC | Yes | Yes | Yes | Number |  |  | kilowatt_hour | kilowatt_hour | 0 | 0 |  | C | common,energy,general,sensor | ATS,BRK,INV,PDU,PFC,PM,RECT,RPP,STS,TVS,UPS | 2.15 (Released),2.16 (Pre-Release)
energyMax | energyMax | Energy Maximum | Energy Maximum |  | energyMax | Yes | No | Yes | Number |  |  | kilowatt_hour | kilowatt_hour | 0 | 0 |  |  | common,energy,max,calc | PRLY | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
energyMaxDateTime | energyMaxDateTime | Energy Maximum Date & Time | Energy Maximum Date & Time |  | energyMaxDateTime | Yes | No | No | Str | [8 empty] | common,energy,dateTime,calc | PRLY | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
energyRecoveryMode | energyRecoveryMode | Energy Recovery Mode | Energy Recovery Mode |  | energyRecoveryMode | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | energy,recovery,mode,cmd | AHU,CRAC,CRAH,DHU,DOAS,EC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
environmentalIndex | environmentalIndex | Environmental Index | Environmental Index |  | environmentalIndex | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | environmentalIndex,calc | FPB,VAV | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
equipDescription | equipDescription | Equipment Description | Equipment Description |  | equipDescription | No | No | No | Str | [8 empty] | blacklist | AC,AFMS,AHU,ATS,ATU,BATT,BLND,BLR,BRK,BTU,CF,CLR,CM,CMP,CRAC,CRAH,CU,CUH,CWS,DAC,DCU,DCWS,DH,DHU,DHWS,DOAS,DOOR,DRY,EC,EF,ELV,ENC,ERU,FC,FCU,FDS,FEXT,FP,FPB,FSD,FSEP,FSS,GBL,GDS,GEN,GEO,GINT,GM,HDS,HP,HRU,HT,HUM,HVHS,HVLS,HWS,INV,LDS,LS,LTGE,LTGI,MAU,MMS,MSC,NC,OF,PDU,PFC,PH,PINT,PIU,PM,PMP,PRLY,PV,PWS,REC,RECT,RF,RFG,ROS,RP,RPC,RPF,RPP,RRS,RTU,SCRB,SEC,SKYL,SM,SMEX,SMP,SMS,STS,SUP,TF,TNK,TRN,TVS,TWR,UH,UPS,UV,VAV,VBTU,VFD,VGM,VPM,VRF,VWM,WH,WM,WNDW,WS,WSS,WTHR,WTS,XFMR,ZD,ZN,CDA,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
equipName | equipName | Equipment Display Name | Equipment Display Name |  | equipName | No | No | No | Str | [8 empty] | blacklist | AC,AFMS,AHU,ATS,ATU,BATT,BLND,BLR,BRK,BTU,CF,CLR,CM,CMP,CRAC,CRAH,CU,CUH,CWS,DAC,DCU,DCWS,DH,DHU,DHWS,DOAS,DOOR,DRY,EC,EF,ELV,ENC,ERU,FC,FCU,FDS,FEXT,FP,FPB,FSD,FSEP,FSS,GBL,GDS,GEN,GEO,GINT,GM,HDS,HP,HRU,HT,HUM,HVHS,HVLS,HWS,INV,LDS,LS,LTGE,LTGI,MAU,MMS,MSC,NC,OF,PDU,PFC,PH,PINT,PIU,PM,PMP,PRLY,PV,PWS,REC,RECT,RF,RFG,ROS,RP,RPC,RPF,RPP,RRS,RTU,SCRB,SEC,SKYL,SM,SMEX,SMP,SMS,STS,SUP,TF,TNK,TRN,TVS,TWR,UH,UPS,UV,VAV,VBTU,VFD,VGM,VPM,VRF,VWM,WH,WM,WNDW,WS,WSS,WTHR,WTS,XFMR,ZD,ZN,CDA,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
equipNotes | equipNotes | Equipment Notes | Equipment Notes |  | equipNotes | No | No | No | Str | [8 empty] | blacklist | AC,AFMS,AHU,ATS,ATU,BATT,BLND,BLR,BRK,BTU,CF,CLR,CM,CMP,CRAC,CRAH,CU,CUH,CWS,DAC,DCU,DCWS,DH,DHU,DHWS,DOAS,DOOR,DRY,EC,EF,ELV,ENC,ERU,FC,FCU,FDS,FEXT,FP,FPB,FSD,FSEP,FSS,GBL,GDS,GEN,GEO,GINT,GM,HDS,HP,HRU,HT,HUM,HVHS,HVLS,HWS,INV,LDS,LS,LTGE,LTGI,MAU,MMS,MSC,NC,OF,PDU,PFC,PH,PINT,PIU,PM,PMP,PRLY,PV,PWS,REC,RECT,RF,RFG,ROS,RP,RPC,RPF,RPP,RRS,RTU,SCRB,SEC,SKYL,SM,SMEX,SMP,SMS,STS,SUP,TF,TNK,TRN,TVS,TWR,UH,UPS,UV,VAV,VBTU,VFD,VGM,VPM,VRF,VWM,WH,WM,WNDW,WS,WSS,WTHR,WTS,XFMR,ZD,ZN,CDA,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
equipRevision | equipRevision | Equipment Revision | Equipment Revision |  | equipRevision | No | No | No | Str | [8 empty] | blacklist | AC,AFMS,AHU,ATS,ATU,BATT,BLND,BLR,BRK,BTU,CF,CLR,CM,CMP,CRAC,CRAH,CU,CUH,CWS,DAC,DCU,DCWS,DH,DHU,DHWS,DOAS,DOOR,DRY,EC,EF,ELV,ENC,ERU,FC,FCU,FDS,FEXT,FP,FPB,FSD,FSEP,FSS,GBL,GDS,GEN,GEO,GINT,GM,HDS,HP,HRU,HT,HUM,HVHS,HVLS,HWS,INV,LDS,LS,LTGE,LTGI,MAU,MMS,MSC,NC,OF,PDU,PFC,PH,PINT,PIU,PM,PMP,PRLY,PV,PWS,REC,RECT,RF,RFG,ROS,RP,RPC,RPF,RPP,RRS,RTU,SCRB,SEC,SKYL,SM,SMEX,SMP,SMS,STS,SUP,TF,TNK,TRN,TVS,TWR,UH,UPS,UV,VAV,VBTU,VFD,VGM,VPM,VRF,VWM,WH,WM,WNDW,WS,WSS,WTHR,WTS,XFMR,ZD,ZN,CDA,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
equipStatLocation | equipStatLocation | Equipment Sensor Location | Equipment Sensor Location |  | equipStatLocation | No | No | No | Str | [8 empty] | blacklist | AC,AFMS,AHU,ATS,ATU,BATT,BLND,BLR,BRK,BTU,CF,CLR,CM,CMP,CRAC,CRAH,CU,CUH,CWS,DAC,DCU,DCWS,DH,DHU,DHWS,DOAS,DOOR,DRY,EC,EF,ELV,ENC,ERU,FC,FCU,FDS,FEXT,FP,FPB,FSD,FSEP,FSS,GBL,GDS,GEN,GEO,GINT,GM,HDS,HP,HRU,HT,HUM,HVHS,HVLS,HWS,INV,LDS,LS,LTGE,LTGI,MAU,MMS,MSC,NC,OF,PDU,PFC,PH,PINT,PIU,PM,PMP,PRLY,PV,PWS,REC,RECT,RF,RFG,ROS,RP,RPC,RPF,RPP,RRS,RTU,SCRB,SEC,SKYL,SM,SMEX,SMP,SMS,STS,SUP,TF,TNK,TRN,TVS,TWR,UH,UPS,UV,VAV,VBTU,VFD,VGM,VPM,VRF,VWM,WH,WM,WNDW,WS,WSS,WTHR,WTS,XFMR,ZD,ZN,CDA,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
equipServedBy | equipServedBy | Equipment Served By | Equipment Served By |  | equipServedBy | No | No | No | Str | [8 empty] | blacklist | AC,AFMS,AHU,ATS,ATU,BATT,BLND,BLR,BRK,BTU,CF,CLR,CM,CMP,CRAC,CRAH,CU,CUH,CWS,DAC,DCU,DCWS,DH,DHU,DHWS,DOAS,DOOR,DRY,EC,EF,ELV,ENC,ERU,FC,FCU,FDS,FEXT,FP,FPB,FSD,FSEP,FSS,GBL,GDS,GEN,GEO,GINT,GM,HDS,HP,HRU,HT,HUM,HVHS,HVLS,HWS,INV,LDS,LS,LTGE,LTGI,MAU,MMS,MSC,NC,OF,PDU,PFC,PH,PINT,PIU,PM,PMP,PRLY,PV,PWS,REC,RECT,RF,RFG,ROS,RP,RPC,RPF,RPP,RRS,RTU,SCRB,SEC,SKYL,SM,SMEX,SMP,SMS,STS,SUP,TF,TNK,TRN,TVS,TWR,UH,UPS,UV,VAV,VBTU,VFD,VGM,VPM,VRF,VWM,WH,WM,WNDW,WS,WSS,WTHR,WTS,XFMR,ZD,ZN,CDA,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
equipServes | equipServes | Equipment Serves | Equipment Serves |  | equipServes | No | No | No | Str | [8 empty] | blacklist | AC,AFMS,AHU,ATS,ATU,BATT,BLND,BLR,BRK,BTU,CF,CLR,CM,CMP,CRAC,CRAH,CU,CUH,CWS,DAC,DCU,DCWS,DH,DHU,DHWS,DOAS,DOOR,DRY,EC,EF,ELV,ENC,ERU,FC,FCU,FDS,FEXT,FP,FPB,FSD,FSEP,FSS,GBL,GDS,GEN,GEO,GINT,GM,HDS,HP,HRU,HT,HUM,HVHS,HVLS,HWS,INV,LDS,LS,LTGE,LTGI,MAU,MMS,MSC,NC,OF,PDU,PFC,PH,PINT,PIU,PM,PMP,PRLY,PV,PWS,REC,RECT,RF,RFG,ROS,RP,RPC,RPF,RPP,RRS,RTU,SCRB,SEC,SKYL,SM,SMEX,SMP,SMS,STS,SUP,TF,TNK,TRN,TVS,TWR,UH,UPS,UV,VAV,VBTU,VFD,VGM,VPM,VRF,VWM,WH,WM,WNDW,WS,WSS,WTHR,WTS,XFMR,ZD,ZN,CDA,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
equipTag | equipTag | Equipment Short Name | Equipment Short Name |  | equipTag | No | No | No | Str | [8 empty] | blacklist | AC,AFMS,AHU,ATS,ATU,BATT,BLND,BLR,BRK,BTU,CF,CLR,CM,CMP,CRAC,CRAH,CU,CUH,CWS,DAC,DCU,DCWS,DH,DHU,DHWS,DOAS,DOOR,DRY,EC,EF,ELV,ENC,ERU,FC,FCU,FDS,FEXT,FP,FPB,FSD,FSEP,FSS,GBL,GDS,GEN,GEO,GINT,GM,HDS,HP,HRU,HT,HUM,HVHS,HVLS,HWS,INV,LDS,LS,LTGE,LTGI,MAU,MMS,MSC,NC,OF,PDU,PFC,PH,PINT,PIU,PM,PMP,PRLY,PV,PWS,REC,RECT,RF,RFG,ROS,RP,RPC,RPF,RPP,RRS,RTU,SCRB,SEC,SKYL,SM,SMEX,SMP,SMS,STS,SUP,TF,TNK,TRN,TVS,TWR,UH,UPS,UV,VAV,VBTU,VFD,VGM,VPM,VRF,VWM,WH,WM,WNDW,WS,WSS,WTHR,WTS,XFMR,ZD,ZN,CDA,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
equipSite | equipSite | Equipment Site Name | Equipment Site Name |  | equipSite | No | No | No | Str | [8 empty] | blacklist | AC,AFMS,AHU,ATS,ATU,BATT,BLND,BLR,BRK,BTU,CF,CLR,CM,CMP,CRAC,CRAH,CU,CUH,CWS,DAC,DCU,DCWS,DH,DHU,DHWS,DOAS,DOOR,DRY,EC,EF,ELV,ENC,ERU,FC,FCU,FDS,FEXT,FP,FPB,FSD,FSEP,FSS,GBL,GDS,GEN,GEO,GINT,GM,HDS,HP,HRU,HT,HUM,HVHS,HVLS,HWS,INV,LDS,LS,LTGE,LTGI,MAU,MMS,MSC,NC,OF,PDU,PFC,PH,PINT,PIU,PM,PMP,PRLY,PV,PWS,REC,RECT,RF,RFG,ROS,RP,RPC,RPF,RPP,RRS,RTU,SCRB,SEC,SKYL,SM,SMEX,SMP,SMS,STS,SUP,TF,TNK,TRN,TVS,TWR,UH,UPS,UV,VAV,VBTU,VFD,VGM,VPM,VRF,VWM,WH,WM,WNDW,WS,WSS,WTHR,WTS,XFMR,ZD,ZN,CDA,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
equipStatus | equipStatus | Equipment Status | Equipment Status |  | equipStatus | No | No | No | Str | Incomplete/Complete | Incomplete/Complete | [6 empty] | blacklist | AC,AFMS,AHU,ATS,ATU,BATT,BLND,BLR,BRK,BTU,CF,CLR,CM,CMP,CRAC,CRAH,CU,CUH,CWS,DAC,DCU,DCWS,DH,DHU,DHWS,DOAS,DOOR,DRY,EC,EF,ELV,ENC,ERU,FC,FCU,FDS,FEXT,FP,FPB,FSD,FSEP,FSS,GBL,GDS,GEN,GEO,GINT,GM,HDS,HP,HRU,HT,HUM,HVHS,HVLS,HWS,INV,LDS,LS,LTGE,LTGI,MAU,MMS,MSC,NC,OF,PDU,PFC,PH,PINT,PIU,PM,PMP,PRLY,PV,PWS,REC,RECT,RF,RFG,ROS,RP,RPC,RPF,RPP,RRS,RTU,SCRB,SEC,SKYL,SM,SMEX,SMP,SMS,STS,SUP,TF,TNK,TRN,TVS,TWR,UH,UPS,UV,VAV,VBTU,VFD,VGM,VPM,VRF,VWM,WH,WM,WNDW,WS,WSS,WTHR,WTS,XFMR,ZD,ZN,CDA,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
equipStatusMsg | equipStatusMsg | Equipment Status Message | Equipment Status Message |  | equipStatusMsg | No | No | No | Str | [8 empty] | blacklist | AC,AFMS,AHU,ATS,ATU,BATT,BLND,BLR,BRK,BTU,CF,CLR,CM,CMP,CRAC,CRAH,CU,CUH,CWS,DAC,DCU,DCWS,DH,DHU,DHWS,DOAS,DOOR,DRY,EC,EF,ELV,ENC,ERU,FC,FCU,FDS,FEXT,FP,FPB,FSD,FSEP,FSS,GBL,GDS,GEN,GEO,GINT,GM,HDS,HP,HRU,HT,HUM,HVHS,HVLS,HWS,INV,LDS,LS,LTGE,LTGI,MAU,MMS,MSC,NC,OF,PDU,PFC,PH,PINT,PIU,PM,PMP,PRLY,PV,PWS,REC,RECT,RF,RFG,ROS,RP,RPC,RPF,RPP,RRS,RTU,SCRB,SEC,SKYL,SM,SMEX,SMP,SMS,STS,SUP,TF,TNK,TRN,TVS,TWR,UH,UPS,UV,VAV,VBTU,VFD,VGM,VPM,VRF,VWM,WH,WM,WNDW,WS,WSS,WTHR,WTS,XFMR,ZD,ZN,CDA,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
evapBypassFlow | evapBypassFlowXXXX | Evaporator Bypass Flow | Evaporator Bypass Flow XX |  | evapBypassFlow(\d{0,4}) | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | chilled,water,bypass,flow,sensor | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapBypassFlowDb | evapBypassFlowXXXXDb | Evaporator Bypass Flow Deadband | Evaporator Bypass Flow XX Deadband |  | evapBypassFlow(\d{0,4})Db | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | chilled,water,bypass,flow,deadband,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapBypassFlowHiSp | evapBypassFlowXXXXHiSp | Evaporator Bypass Flow High Setpoint | Evaporator Bypass Flow XX High Setpoint |  | evapBypassFlow(\d{0,4})HiSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | chilled,water,bypass,flow,high,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapBypassFlowLoSp | evapBypassFlowXXXXLoSp | Evaporator Bypass Flow Low Setpoint | Evaporator Bypass Flow XX Low Setpoint |  | evapBypassFlow(\d{0,4})LoSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | chilled,water,bypass,flow,low,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapBypassFlowMaxSp | evapBypassFlowXXXXMaxSp | Evaporator Bypass Flow Max Reset Setpoint | Evaporator Bypass Flow XX Max Reset Setpoint |  | evapBypassFlow(\d{0,4})MaxSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | chilled,water,bypass,flow,max,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapBypassFlowMinSp | evapBypassFlowXXXXMinSp | Evaporator Bypass Flow Min Reset Setpoint | Evaporator Bypass Flow XX Min Reset Setpoint |  | evapBypassFlow(\d{0,4})MinSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | chilled,water,bypass,flow,min,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapBypassFlowSp | evapBypassFlowXXXXSp | Evaporator Bypass Flow Setpoint | Evaporator Bypass Flow XX Setpoint |  | evapBypassFlow(\d{0,4})Sp | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | chilled,water,bypass,flow,effective,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapBypassTemp | evapBypassTempXXXX | Evaporator Bypass Temperature | Evaporator Bypass Temperature XX |  | evapBypassTemp(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | chilled,water,bypass,temp,sensor | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapBypassValve | evapBypassValveXXXX | Evaporator Bypass Valve Command | Evaporator Bypass Valve XX Command |  | evapBypassValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | chilled,water,bypass,valve,position,cmd | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapBypassValveFb | evapBypassValveXXXXFb | Evaporator Bypass Valve Feedback | Evaporator Bypass Valve XX Feedback |  | evapBypassValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | chilled,water,bypass,valve,position,sensor | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapEnergy | evapEnergy | Evaporator Energy | Evaporator Energy |  | evapEnergy | Yes | Yes | No | Number |  |  | tons_refrigeration_hour | tons_refrigeration_hour | 0 | 0 |  |  | chilled,water,energy,common,sensor | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapEnteringFlow | evapEnteringFlowXXXX | Evaporator Entering Flow | Evaporator Entering Flow XX |  | evapEnteringFlow(\d{0,4}) | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | chilled,water,entering,flow,sensor | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapEnteringFlowDb | evapEnteringFlowXXXXDb | Evaporator Entering Flow Deadband | Evaporator Entering Flow XX Deadband |  | evapEnteringFlow(\d{0,4})Db | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | chilled,water,entering,flow,deadband,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapEnteringFlowHiSp | evapEnteringFlowXXXXHiSp | Evaporator Entering Flow High Setpoint | Evaporator Entering Flow XX High Setpoint |  | evapEnteringFlow(\d{0,4})HiSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | chilled,water,entering,flow,high,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapEnteringFlowLoSp | evapEnteringFlowXXXXLoSp | Evaporator Entering Flow Low Setpoint | Evaporator Entering Flow XX Low Setpoint |  | evapEnteringFlow(\d{0,4})LoSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | chilled,water,entering,flow,low,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapEnteringFlowMaxSp | evapEnteringFlowXXXXMaxSp | Evaporator Entering Flow Max Setpoint | Evaporator Entering Flow XX Max Setpoint |  | evapEnteringFlow(\d{0,4})MaxSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | chilled,water,entering,flow,max,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapEnteringFlowMinSp | evapEnteringFlowXXXXMinSp | Evaporator Entering Flow Min Setpoint | Evaporator Entering Flow XX Min Setpoint |  | evapEnteringFlow(\d{0,4})MinSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | chilled,water,entering,flow,min,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapEnteringFlowSp | evapEnteringFlowXXXXSp | Evaporator Entering Flow Setpoint | Evaporator Entering Flow XX Setpoint |  | evapEnteringFlow(\d{0,4})Sp | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | chilled,water,entering,flow,effective,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapEnteringIsoValveAlarm | evapEnteringIsoValveXXXXAlarm | Evaporator Entering Isolation Valve Alarm | Evaporator Entering Isolation Valve XX Alarm |  | evapEnteringIsoValve(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | chilled,water,entering,iso,valve,alarm | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapEnteringIsoValve | evapEnteringIsoValveXXXX | Evaporator Entering Isolation Valve Command | Evaporator Entering Isolation Valve XX Command |  | evapEnteringIsoValve(\d{0,4}) | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | chilled,water,entering,iso,valve,position,cmd | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapEnteringIsoValveFb | evapEnteringIsoValveXXXXFb | Evaporator Entering Isolation Valve Feedback | Evaporator Entering Isolation Valve XX Feedback |  | evapEnteringIsoValve(\d{0,4})Fb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | chilled,water,entering,iso,valve,position,sensor | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapEnteringIsoValveOvr | evapEnteringIsoValveXXXXOvr | Evaporator Entering Isolation Valve Override | Evaporator Entering Isolation Valve XX Override |  | evapEnteringIsoValve(\d{0,4})Ovr | No | No | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | chilled,water,entering,iso,valve,position,ovr | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapEnteringPressure | evapEnteringPressureXXXX | Evaporator Entering Pressure | Evaporator Entering Pressure XX |  | evapEnteringPressure(\d{0,4}) | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | chilled,water,entering,pressure,general,sensor | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapEnteringTemp | evapEnteringTempXXXX | Evaporator Entering Temperature | Evaporator Entering Temperature XX |  | evapEnteringTemp(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | chilled,water,entering,temp,sensor | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapFlowFault | evapFlowFault | Evaporator Flow Fault | Evaporator Flow Fault |  | evapFlowFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | chilled,water,flow,fault | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapFlowLoAlarm | evapFlowLoAlarm | Evaporator Flow Low Alarm | Evaporator Flow Low Alarm |  | evapFlowLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | chilled,water,flow,low,alarm | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapFlowStatus | evapFlowStatus | Evaporator Flow Status | Evaporator Flow Status |  | evapFlowStatus | Yes | Yes | No | Bool | Flow/No Flow | Flow/No Flow | [6 empty] | chilled,water,flow,status,sensor | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapLeavingFlow | evapLeavingFlowXXXX | Evaporator Leaving Flow | Evaporator Leaving Flow XX |  | evapLeavingFlow(\d{0,4}) | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | chilled,water,leaving,flow,sensor | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapLeavingFlowDb | evapLeavingFlowXXXXDb | Evaporator Leaving Flow Deadband | Evaporator Leaving Flow XX Deadband |  | evapLeavingFlow(\d{0,4})Db | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | chilled,water,leaving,flow,deadband,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapLeavingFlowHiSp | evapLeavingFlowXXXXHiSp | Evaporator Leaving Flow High Setpoint | Evaporator Leaving Flow XX High Setpoint |  | evapLeavingFlow(\d{0,4})HiSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | chilled,water,leaving,flow,high,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapLeavingFlowLoSp | evapLeavingFlowXXXXLoSp | Evaporator Leaving Flow Low Setpoint | Evaporator Leaving Flow XX Low Setpoint |  | evapLeavingFlow(\d{0,4})LoSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | chilled,water,leaving,flow,low,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapLeavingFlowMaxSp | evapLeavingFlowXXXXMaxSp | Evaporator Leaving Flow Max Setpoint | Evaporator Leaving Flow XX Max Setpoint |  | evapLeavingFlow(\d{0,4})MaxSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | chilled,water,leaving,flow,max,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapLeavingFlowMinSp | evapLeavingFlowXXXXMinSp | Evaporator Leaving Flow Min Setpoint | Evaporator Leaving Flow XX Min Setpoint |  | evapLeavingFlow(\d{0,4})MinSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | chilled,water,leaving,flow,min,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapLeavingFlowSp | evapLeavingFlowXXXXSp | Evaporator Leaving Flow Setpoint | Evaporator Leaving Flow XX Setpoint |  | evapLeavingFlow(\d{0,4})Sp | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | chilled,water,leaving,flow,effective,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapLeavingIsoValveAlarm | evapLeavingIsoValveXXXXAlarm | Evaporator Leaving Isolation Valve Alarm | Evaporator Leaving Isolation Valve XX Alarm |  | evapLeavingIsoValve(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | chilled,water,leaving,iso,valve,alarm | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapLeavingIsoValve | evapLeavingIsoValveXXXX | Evaporator Leaving Isolation Valve Command | Evaporator Leaving Isolation Valve XX Command |  | evapLeavingIsoValve(\d{0,4}) | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | chilled,water,leaving,iso,valve,position,cmd | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapLeavingIsoValveFb | evapLeavingIsoValveXXXXFb | Evaporator Leaving Isolation Valve Feedback | Evaporator Leaving Isolation Valve XX Feedback |  | evapLeavingIsoValve(\d{0,4})Fb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | chilled,water,leaving,iso,valve,position,sensor | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapLeavingIsoValveOvr | evapLeavingIsoValveXXXXOvr | Evaporator Leaving Isolation Valve Override | Evaporator Leaving Isolation Valve XX Override |  | evapLeavingIsoValve(\d{0,4})Ovr | No | No | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | chilled,water,leaving,iso,valve,position,ovr | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapLeavingPressure | evapLeavingPressureXXXX | Evaporator Leaving Pressure | Evaporator Leaving Pressure XX |  | evapLeavingPressure(\d{0,4}) | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | chilled,water,leaving,pressure,general,sensor | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapLeavingTemp | evapLeavingTempXXXX | Evaporator Leaving Temperature | Evaporator Leaving Temperature XX |  | evapLeavingTemp(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | chilled,water,leaving,temp,sensor | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapLeavingTempDb | evapLeavingTempXXXXDb | Evaporator Leaving Temperature Deadband | Evaporator Leaving Temperature XX Deadband |  | evapLeavingTemp(\d{0,4})Db | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | chilled,water,leaving,temp,deadband,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapLeavingTempHiSp | evapLeavingTempXXXXHiSp | Evaporator Leaving Temperature High Setpoint | Evaporator Leaving Temperature XX High Setpoint |  | evapLeavingTemp(\d{0,4})HiSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | chilled,water,leaving,temp,high,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapLeavingTempLoSp | evapLeavingTempXXXXLoSp | Evaporator Leaving Temperature Low Setpoint | Evaporator Leaving Temperature XX Low Setpoint |  | evapLeavingTemp(\d{0,4})LoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | chilled,water,leaving,temp,low,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapLeavingTempMaxSp | evapLeavingTempXXXXMaxSp | Evaporator Leaving Temperature Max Setpoint | Evaporator Leaving Temperature XX Max Setpoint |  | evapLeavingTemp(\d{0,4})MaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | chilled,water,leaving,temp,max,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapLeavingTempMinSp | evapLeavingTempXXXXMinSp | Evaporator Leaving Temperature Min Setpoint | Evaporator Leaving Temperature XX Min Setpoint |  | evapLeavingTemp(\d{0,4})MinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | chilled,water,leaving,temp,min,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapLeavingTempSp | evapLeavingTempXXXXSp | Evaporator Leaving Temperature Setpoint | Evaporator Leaving Temperature XX Setpoint |  | evapLeavingTemp(\d{0,4})Sp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | chilled,water,leaving,temp,effective,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapLeavingTempSpOvr | evapLeavingTempXXXXSpOvr | Evaporator Leaving Temperature Setpoint Override | Evaporator Leaving Temperature XX Setpoint Override |  | evapLeavingTemp(\d{0,4})SpOvr | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | chilled,water,leaving,temp,ovr,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPower | evapPower | Evaporator Power | Evaporator Power |  | evapPower | Yes | Yes | No | Number |  |  | tons_refrigeration | tons_refrigeration | 1 | 1 |  |  | chilled,water,power,common,sensor | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPressureDelta | evapPressureDelta | Evaporator Pressure Differential | Evaporator Pressure Differential |  | evapPressureDelta | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | chilled,water,delta,pressure,common,sensor | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPressureDeltaDb | evapPressureDeltaDb | Evaporator Pressure Differential Deadband | Evaporator Pressure Differential Deadband |  | evapPressureDeltaDb | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | chilled,water,delta,pressure,deadband,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPressureDeltaHiSp | evapPressureDeltaHiSp | Evaporator Pressure Differential High Setpoint | Evaporator Pressure Differential High Setpoint |  | evapPressureDeltaHiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | chilled,water,delta,pressure,high,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPressureDeltaLoSp | evapPressureDeltaLoSp | Evaporator Pressure Differential Low Setpoint | Evaporator Pressure Differential Low Setpoint |  | evapPressureDeltaLoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | chilled,water,delta,pressure,low,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPressureDeltaMaxSp | evapPressureDeltaMaxSp | Evaporator Pressure Differential Max Setpoint | Evaporator Pressure Differential Max Setpoint |  | evapPressureDeltaMaxSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | chilled,water,delta,pressure,max,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPressureDeltaMinSp | evapPressureDeltaMinSp | Evaporator Pressure Differential Min Setpoint | Evaporator Pressure Differential Min Setpoint |  | evapPressureDeltaMinSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | chilled,water,delta,pressure,min,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPressureDeltaSp | evapPressureDeltaSp | Evaporator Pressure Differential Setpoint | Evaporator Pressure Differential Setpoint |  | evapPressureDeltaSp | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | chilled,water,delta,pressure,effective,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPumpAlarm | evapPumpXXXXAlarm | Evaporator Pump Alarm | Evaporator Pump XX Alarm |  | evapPump(\w{0,4}(?=[A-Z]¦$))Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | chilled,water,pump,common,alarm | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPumpAlarmReset | evapPumpXXXXAlarmReset | Evaporator Pump Alarm Reset | Evaporator Pump XX Alarm Reset |  | evapPump(\w{0,4}(?=[A-Z]¦$))AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | chilled,water,pump,reset,alarm | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPump | evapPumpXXXX | Evaporator Pump Command | Evaporator Pump XX Command |  | evapPump((?:(?!Lead)(?!Ovr)\w){0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | chilled,water,pump,status,cmd | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPumpCurrent | evapPumpXXXXCurrent | Evaporator Pump Current | Evaporator Pump XX Current |  | evapPump(\w{0,4}(?=[A-Z]¦$))Current | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | chilled,water,pump,current,sensor | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPumpEnable | evapPumpXXXXEnable | Evaporator Pump Enable | Evaporator Pump XX Enable |  | evapPump(\w{0,4}(?=[A-Z]¦$))Enable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | chilled,water,pump,enable,cmd | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPumpEnableDb | evapPumpXXXXEnableDb | Evaporator Pump Enable Deadband | Evaporator Pump XX Enable Deadband |  | evapPump(\w{0,4}(?=[A-Z]¦$))EnableDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | chilled,water,pump,enable,deadband,sp | CLR | 2.15 (Released),2.16 (Pre-Release)
evapPumpEnableSp | evapPumpXXXXEnableSp | Evaporator Pump Enable Setpoint | Evaporator Pump XX Enable Setpoint |  | evapPump((?:(?!Lag)\w){0,4}(?=[A-Z]¦$))EnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | chilled,water,pump,enable,effective,sp | CLR | 2.15 (Released),2.16 (Pre-Release)
evapPumpEnteringPressure | evapPumpXXXXEnteringPressure | Evaporator Pump Entering Pressure | Evaporator Pump XX Entering Pressure |  | evapPump(\w{0,4}(?=[A-Z]¦$))EnteringPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | chilled,water,pump,entering,pressure,sensor | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPumpFault | evapPumpXXXXFault | Evaporator Pump Fault | Evaporator Pump XX Fault |  | evapPump(\w{0,4}(?=[A-Z]¦$))Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | chilled,water,pump,fault,common | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPumpLagDisableSp | evapPumpXXXXLagDisableSp | Evaporator Pump Lag Disable Setpoint | Evaporator Pump XX Lag Disable Setpoint |  | evapPump(\w{0,4}(?=[A-Z]¦$))LagDisableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | chilled,water,pump,lag,disable,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPumpLagEnableSp | evapPumpXXXXLagEnableSp | Evaporator Pump Lag Enable Setpoint | Evaporator Pump XX Lag Enable Setpoint |  | evapPump(\w{0,4}(?=[A-Z]¦$))LagEnableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | chilled,water,pump,lag,enable,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPumpLagReq | evapPumpXXXXLagReq | Evaporator Pump Lag Request | Evaporator Pump XX Lag Request |  | evapPump(\w{0,4}(?=[A-Z]¦$))LagReq | No | No | No | Bool | Request/No Request | Request/No Request | [6 empty] | chilled,water,pump,lag,request,cmd | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPumpLead | evapPumpLead | Evaporator Pump Lead | Evaporator Pump Lead |  | evapPumpLead | Yes | Yes | No | Bool | Lead 1/Lead 2 | Lead 1/Lead 2 | [6 empty] | chilled,water,pump,lead,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPumpLeadXor | evapPumpLeadXor | Evaporator Pump Lead Change Over | Evaporator Pump Lead Change Over |  | evapPumpLeadXor | No | No | No | Bool | On/Off | On/Off | [6 empty] | chilled,water,pump,lead,changeOver,cmd | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPumpLeadXorRuntimeSp | evapPumpLeadXorRuntimeSp | Evaporator Pump Lead Change Over Runtime Setpoint | Evaporator Pump Lead Change Over Runtime Setpoint |  | evapPumpLeadXorRuntimeSp | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | CLR | 2.15 (Released),2.16 (Pre-Release)
evapPumpLeavingPressure | evapPumpXXXXLeavingPressure | Evaporator Pump Leaving Pressure | Evaporator Pump XX Leaving Pressure |  | evapPump(\w{0,4}(?=[A-Z]¦$))LeavingPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | chilled,water,pump,leaving,pressure,sensor | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPumpMaint | evapPumpXXXXMaint | Evaporator Pump Maintenance | Evaporator Pump XX Maintenance |  | evapPump(\w{0,4}(?=[A-Z]¦$))Maint | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | chilled,water,pump,maintenance,common,cmd | CLR | 2.15 (Released),2.16 (Pre-Release)
evapPumpMaintSwitch | evapPumpXXXXMaintSwitch | Evaporator Pump Maintenance Switch | Evaporator Pump XX Maintenance Switch |  | evapPump(\w{0,4}(?=[A-Z]¦$))MaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | chilled,water,pump,maintenance,switch,cmd | CLR | 2.15 (Released),2.16 (Pre-Release)
evapPumpOvr | evapPumpXXXXOvr | Evaporator Pump Override | Evaporator Pump XX Override |  | evapPump(\w{0,4}(?=[A-Z]¦$))Ovr | No | No | No | Bool | On/Off | On/Off | [6 empty] | chilled,water,pump,status,ovr | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPumpPressureDelta | evapPumpXXXXPressureDelta | Evaporator Pump Pressure Delta | Evaporator Pump XX Pressure Delta |  | evapPump(\w{0,4}(?=[A-Z]¦$))PressureDelta | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | chilled,water,pump,pressure,delta,sensor | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPumpPressureHiAlarm | evapPumpXXXXPressureHiAlarm | Evaporator Pump Pressure High Alarm | Evaporator Pump XX Pressure High Alarm |  | evapPump(\w{0,4}(?=[A-Z]¦$))PressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | chilled,water,pump,pressure,high,alarm | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPumpPressureHiSp | evapPumpXXXXPressureHiSp | Evaporator Pump Pressure High Setpoint | Evaporator Pump XX Pressure High Setpoint |  | evapPump(\w{0,4}(?=[A-Z]¦$))PressureHiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | chilled,water,pump,pressure,high,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPumpPressureLoAlarm | evapPumpXXXXPressureLoAlarm | Evaporator Pump Pressure Low Alarm | Evaporator Pump XX Pressure Low Alarm |  | evapPump(\w{0,4}(?=[A-Z]¦$))PressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | chilled,water,pump,pressure,low,alarm | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPumpPressureLoSp | evapPumpXXXXPressureLoSp | Evaporator Pump Pressure Low Setpoint | Evaporator Pump XX Pressure Low Setpoint |  | evapPump(\w{0,4}(?=[A-Z]¦$))PressureLoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | chilled,water,pump,pressure,low,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPumpRuntime | evapPumpXXXXRuntime | Evaporator Pump Runtime | Evaporator Pump XX Runtime |  | evapPump(\w{0,4}(?=[A-Z]¦$))Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | CLR | 2.15 (Released),2.16 (Pre-Release)
evapPumpSpeed | evapPumpXXXXSpeed | Evaporator Pump Speed | Evaporator Pump XX Speed |  | evapPump(\w{0,4}(?=[A-Z]¦$))Speed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | chilled,water,pump,speed,cmd | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPumpSpeedFb | evapPumpXXXXSpeedFb | Evaporator Pump Speed Feedback | Evaporator Pump XX Speed Feedback |  | evapPump(\w{0,4}(?=[A-Z]¦$))SpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | chilled,water,pump,speed,sensor | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPumpSpeedMaxSp | evapPumpXXXXSpeedMaxSp | Evaporator Pump Speed Max Setpoint | Evaporator Pump XX Speed Max Setpoint |  | evapPump(\w{0,4}(?=[A-Z]¦$))SpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | chilled,water,pump,speed,max,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPumpSpeedMinSp | evapPumpXXXXSpeedMinSp | Evaporator Pump Speed Min Setpoint | Evaporator Pump XX Speed Min Setpoint |  | evapPump(\w{0,4}(?=[A-Z]¦$))SpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | chilled,water,pump,speed,min,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPumpSpeedOvr | evapPumpXXXXSpeedOvr | Evaporator Pump Speed Override | Evaporator Pump XX Speed Override |  | evapPump(\w{0,4}(?=[A-Z]¦$))SpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | chilled,water,pump,speed,ovr | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPumpSpeedSp | evapPumpXXXXSpeedSp | Evaporator Pump Speed Setpoint | Evaporator Pump XX Speed Setpoint |  | evapPump(\w{0,4}(?=[A-Z]¦$))SpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | chilled,water,pump,speed,effective,sp | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapPumpStatus | evapPumpXXXXStatus | Evaporator Pump Status | Evaporator Pump XX Status |  | evapPump(\w{0,4}(?=[A-Z]¦$))Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | chilled,water,pump,status,sensor | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapStrainerAlarm | evapStrainerAlarm | Evaporator Strainer Alarm | Evaporator Strainer Alarm |  | evapStrainerAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | chilled,water,strainer,alarm | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapStrainerEnable | evapStrainerEnable | Evaporator Strainer Enable | Evaporator Strainer Enable |  | evapStrainerEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | chilled,water,strainer,enable,cmd | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
evapTempDelta | evapTempDelta | Evaporator Temperature Differential | Evaporator Temperature Differential |  | evapTempDelta | Yes | Yes | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | chilled,water,delta,temp,sensor | CLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
eventCount | eventCount | Event Count | Event Count |  | eventCount | Yes | No | No | Number |  |  |  |  | 0 | 0 |  |  | event,count,sensor | PRLY | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
eventDate | eventDate | Event Date | Event Date |  | eventDate | Yes | No | No | Str | [8 empty] | event,date,sensor | PRLY | 2.12,2.13,2.14,2.15 (Released)
eventType | eventType | Event Type | Event Type |  | eventType | Yes | No | No | Str | [8 empty] | event,type,sensor | PRLY | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFlow | exhaustFlowXXXX | Exhaust Airflow | Exhaust Airflow XX |  | exhaustFlow(\d{0,4}) | Yes | Yes | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | common,exhaust,air,flow,sensor | AFMS,AHU,CU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFlowAlarm | exhaustFlowXXXXAlarm | Exhaust Airflow Alarm | Exhaust Airflow XX Alarm |  | exhaustFlow(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | exhaust,air,flow,alarm | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFlowDb | exhaustFlowXXXXDb | Exhaust Airflow Deadband | Exhaust Airflow XX Deadband |  | exhaustFlow(\d{0,4})Db | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | exhaust,air,flow,deadband,sp | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFlowHiSp | exhaustFlowXXXXHiSp | Exhaust Airflow High Setpoint | Exhaust Airflow XX High Setpoint |  | exhaustFlow(\d{0,4})HiSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | exhaust,air,flow,high,sp | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFlowLoSp | exhaustFlowXXXXLoSp | Exhaust Airflow Low Setpoint | Exhaust Airflow XX Low Setpoint |  | exhaustFlow(\d{0,4})LoSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | exhaust,air,flow,low,sp | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFlowMaxSp | exhaustFlowXXXXMaxSp | Exhaust Airflow Max Reset Setpoint | Exhaust Airflow XX Max Reset Setpoint |  | exhaustFlow(\d{0,4})MaxSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | exhaust,air,flow,max,sp | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFlowMinSp | exhaustFlowXXXXMinSp | Exhaust Airflow Min Reset Setpoint | Exhaust Airflow XX Min Reset Setpoint |  | exhaustFlow(\d{0,4})MinSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | exhaust,air,flow,min,sp | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFlowOffsetSp | exhaustFlowXXXXOffsetSp | Exhaust Airflow Offset Setpoint | Exhaust Airflow XX Offset Setpoint |  | exhaustFlow(\d{0,4})OffsetSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | exhaust,air,flow,offset,sp | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFlowSp | exhaustFlowXXXXSp | Exhaust Airflow Setpoint | Exhaust Airflow XX Setpoint |  | exhaustFlow(\d{0,4})Sp | Yes | Yes | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | exhaust,air,flow,effective,sp | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFlowStatus | exhaustFlowXXXXStatus | Exhaust Airflow Status | Exhaust Airflow XX Status |  | exhaustFlow(\d{0,4})Status | Yes | Yes | No | Bool | Flow/No Flow | Flow/No Flow | [6 empty] | exhaust,air,flow,status,sensor | AHU,DHU,DOAS,EC,EF,FPB,HP,MAU,RTU,SMEX,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFlowUnoccSp | exhaustFlowXXXXUnoccSp | Exhaust Airflow Unoccupied Setpoint | Exhaust Airflow XX Unoccupied Setpoint |  | exhaustFlow(\d{0,4})UnoccSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | exhaust,air,flow,unoccupied,sp | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustCO | exhaustCOXXXX | Exhaust CO | Exhaust CO XX |  | exhaustCO(?:(?!2)(\d{0,4})?) | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | exhaust,air,co,sensor | AHU,DOAS,EF,ERU,HRU,MAU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustCO2 | exhaustCO2XXXX | Exhaust CO2 | Exhaust CO2 XX |  | exhaustCO2(?:(\d{0,4})?) | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | exhaust,air,co2,sensor | AHU,DHU,DOAS,EC,EF,ERU,HP,HRU,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustCO2Sp | exhaustCO2XXXXSp | Exhaust CO2 Setpoint | Exhaust CO2 XX Setpoint |  | exhaustCO2(?:(\d{0,4})?)Sp | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | exhaust,air,co2,sp | AHU,DHU,DOAS,EC,EF,ERU,HP,HRU,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustDamper | exhaustDamperXXXX | Exhaust Damper | Exhaust Damper XX |  | exhaustDamper(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | common,exhaust,air,damper,position,cmd | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustDamperAlarm | exhaustDamperXXXXAlarm | Exhaust Damper Alarm | Exhaust Damper XX Alarm |  | exhaustDamper(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | common,exhaust,air,damper,position,alarm | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustDamperFb | exhaustDamperXXXXFb | Exhaust Damper Feedback | Exhaust Damper XX Feedback |  | exhaustDamper(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | common,exhaust,air,damper,position,sensor | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustDamperMinSp | exhaustDamperXXXXMinSp | Exhaust Damper Minimum Setpoint | Exhaust Damper XX Minimum Setpoint |  | exhaustDamper(\d{0,4})MinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | common,exhaust,air,damper,position,min,sp | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustDamperOvr | exhaustDamperXXXXOvr | Exhaust Damper Override | Exhaust Damper XX Override |  | exhaustDamper(\d{0,4})Ovr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | common,exhaust,air,damper,position,ovr | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustDewpoint | exhaustDewpoint | Exhaust Dewpoint | Exhaust Dewpoint |  | exhaustDewpoint | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | exhaust,air,dewpoint,sensor | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustEnthalpy | exhaustEnthalpy | Exhaust Enthalpy | Exhaust Enthalpy |  | exhaustEnthalpy | Yes | Yes | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | exhaust,air,enthalpy,sensor | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanAlarm | exhaustFanXXXXAlarm | Exhaust Fan Alarm | Exhaust Fan XX Alarm |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | exhaust,air,fan,general,common,alarm | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanAlarmReset | exhaustFanXXXXAlarmReset | Exhaust Fan Alarm Reset | Exhaust Fan XX Alarm Reset |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | exhaust,air,fan,general,reset,alarm | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFan | exhaustFanXXXX | Exhaust Fan Command | Exhaust Fan XX Command |  | exhaustFan((?:(?!Lead)(?!Mode)(?!Ovr)\w){0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | exhaust,air,fan,status,cmd | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanCurrent | exhaustFanXXXXCurrent | Exhaust Fan Current | Exhaust Fan XX Current |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))Current | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | exhaust,air,fan,current,sensor | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanDCVoltage | exhaustFanXXXXDCVoltage | Exhaust Fan DC Voltage | Exhaust Fan XX DC Voltage |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))DCVoltage | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  |  | exhaust,air,fan,dcVolt,sensor | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanDisableSp | exhaustFanXXXXDisableSp | Exhaust Fan Disable Setpoint | Exhaust Fan XX Disable Setpoint |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))DisableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | exhaust,air,fan,disable,sp | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanDriveAlarm | exhaustFanXXXXDriveAlarm | Exhaust Fan Drive Alarm | Exhaust Fan XX Drive Alarm |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))DriveAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | exhaust,air,fan,drive,alarm | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanDriveTemp | exhaustFanXXXXDriveTemp | Exhaust Fan Drive Temperature | Exhaust Fan XX Drive Temperature |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))DriveTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | exhaust,air,fan,driveTemp,sensor | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanEnable | exhaustFanXXXXEnable | Exhaust Fan Enable Command | Exhaust Fan XX Enable Command |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))Enable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | exhaust,air,fan,enable,cmd | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.15 (Released),2.16 (Pre-Release)
exhaustFanEnableDb | exhaustFanXXXXEnableDb | Exhaust Fan Enable Deadband | Exhaust Fan XX Enable Deadband |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))EnableDb | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | exhaust,air,fan,enable,deadband,sp | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanEnableSp | exhaustFanXXXXEnableSp | Exhaust Fan Enable Setpoint | Exhaust Fan XX Enable Setpoint |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))EnableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | exhaust,air,fan,enable,effective,sp | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanEnergy | exhaustFanXXXXEnergy | Exhaust Fan Energy | Exhaust Fan XX Energy |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))Energy | Yes | Yes | No | Number |  |  | kilowatt_hour | kilowatt_hour | 0 | 0 |  |  | exhaust,air,fan,energy,sensor | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanEnteringPressure | exhaustFanXXXXEnteringPressure | Exhaust Fan Entering Pressure | Exhaust Fan XX Entering Pressure |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))EnteringPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | exhaust,air,fan,entering,pressure,sensor | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanFault | exhaustFanXXXXFault | Exhaust Fan Fault | Exhaust Fan XX Fault |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | exhaust,air,fan,fault,common | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanFaultCode | exhaustFanXXXXFaultCode | Exhaust Fan Fault Code | Exhaust Fan XX Fault Code |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))FaultCode | Yes | Yes | No | Str | [8 empty] | exhaust,air,fan,fault,code | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.15 (Released)
exhaustFanFaultReset | exhaustFanXXXXFaultReset | Exhaust Fan Fault Reset | Exhaust Fan XX Fault Reset |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))FaultReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | exhaust,air,fan,fault,reset | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanFilterAlarm | exhaustFanXXXXFilterAlarm | Exhaust Fan Filter Alarm | Exhaust Fan XX Filter Alarm |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))FilterAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | exhaust,air,fan,filter,common,alarm | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanFilterAlarmReset | exhaustFanXXXXFilterAlarmReset | Exhaust Fan Filter Alarm Reset | Exhaust Fan XX Filter Alarm Reset |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))FilterAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | exhaust,air,fan,filter,reset,alarm | AHU,DHU,DOAS,EC,EF,ERU,HP,HRU,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanFilterPressureDelta | exhaustFanXXXXFilterPressureDelta | Exhaust Fan Filter Pressure Delta | Exhaust Fan XX Filter Pressure Delta |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))FilterPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | exhaust,air,fan,filter,pressure,delta,sensor | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released)
exhaustFanFilterRuntime | exhaustFanXXXXFilterRuntime | Exhaust Fan Filter Runtime | Exhaust Fan XX Filter Runtime |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))FilterRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.15 (Released),2.16 (Pre-Release)
exhaustFanFrequency | exhaustFanXXXXFrequency | Exhaust Fan Frequency | Exhaust Fan XX Frequency |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))Frequency | Yes | Yes | No | Number |  |  | hertz | hertz | 1 | 1 |  |  | exhaust,air,fan,freq,sensor | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanHandMode | exhaustFanXXXXHandMode | Exhaust Fan Hand/Auto Mode | Exhaust Fan XX Hand/Auto Mode |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))HandMode | Yes | Yes | No | Bool | Hand/Auto | Hand/Auto | [6 empty] | exhaust,air,fan,handMode,sensor | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanLead | exhaustFanLead | Exhaust Fan Lead | Exhaust Fan Lead |  | exhaustFanLead | Yes | Yes | No | Bool | Lead 1/Lead 2 | Lead 1/Lead 2 | [6 empty] | exhaust,air,fan,lead,sp | AHU,DHU,DOAS,EC,EF,ERU,HP,HRU,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanLeadXor | exhaustFanLeadXor | Exhaust Fan Lead Change Over | Exhaust Fan Lead Change Over |  | exhaustFanLeadXor | No | No | No | Bool | On/Off | On/Off | [6 empty] | exhaust,air,fan,lead,changeOver,cmd | AHU,DHU,DOAS,EC,EF,ERU,HP,HRU,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanLeadXorRuntimeSp | exhaustFanLeadXorRuntimeSp | Exhaust Fan Lead Change Over Runtime Setpoint | Exhaust Fan Lead Change Over Runtime Setpoint |  | exhaustFanLeadXorRuntimeSp | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,DHU,DOAS,EC,EF,ERU,HP,HRU,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanLeavingPressure | exhaustFanXXXXLeavingPressure | Exhaust Fan Leaving Pressure | Exhaust Fan XX Leaving Pressure |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))LeavingPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | exhaust,air,fan,leaving,pressure,sensor | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanMaintSwitch | exhaustFanXXXXMaintSwitch | Exhaust Fan Maintenance Switch | Exhaust Fan XX Maintenance Switch |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))MaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | exhaust,air,fan,maintenance,switch,cmd | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanMode | exhaustFanXXXXMode | Exhaust Fan Mode | Exhaust Fan XX Mode |  | exhaustFan((?:(?!Hand)\w){0,4}(?=[A-Z]¦$))Mode | Yes | No | No | Str | Continuous/Cycling | Continuous/Cycling | [6 empty] | blacklist | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanModeOvr | exhaustFanXXXXModeOvr | Exhaust Fan Mode Override | Exhaust Fan XX Mode Override |  | exhaustFan((?:(?!Hand)\w){0,4}(?=[A-Z]¦$))ModeOvr | Yes | No | No | Str | Continuous/Cycling | Continuous/Cycling | [6 empty] | blacklist | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.15 (Released),2.16 (Pre-Release)
exhaustFanMotorSpeed | exhaustFanXXXXMotorSpeed | Exhaust Fan Motor Speed | Exhaust Fan XX Motor Speed |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))MotorSpeed | Yes | Yes | No | Number |  |  | revolutions_per_minute | revolutions_per_minute | 0 | 0 |  |  | exhaust,air,fan,motorSpeed,sensor | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanMotorTemp | exhaustFanXXXXMotorTemp | Exhaust Fan Motor Temperature | Exhaust Fan XX Motor Temperature |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))MotorTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | exhaust,air,fan,motorTemp,sensor | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanOvr | exhaustFanXXXXOvr | Exhaust Fan Override | Exhaust Fan XX Override |  | exhaustFan((?:(?!Mode)\w){0,4}(?=[A-Z]¦$))Ovr | No | No | No | Bool | On/Off | On/Off | [6 empty] | exhaust,air,fan,status,ovr | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.15 (Released),2.16 (Pre-Release)
exhaustFanPressureDelta | exhaustFanXXXXPressureDelta | Exhaust Fan Pressure Delta | Exhaust Fan XX Pressure Delta |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))PressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | exhaust,air,fan,common,pressure,delta,sensor | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanPressureHiAlarm | exhaustFanXXXXPressureHiAlarm | Exhaust Fan Pressure High Alarm | Exhaust Fan XX Pressure High Alarm |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))PressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | exhaust,air,fan,pressure,high,alarm | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanPressureHiSp | exhaustFanXXXXPressureHiSp | Exhaust Fan Pressure High Setpoint | Exhaust Fan XX Pressure High Setpoint |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))PressureHiSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | exhaust,air,fan,pressure,high,sp | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanPressureLoAlarm | exhaustFanXXXXPressureLoAlarm | Exhaust Fan Pressure Low Alarm | Exhaust Fan XX Pressure Low Alarm |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))PressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | exhaust,air,fan,pressure,low,alarm | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanPressureLoSp | exhaustFanXXXXPressureLoSp | Exhaust Fan Pressure Low Setpoint | Exhaust Fan XX Pressure Low Setpoint |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))PressureLoSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | exhaust,air,fan,pressure,low,sp | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanPowerReal | exhaustFanXXXXPowerReal | Exhaust Fan Real Power | Exhaust Fan XX Real Power |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))PowerReal | Yes | Yes | No | Number |  |  | kilowatt | kilowatt | 1 | 1 |  | N | exhaust,air,fan,power,real,sensor | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanRuntime | exhaustFanXXXXRuntime | Exhaust Fan Runtime | Exhaust Fan XX Runtime |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.15 (Released),2.16 (Pre-Release)
exhaustFanShutdownSwitch | exhaustFanXXXXShutdownSwitch | Exhaust Fan Shutdown Switch | Exhaust Fan XX Shutdown Switch |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))ShutdownSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | exhaust,air,fan,shutdown,switch,cmd | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanSpeed | exhaustFanXXXXSpeed | Exhaust Fan Speed | Exhaust Fan XX Speed |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))Speed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | exhaust,air,fan,speed,cmd | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanSpeedSpBAS | exhaustFanXXXXSpeedSpBAS | Exhaust Fan Speed BAS Setpoint | Exhaust Fan XX Speed BAS Setpoint |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))SpeedSpBAS | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | exhaust,air,fan,speed,bas,sp | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanSpeedFb | exhaustFanXXXXSpeedFb | Exhaust Fan Speed Feedback | Exhaust Fan XX Speed Feedback |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))SpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | exhaust,air,fan,speed,sensor | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanSpeedMaxSp | exhaustFanXXXXSpeedMaxSp | Exhaust Fan Speed Max Setpoint | Exhaust Fan XX Speed Max Setpoint |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))SpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | exhaust,air,fan,speed,max,sp | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanSpeedMinSp | exhaustFanXXXXSpeedMinSp | Exhaust Fan Speed Min Setpoint | Exhaust Fan XX Speed Min Setpoint |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))SpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | exhaust,air,fan,speed,min,sp | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanSpeedOffsetSp | exhaustFanXXXXSpeedOffsetSp | Exhaust Fan Speed Offset Setpoint | Exhaust Fan XX Speed Offset Setpoint |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))SpeedOffsetSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | exhaust,air,fan,speed,offset,sp | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanSpeedOvr | exhaustFanXXXXSpeedOvr | Exhaust Fan Speed Override | Exhaust Fan XX Speed Override |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))SpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | exhaust,air,fan,speed,ovr | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanSpeedSp | exhaustFanXXXXSpeedSp | Exhaust Fan Speed Setpoint | Exhaust Fan XX Speed Setpoint |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))SpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | exhaust,air,fan,speed,effective,sp | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanSpeedStage | exhaustFanXXXXSpeedStage | Exhaust Fan Speed Stage | Exhaust Fan XX Speed Stage |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))SpeedStage | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | exhaust,air,fan,speed,stage | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanStageSp | exhaustFanXXXXStageYYYYSp | Exhaust Fan Stage Setpoint | Exhaust Fan XX Stage YY Setpoint |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))Stage(\d{0,4})Sp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 | YY |  | exhaust,air,fan,sp | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanStatus | exhaustFanXXXXStatus | Exhaust Fan Status | Exhaust Fan XX Status |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | exhaust,air,fan,status,sensor | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanTorque | exhaustFanXXXXTorque | Exhaust Fan Torque | Exhaust Fan XX Torque |  | exhaustFan(\w{0,4}(?=[A-Z]¦$))Torque | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | exhaust,air,fan,torque,sensor | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustFanVoltage | exhaustFanXXXXVoltage | Exhaust Fan Voltage | Exhaust Fan XX Voltage |  | exhaustFan((?:(?!DC)\w){0,4}(?=[A-Z]¦$))Voltage | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  | N | exhaust,air,fan,volt,sensor | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustHumidity | exhaustHumidityXXXX | Exhaust Humidity | Exhaust Humidity XX |  | exhaustHumidity(\d{0,4}) | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | exhaust,air,humidity,sensor | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustHumidityHiAlarm | exhaustHumidityXXXXHiAlarm | Exhaust Humidity High Alarm | Exhaust Humidity XX High Alarm |  | exhaustHumidity(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | exhaust,air,humidity,high,alarm | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustHumidityLoAlarm | exhaustHumidityXXXXLoAlarm | Exhaust Humidity Low Alarm | Exhaust Humidity XX Low Alarm |  | exhaustHumidity(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | exhaust,air,humidity,low,alarm | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustIsoDamper | exhaustIsoDamperXXXX | Exhaust Isolation Damper | Exhaust Isolation Damper XX |  | exhaustIsoDamper(\d{0,4}) | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | exhaust,air,iso,damper,position,cmd | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustIsoDamperFb | exhaustIsoDamperXXXXFb | Exhaust Isolation Damper Feedback | Exhaust Isolation Damper XX Feedback |  | exhaustIsoDamper(\d{0,4})Fb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | exhaust,air,iso,damper,position,sensor | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustIsoDamperOvr | exhaustIsoDamperXXXXOvr | Exhaust Isolation Damper Override | Exhaust Isolation Damper XX Override |  | exhaustIsoDamper(\d{0,4})Ovr | No | No | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | exhaust,air,iso,damper,position,ovr | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustPressure | exhaustPressureXXXX | Exhaust Pressure | Exhaust Pressure XX |  | exhaustPressure(\d{0,4}) | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | exhaust,air,static,pressure,sensor | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustPressureAvg | exhaustPressureAvg | Exhaust Pressure (Average) | Exhaust Pressure (Average) |  | exhaustPressureAvg | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | exhaust,air,static,pressure,avg,calc | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.15 (Released),2.16 (Pre-Release)
exhaustPressureDb | exhaustPressureXXXXDb | Exhaust Pressure Deadband | Exhaust Pressure XX Deadband |  | exhaustPressure(\d{0,4})Db | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | exhaust,air,static,pressure,deadband,sp | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustPressureHiAlarm | exhaustPressureXXXXHiAlarm | Exhaust Pressure High Alarm | Exhaust Pressure XX High Alarm |  | exhaustPressure(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | exhaust,air,static,pressure,high,alarm | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustPressureHiSp | exhaustPressureXXXXHiSp | Exhaust Pressure High Setpoint | Exhaust Pressure XX High Setpoint |  | exhaustPressure(\d{0,4})HiSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | exhaust,air,static,pressure,high,sp | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustPressureLoAlarm | exhaustPressureXXXXLoAlarm | Exhaust Pressure Low Alarm | Exhaust Pressure XX Low Alarm |  | exhaustPressure(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | exhaust,air,static,pressure,low,alarm | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustPressureLoSp | exhaustPressureXXXXLoSp | Exhaust Pressure Low Setpoint | Exhaust Pressure XX Low Setpoint |  | exhaustPressure(\d{0,4})LoSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | exhaust,air,static,pressure,low,sp | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustPressureMaxSp | exhaustPressureXXXXMaxSp | Exhaust Pressure Max Reset Setpoint | Exhaust Pressure XX Max Reset Setpoint |  | exhaustPressure(\d{0,4})MaxSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | exhaust,air,static,pressure,max,sp | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustPressureMinSp | exhaustPressureXXXXMinSp | Exhaust Pressure Min Reset Setpoint | Exhaust Pressure XX Min Reset Setpoint |  | exhaustPressure(\d{0,4})MinSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | exhaust,air,static,pressure,min,sp | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustPressureSp | exhaustPressureXXXXSp | Exhaust Pressure Setpoint | Exhaust Pressure XX Setpoint |  | exhaustPressure(\d{0,4})Sp | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | exhaust,air,static,pressure,effective,sp | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustTemp | exhaustTempXXXX | Exhaust Temperature | Exhaust Temperature XX |  | exhaustTemp(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | exhaust,air,temp,sensor | AFMS,AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustTempFault | exhaustTempXXXXFault | Exhaust Temperature Fault | Exhaust Temperature XX Fault |  | exhaustTemp(\d{0,4})Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | exhaust,air,temp,fault | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustTempHiAlarm | exhaustTempXXXXHiAlarm | Exhaust Temperature High Alarm | Exhaust Temperature XX High Alarm |  | exhaustTemp(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | exhaust,air,temp,high,alarm | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustTempHiSp | exhaustTempXXXXHiSp | Exhaust Temperature High Setpoint | Exhaust Temperature XX High Setpoint |  | exhaustTemp(\d{0,4})HiSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | exhaust,air,temp,high,sp | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustTempLoAlarm | exhaustTempXXXXLoAlarm | Exhaust Temperature Low Alarm | Exhaust Temperature XX Low Alarm |  | exhaustTemp(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | exhaust,air,temp,low,alarm | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustTempLoSp | exhaustTempXXXXLoSp | Exhaust Temperature Low Setpoint | Exhaust Temperature XX Low Setpoint |  | exhaustTemp(\d{0,4})LoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | exhaust,air,temp,low,sp | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustTempMaxSp | exhaustTempXXXXMaxSp | Exhaust Temperature Max Setpoint | Exhaust Temperature XX Max Setpoint |  | exhaustTemp(\d{0,4})MaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | exhaust,air,temp,max,sp | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustTempMinSp | exhaustTempXXXXMinSp | Exhaust Temperature Min Setpoint | Exhaust Temperature XX Min Setpoint |  | exhaustTemp(\d{0,4})MinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | exhaust,air,temp,min,sp | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustTempSp | exhaustTempXXXXSp | Exhaust Temperature Setpoint | Exhaust Temperature XX Setpoint |  | exhaustTemp(\d{0,4})Sp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | exhaust,air,temp,effective,sp | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustVelocity | exhaustVelocityXXXX | Exhaust Velocity | Exhaust Velocity XX |  | exhaustVelocity(\d{0,4}) | Yes | Yes | No | Number |  |  | feet_per_minute | meters_per_second | 1 | 1 |  |  | exhaust,air,velocity,sensor | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
exhaustVelocityPressure | exhaustVelocityXXXXPressure | Exhaust Velocity Pressure | Exhaust Velocity XX Pressure |  | exhaustVelocity(\d{0,4})Pressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | exhaust,air,dynamic,pressure,sensor | AHU,DHU,DOAS,EC,EF,HP,MAU,RTU,SMEX,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
expansionTankPressure | expansionTankPressure | Expansion Tank Pressure | Expansion Tank Pressure |  | expansionTankPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | expansion,tank,pressure,sensor | CWS,DCWS,DHWS,HWS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
faceBypassDamper | faceBypassDamper | Face Bypass Damper Command | Face Bypass Damper Command |  | faceBypassDamper | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | faceBypass,damper,position,cmd | AHU,DHU,DOAS,EC,HP,MAU,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
faceBypassDamperDb | faceBypassDamperDb | Face Bypass Damper Deadband | Face Bypass Damper Deadband |  | faceBypassDamperDb | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | faceBypass,damper,position,deadband,sp | AHU,DHU,DOAS,EC,HP,MAU,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
faceBypassDamperEnableSp | faceBypassDamperEnableSp | Face Bypass Damper Enable Setpoint | Face Bypass Damper Enable Setpoint |  | faceBypassDamperEnableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | faceBypass,damper,position,enable,sp | AHU,DHU,DOAS,EC,HP,MAU,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
faceBypassDamperFb | faceBypassDamperFb | Face Bypass Damper Feedback | Face Bypass Damper Feedback |  | faceBypassDamperFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | faceBypass,damper,position,sensor | AHU,DHU,DOAS,EC,HP,MAU,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
faceBypassDamperMaxSp | faceBypassDamperMaxSp | Face Bypass Damper Max Reset Setpoint | Face Bypass Damper Max Reset Setpoint |  | faceBypassDamperMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | faceBypass,damper,position,max,sp | AHU,DHU,DOAS,EC,HP,MAU,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
faceBypassDamperMinSp | faceBypassDamperMinSp | Face Bypass Damper Min Reset Setpoint | Face Bypass Damper Min Reset Setpoint |  | faceBypassDamperMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | faceBypass,damper,position,min,sp | AHU,DHU,DOAS,EC,HP,MAU,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
faceBypassDamperEnable | faceBypassDamperEnable | Face Bypass Damper Mode Enable | Face Bypass Damper Mode Enable |  | faceBypassDamperEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | faceBypass,damper,enable,cmd | AHU,DHU,DOAS,EC,HP,MAU,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
faceBypassDamperOvr | faceBypassDamperOvr | Face Bypass Damper Override | Face Bypass Damper Override |  | faceBypassDamperOvr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | faceBypass,damper,position,ovr | AHU,DHU,DOAS,EC,HP,MAU,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
faceDamper | faceDamperXXXX | Face Damper Command | Face Damper XX Command |  | faceDamper(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | face,damper,position,cmd | AHU,DHU,DOAS,EC,HP,MAU,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
faceDamperEnable | faceDamperXXXXEnable | Face Damper Enable Command | Face Damper XX Enable Command |  | faceDamper(\d{0,4})Enable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | face,damper,enable,cmd | AHU,DHU,DOAS,EC,HP,MAU,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
faceDamperFb | faceDamperXXXXFb | Face Damper Feedback | Face Damper XX Feedback |  | faceDamper(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | face,damper,position,sensor | AHU,DHU,DOAS,EC,HP,MAU,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
faceDamperOvr | faceDamperXXXXOvr | Face Damper Override | Face Damper XX Override |  | faceDamper(\d{0,4})Ovr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | face,damper,position,ovr | AHU,DHU,DOAS,EC,HP,MAU,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fireAlarm | fireXXXXAlarm | Fire Alarm | Fire XX Alarm |  | fire(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | fire,system,alarm | FP,HVHS,HVLS,MSC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fireDeviceStatus | fireDeviceStatus | Fire Device Status | Fire Device Status |  | fireDeviceStatus | Yes | Yes | No | Str | [8 empty] | fire,device,status,sensor | FP,FSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fireExtinguisherAlarm | fireExtinguisherXXXXAlarm | Fire Extinguisher Alarm | Fire Extinguisher XX Alarm |  | fireExtinguisher(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | fire,extinguisher,alarm | FEXT,MSC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fireExtinguisherPressure | fireExtinguisherXXXXPressure | Fire Extinguisher Pressure | Fire Extinguisher XX Pressure |  | fireExtinguisher(\d{0,4})Pressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | fire,extinguisher,pressure,sensor | FEXT,MSC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
firePumpAlarm | firePumpXXXXAlarm | Fire Pump Alarm | Fire Pump XX Alarm |  | firePump(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | fire,pump,common,alarm | FP,FSS,MSC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
firePumpAlarmReset | firePumpXXXXAlarmReset | Fire Pump Alarm Reset | Fire Pump XX Alarm Reset |  | firePump(\d{0,4})AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | fire,pump,reset,alarm | FP,FSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
firePump | firePumpXXXX | Fire Pump Command | Fire Pump XX Command |  | firePump(\d{0,4}) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | fire,pump,status,cmd | FP,FSS,MSC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
firePumpFault | firePumpXXXXFault | Fire Pump Fault | Fire Pump XX Fault |  | firePump(\d{0,4})Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | fire,pump,fault | FP,FSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
firePumpHandMode | firePumpXXXXHandMode | Fire Pump Hand/Auto Mode | Fire Pump XX Hand/Auto Mode |  | firePump(\d{0,4})HandMode | Yes | Yes | No | Bool | Hand/Auto | Hand/Auto | [6 empty] | fire,pump,handMode,sensor | FP,FSS,MSC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
firePumpStarts | firePumpXXXXStarts | Fire Pump Starts | Fire Pump XX Starts |  | firePump(\d{0,4})Starts | Yes | No | No | Number |  |  |  |  | 0 | 0 |  |  | fire,pump,starts,common,sensor | FP,FSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
firePumpStartsDay | firePumpXXXXStartsDay | Fire Pump Starts Day | Fire Pump XX Starts Day |  | firePump(\d{0,4})StartsDay | Yes | No | No | Number |  |  |  |  | 0 | 0 |  |  | fire,pump,starts,day,sensor | FP,FSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
firePumpStartsDayHiSp | firePumpXXXXStartsDayHiSp | Fire Pump Starts Day High Setpoint | Fire Pump XX Starts Day High Setpoint |  | firePump(\d{0,4})StartsDayHiSp | No | No | No | Number |  |  |  |  | 0 | 0 |  |  | fire,pump,starts,day,high,sp | FP,FSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
firePumpStartsHour | firePumpXXXXStartsHour | Fire Pump Starts Hour | Fire Pump XX Starts Hour |  | firePump(\d{0,4})StartsHour | Yes | No | No | Number |  |  |  |  | 0 | 0 |  |  | fire,pump,starts,hour,sensor | FP,FSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
firePumpStartsHourHiSp | firePumpXXXXStartsHourHiSp | Fire Pump Starts Hour High Setpoint | Fire Pump XX Starts Hour High Setpoint |  | firePump(\d{0,4})StartsHourHiSp | No | No | No | Number |  |  |  |  | 0 | 0 |  |  | fire,pump,starts,hour,high,sp | FP,FSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
firePumpStatus | firePumpXXXXStatus | Fire Pump Status | Fire Pump XX Status |  | firePump(\d{0,4})Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | fire,pump,status,sensor | FP,FSS,MSC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fireWarning | fireXXXXWarning | Fire Warning | Fire XX Warning |  | fire(\d{0,4})Warning | Yes | Yes | No | Bool | Warning/Normal | Warning/Normal | [6 empty] | fire,warning | FP,MSC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fixture | fixtureXXXX | Fixture Command | Fixture XX Command |  | fixture(\d{0,4}) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | fixture,status,cmd | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fixtureDimmer | fixtureXXXXDimmer | Fixture Dimmer Command | Fixture XX Dimmer Command |  | fixture(\d{0,4})Dimmer | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | fixture,dimmer,cmd | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fixtureDimLevel | fixtureXXXXDimLevel | Fixture Dimming Level Command | Fixture XX Dimming Level Command |  | fixture(\d{0,4})DimLevel | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | fixture,dimming,cmd | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fixtureDimLevelFb | fixtureXXXXDimLevelFb | Fixture Dimming Level Feedback | Fixture XX Dimming Level Feedback |  | fixture(\d{0,4})DimLevelFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | fixture,dimming,sensor | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fixtureDimLevelOvr | fixtureXXXXDimLevelOvr | Fixture Dimming Level Override | Fixture XX Dimming Level Override |  | fixture(\d{0,4})DimLevelOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | fixture,dimming,ovr | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fixtureDimLevelSp | fixtureXXXXDimLevelSp | Fixture Dimming Level Setpoint | Fixture XX Dimming Level Setpoint |  | fixture(\d{0,4})DimLevelSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | fixture,dimming,sp | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fixtureEnergy | fixtureXXXXEnergy | Fixture Energy | Fixture XX Energy |  | fixture(\d{0,4})Energy | Yes | Yes | Yes | Number |  |  | kilowatt_hour | kilowatt_hour | 0 | 0 |  |  | fixture,energy,sensor | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fixtureLightLevel | fixtureXXXXLightLevel | Fixture Light Level | Fixture XX Light Level |  | fixture(\d{0,4})LightLevel | Yes | Yes | No | Number |  |  | footcandle | lux | 0 | 0 |  |  | fixture,lightLevel,sensor | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fixtureLightLevelMaxSp | fixtureXXXXLightLevelMaxSp | Fixture Light Level Max Reset Setpoint | Fixture XX Light Level Max Reset Setpoint |  | fixture(\d{0,4})LightLevelMaxSp | No | No | No | Number |  |  | footcandle | lux | 0 | 0 |  |  | fixture,lightLevel,max,sp | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fixtureLightLevelMinSp | fixtureXXXXLightLevelMinSp | Fixture Light Level Min Reset Setpoint | Fixture XX Light Level Min Reset Setpoint |  | fixture(\d{0,4})LightLevelMinSp | No | No | No | Number |  |  | footcandle | lux | 0 | 0 |  |  | fixture,lightLevel,min,sp | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fixtureLightLevelSp | fixtureXXXXLightLevelSp | Fixture Light Level Setpoint | Fixture XX Light Level Setpoint |  | fixture(\d{0,4})LightLevelSp | Yes | Yes | No | Number |  |  | footcandle | lux | 0 | 0 |  |  | fixture,lightLevel,effective,sp | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fixtureMode | fixtureXXXXMode | Fixture Mode | Fixture XX Mode |  | fixture(\d{0,4})Mode | Yes | No | No | Str |  | Normal/Timed/Latched/External | [6 empty] | fixture,mode,sp | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fixtureOffCmd | fixtureXXXXOffCmd | Fixture Off Command | Fixture XX Off Command |  | fixture(\d{0,4})OffCmd | Yes | Yes | No | Bool | Off/Auto | Off/Auto | [6 empty] | fixture,off,cmd | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fixtureOnCmd | fixtureXXXXOnCmd | Fixture On Command | Fixture XX On Command |  | fixture(\d{0,4})OnCmd | Yes | Yes | No | Bool | On/Auto | On/Auto | [6 empty] | fixture,on,cmd | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fixtureOvr | fixtureXXXXOvr | Fixture Override | Fixture XX Override |  | fixture(\d{0,4})Ovr | No | No | No | Bool | On/Off | On/Off | [6 empty] | fixture,status,ovr | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fixtureStatus | fixtureXXXXStatus | Fixture Status | Fixture XX Status |  | fixture(\d{0,4})Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | fixture,status,sensor | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
flameAlarm | flameAlarm | Flame Alarm | Flame Alarm |  | flameAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | flame,common,alarm | AHU,BLR,HWS,MAU,RTU,SMS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
flameFailAlarm | flameFailAlarm | Flame Fail Alarm | Flame Fail Alarm |  | flameFailAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | flame,fail,alarm | AHU,BLR,HWS,MAU,RTU,SMS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
flow | flow | Flow Rate | Flow Rate |  | flow | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | common,flowRate,sensor | BLR,BTU,CLR,CM,CWS,GEO,GM,HWS,SM,SMS,TWR,VBTU,VGM,VWM,WM,WS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
flowHiSp | flowHiSp | Flow Rate High Setpoint | Flow Rate High Setpoint |  | flowHiSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | common,flowRate,high,sp | BTU,GM,VBTU,VGM,VWM,WM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
flushMode | flushMode | Flush Mode | Flush Mode |  | flushMode | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | flush,mode,cmd | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
freezeProtect | freezeProtect | Freeze Protection | Freeze Protection |  | freezeProtect | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | freeze,protect,common,cmd | AHU,SKYL | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
freezeProtectAlarm | freezeProtectAlarm | Freeze Protection Alarm | Freeze Protection Alarm |  | freezeProtectAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | freeze,protect,common,alarm | AHU,SKYL | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
freezeProtectEnable | freezeProtectEnable | Freeze Protection Enable | Freeze Protection Enable |  | freezeProtectEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | freeze,protect,enable,cmd | AHU,SKYL | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
freezeProtectEnableSp | freezeProtectEnableSp | Freeze Protection Enable Setpoint | Freeze Protection Enable Setpoint |  | freezeProtectEnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | freeze,protect,enable,sp | AHU,SKYL | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
freezeProtectValve | freezeProtectValve | Freeze Protection Valve Command | Freeze Protection Valve Command |  | freezeProtectValve | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | freeze,protect,valve,position,cmd | AHU,SKYL | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
freezeProtectValveFb | freezeProtectValveFb | Freeze Protection Valve Feedback | Freeze Protection Valve Feedback |  | freezeProtectValveFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | freeze,protect,valve,position,sensor | AHU,SKYL | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
frequency | frequency | Frequency | Frequency |  | frequency | Yes | Yes | No | Number |  |  | hertz | hertz | 1 | 1 |  |  | common,freq,cmd | BRK,CLR,GEN,INV,PDU,PFC,PM,PRLY,PV,RECT,RPP,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
frequencyPhaseA | frequencyPhaseA | Frequency (Phase A) | Frequency (Phase A) |  | frequencyPhaseA | Yes | Yes | No | Number |  |  | hertz | hertz | 1 | 1 |  | A | common,freq,sensor | BRK,CLR,GEN,INV,PDU,PFC,PM,PRLY,PV,RECT,RPP,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
frequencyPhaseB | frequencyPhaseB | Frequency (Phase B) | Frequency (Phase B) |  | frequencyPhaseB | Yes | Yes | No | Number |  |  | hertz | hertz | 1 | 1 |  | B | common,freq,sensor | BRK,CLR,GEN,INV,PDU,PFC,PM,PRLY,PV,RECT,RPP,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
frequencyPhaseC | frequencyPhaseC | Frequency (Phase C) | Frequency (Phase C) |  | frequencyPhaseC | Yes | Yes | No | Number |  |  | hertz | hertz | 1 | 1 |  | C | common,freq,sensor | BRK,CLR,GEN,INV,PDU,PFC,PM,PRLY,PV,RECT,RPP,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
frequencyMaxSp | frequencyMaxSp | Frequency Max Setpoint | Frequency Max Setpoint |  | frequencyMaxSp | No | No | No | Number |  |  | hertz | hertz | 1 | 1 |  |  | common,freq,max,sp | RRS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
frequencyMinSp | frequencyMinSp | Frequency Min Setpoint | Frequency Min Setpoint |  | frequencyMinSp | No | No | No | Number |  |  | hertz | hertz | 1 | 1 |  |  | common,freq,min,sp | RRS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
freshDamper | freshDamper | Fresh Damper Command | Fresh Damper Command |  | freshDamper | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | fresh,air,damper,position,cmd | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
freshDamperFb | freshDamperFb | Fresh Damper Feedback | Fresh Damper Feedback |  | freshDamperFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | fresh,air,damper,position,sensor | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
freshFlow | freshFlow | Fresh Flow | Fresh Flow |  | freshFlow | Yes | Yes | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | fresh,air,flow,sensor | AFMS,AHU,CU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
freshFlowSp | freshFlowSp | Fresh Flow Setpoint | Fresh Flow Setpoint |  | freshFlowSp | Yes | Yes | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | fresh,air,flow,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fuelTotalizer | fuelTotalizer | Fuel Consumption | Fuel Consumption |  | fuelTotalizer | Yes | Yes | Yes | Number |  |  | gallon | liter | 0 | 0 |  |  | fuel,consumption,sensor | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fuelIsoValve | fuelIsoValve | Fuel Isolation Valve Command | Fuel Isolation Valve Command |  | fuelIsoValve | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | fuel,isolation,valve,cmd | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fuelIsoValveFb | fuelIsoValveFb | Fuel Isolation Valve Feedback | Fuel Isolation Valve Feedback |  | fuelIsoValveFb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | fuel,isolation,valve,sensor | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fuelLeakAlarm | fuelLeakAlarm | Fuel Leak Alarm | Fuel Leak Alarm |  | fuelLeakAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | fuel,leak,alarm | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fuelLevel | fuelLevel | Fuel Level | Fuel Level |  | fuelLevel | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | fuel,level,sensor | FC,GEN,PINT | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fuelLevelHiAlarm | fuelLevelHiAlarm | Fuel Level High Alarm | Fuel Level High Alarm |  | fuelLevelHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | fuel,level,high,alarm | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fuelLevelLoAlarm | fuelLevelLoAlarm | Fuel Level Low Alarm | Fuel Level Low Alarm |  | fuelLevelLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | fuel,level,low,alarm | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fuelPressure | fuelPressure | Fuel Pressure | Fuel Pressure |  | fuelPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | fuel,pressure,sensor | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fuelPressureLoAlarm | fuelPressureLoAlarm | Fuel Pressure Low Alarm | Fuel Pressure Low Alarm |  | fuelPressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | fuel,pressure,low,alarm | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fuelPump | fuelPumpXXXX | Fuel Pump Command | Fuel Pump XX Command |  | fuelPump(\d{0,4}) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | fuel,pump,status,cmd | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fuelPumpStatus | fuelPumpXXXXStatus | Fuel Pump Status | Fuel Pump XX Status |  | fuelPump(\d{0,4})Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | fuel,pump,status,sensor | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
fuelTemp | fuelTemp | Fuel Temperature | Fuel Temperature |  | fuelTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | fuel,temp,sensor | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
gasFlowLoAlarm | gasFlowLoAlarm | Gas Flow Low Alarm | Gas Flow Low Alarm |  | gasFlowLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | gas,flow,low,alarm | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
gasIsoValveAlarm | gasIsoValveXXXXAlarm | Gas Isolation Valve Alarm | Gas Isolation Valve XX Alarm |  | gasIsoValve(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | gas,isolation,valve,alarm | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
gasIsoValve | gasIsoValveXXXX | Gas Isolation Valve Command | Gas Isolation Valve XX Command |  | gasIsoValve(\d{0,4}) | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | gas,isolation,valve,cmd | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
gasIsoValveFb | gasIsoValveXXXXFb | Gas Isolation Valve Feedback | Gas Isolation Valve XX Feedback |  | gasIsoValve(\d{0,4})Fb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | gas,isolation,valve,sensor | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
gasPressure | gasPressure | Gas Pressure | Gas Pressure |  | gasPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | common,gas,pressure,sensor | BLR | 2.15 (Released),2.16 (Pre-Release)
gasPressureLoAlarm | gasPressureLoAlarm | Gas Pressure Low Alarm | Gas Pressure Low Alarm |  | gasPressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | gas,pressure,low,alarm | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
gasPressureStatus | gasPressureStatus | Gas Pressure Status | Gas Pressure Status |  | gasPressureStatus | Yes | Yes | No | Bool | Pressure/No Pressure | Pressure/No Pressure | [6 empty] | monitor,gas,pressure,sensor | BLR | 2.15 (Released),2.16 (Pre-Release)
gasSuppression | gasSuppression | Gas Suppression | Gas Suppression |  | gasSuppression | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | gas,suppression,cmd | FP,FSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
gasSuppressionFault | gasSuppressionFault | Gas Suppression Fault | Gas Suppression Fault |  | gasSuppressionFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | gas,suppression,fault | FP,FSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
gateStatus | gateStatus | Gate Status | Gate Status |  | gateStatus | Yes | Yes | No | Bool | Open/Closed | Open/Closed | [6 empty] | gate,status,sensor | MSC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
genAlarm | genAlarm | Generator Alarm | Generator Alarm |  | genAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | generator,common,alarm | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
gen | gen | Generator Command | Generator Command |  | gen | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | generator,status,cmd | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
genDemand | genDemand | Generator Demand | Generator Demand |  | genDemand | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | generator,load,sp | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
genHandMode | genHandMode | Generator Hand/Auto Mode | Generator Hand/Auto Mode |  | genHandMode | Yes | Yes | No | Bool | Hand/Auto | Hand/Auto | [6 empty] | generator,handMode,sensor | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
genMotorSpeed | genMotorSpeed | Generator Motor Speed | Generator Motor Speed |  | genMotorSpeed | Yes | Yes | No | Number |  |  | revolutions_per_minute | revolutions_per_minute | 1 | 1 |  |  | generator,motorSpeed,sensor | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
genMotorSpeedHiAlarm | genMotorSpeedHiAlarm | Generator Motor Speed High Alarm | Generator Motor Speed High Alarm |  | genMotorSpeedHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | generator,motorSpeed,high,alarm | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
genMotorSpeedLoAlarm | genMotorSpeedLoAlarm | Generator Motor Speed Low Alarm | Generator Motor Speed Low Alarm |  | genMotorSpeedLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | generator,motorSpeed,low,alarm | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
genMotorTemp | genMotorTemp | Generator Motor Temperature | Generator Motor Temperature |  | genMotorTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | generator,motorTemp,sensor | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
genMotorTempHiAlarm | genMotorTempHiAlarm | Generator Motor Temperature High Alarm | Generator Motor Temperature High Alarm |  | genMotorTempHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | generator,motorTemp,high,alarm | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
genRuntime | genRuntime | Generator Runtime | Generator Runtime |  | genRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | GEN | 2.15 (Released),2.16 (Pre-Release)
genStarts | genStarts | Generator Starts | Generator Starts |  | genStarts | Yes | No | No | Number |  |  |  |  | 0 | 0 |  |  | generator,starts | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
genStatus | genStatus | Generator Status | Generator Status |  | genStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | generator,status,sensor | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
genSync | genSync | Generator Sync | Generator Sync |  | genSync | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | generator,sync | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
genWarning | genWarning | Generator Warning | Generator Warning |  | genWarning | Yes | Yes | No | Bool | Warning/Normal | Warning/Normal | [6 empty] | generator,warning | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
headPressure | headPressure | Head Pressure | Head Pressure |  | headPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | head,pressure,sensor | AHU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatDetectAlarm | heatDetectAlarm | Heat Detection Alarm | Heat Detection Alarm |  | heatDetectAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | heat,detect,alarm | FP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hxLoad | hxLoad | Heat Exchanger Load | Load |  | hxLoad | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | heatExchanger,load,sensor | HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hxBypassValve | hxBypassValveXXXX | Heat Exchanger Valve Command | Heat Exchanger Valve XX Command |  | hxBypassValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | heatExchanger,water,bypass,valve,position,cmd | HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hxBypassValveFb | hxBypassValveXXXXFb | Heat Exchanger Valve Feedback | Heat Exchanger Valve XX Feedback |  | hxBypassValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | heatExchanger,water,bypass,valve,position,sensor | HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatTraceAlarm | heatTraceXXXXAlarm | Heat Trace Alarm | Heat Trace XX Alarm |  | heatTrace(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | heatTrace,common,alarm | HT | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatTrace | heatTraceXXXX | Heat Trace Command | Heat Trace XX Command |  | heatTrace(\d{0,4}) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | heatTrace,status,cmd | HT | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatTraceStatus | heatTraceXXXXStatus | Heat Trace Status | Heat Trace XX Status |  | heatTrace(\d{0,4})Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | heatTrace,status,sensor | HT | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatTraceTemp | heatTraceXXXXTemp | Heat Trace Temperature | Heat Trace XX Temperature |  | heatTrace(\d{0,4})Temp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | heatTrace,temp,sensor | HT | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCapacityMaxSp | heatingCapacityMaxSp | Heating Capacity Max Setpoint | Heating Capacity Max Setpoint |  | heatingCapacityMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | heat,demand,max,sp | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilDischargeHumidty | heatingCoilXXXXDischargeHumidty | Heating Coil Discharge Humidty | Heating Coil XX Discharge Humidty |  | heatingCoil(\d{0,4})DischargeHumidty | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | heat,coil,air,discharge,humidity,sensor | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released)
heatingCoilDischargeTemp | heatingCoilXXXXDischargeTemp | Heating Coil Discharge Temperature | Heating Coil XX Discharge Temperature |  | heatingCoil(\d{0,4})DischargeTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | heat,coil,air,discharge,temp,sensor | AFMS,AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilDischargeTempDb | heatingCoilXXXXDischargeTempDb | Heating Coil Discharge Temperature Deadband | Heating Coil XX Discharge Temperature Deadband |  | heatingCoil(\d{0,4})DischargeTempDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | heat,coil,air,discharge,temp,deadband,sp | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilDischargeTempHiSp | heatingCoilXXXXDischargeTempHiSp | Heating Coil Discharge Temperature High Setpoint | Heating Coil XX Discharge Temperature High Setpoint |  | heatingCoil(\d{0,4})DischargeTempHiSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | heat,coil,air,discharge,temp,high,sp | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilDischargeTempLoSp | heatingCoilXXXXDischargeTempLoSp | Heating Coil Discharge Temperature Low Setpoint | Heating Coil XX Discharge Temperature Low Setpoint |  | heatingCoil(\d{0,4})DischargeTempLoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | heat,coil,air,discharge,temp,low,sp | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilDischargeTempMaxSp | heatingCoilXXXXDischargeTempMaxSp | Heating Coil Discharge Temperature Max Setpoint | Heating Coil XX Discharge Temperature Max Setpoint |  | heatingCoil(\d{0,4})DischargeTempMaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | heat,coil,air,discharge,temp,max,sp | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilDischargeTempMinSp | heatingCoilXXXXDischargeTempMinSp | Heating Coil Discharge Temperature Min Setpoint | Heating Coil XX Discharge Temperature Min Setpoint |  | heatingCoil(\d{0,4})DischargeTempMinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | heat,coil,air,discharge,temp,min,sp | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilDischargeTempSp | heatingCoilXXXXDischargeTempSp | Heating Coil Discharge Temperature Setpoint | Heating Coil XX Discharge Temperature Setpoint |  | heatingCoil(\d{0,4})DischargeTempSp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | heat,coil,air,discharge,temp,effective,sp | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilDischargeTempUnoccSp | heatingCoilXXXXDischargeTempUnoccSp | Heating Coil Discharge Temperature Unoccupied Setpoint | Heating Coil XX Discharge Temperature Unoccupied Setpoint |  | heatingCoil(\d{0,4})DischargeTempUnoccSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | heat,coil,air,discharge,temp,unoccupied,sp | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilEnergy | heatingCoilXXXXEnergy | Heating Coil Energy | Heating Coil XX Energy |  | heatingCoil(\d{0,4})Energy | Yes | Yes | No | Number |  |  | kilobtu | kilobtu | 0 | 0 |  |  | heat,coil,water,energy,common,sensor | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilEnteringPressure | heatingCoilXXXXEnteringPressure | Heating Coil Entering Pressure | Heating Coil XX Entering Pressure |  | heatingCoil(\d{0,4})EnteringPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | heat,coil,water,entering,pressure,general,sensor | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilEnteringTemp | heatingCoilXXXXEnteringTemp | Heating Coil Entering Temperature | Heating Coil XX Entering Temperature |  | heatingCoil(\d{0,4})EnteringTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | heat,coil,water,entering,temp,sensor | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilFilterAlarm | heatingCoilXXXXFilterAlarm | Heating Coil Filter Alarm | Heating Coil XX Filter Alarm |  | heatingCoil(\d{0,4})FilterAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | heat,coil,air,filter,general,alarm | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilFilterAlarmReset | heatingCoilXXXXFilterAlarmReset | Heating Coil Filter Alarm Reset | Heating Coil XX Filter Alarm Reset |  | heatingCoil(\d{0,4})FilterAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | heat,coil,air,filter,reset,alarm | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,FPB,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilFilterPressureDelta | heatingCoilXXXXFilterPressureDelta | Heating Coil Filter Pressure Delta | Heating Coil XX Filter Pressure Delta |  | heatingCoil(\d{0,4})FilterPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | heat,coil,air,filter,pressure,delta,sensor | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released)
heatingCoilFilterRuntime | heatingCoilXXXXFilterRuntime | Heating Coil Filter Runtime | Heating Coil XX Filter Runtime |  | heatingCoil(\d{0,4})FilterRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.15 (Released),2.16 (Pre-Release)
heatingCoilFlow | heatingCoilXXXXFlow | Heating Coil Flow | Heating Coil XX Flow |  | heatingCoil(\d{0,4})Flow | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | heat,coil,water,flow,status,cmd | AFMS,AHU,ATU,CRAC,CRAH,CU,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilFlowStatus | heatingCoilXXXXFlowStatus | Heating Coil Flow Status | Heating Coil XX Flow Status |  | heatingCoil(\d{0,4})FlowStatus | Yes | Yes | No | Bool | Flow/No Flow | Flow/No Flow | [6 empty] | heat,coil,water,flow,status,sensor | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilLeavingPressure | heatingCoilXXXXLeavingPressure | Heating Coil Leaving Pressure | Heating Coil XX Leaving Pressure |  | heatingCoil(\d{0,4})LeavingPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | heat,coil,water,leaving,pressure,general,sensor | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilLeavingTemp | heatingCoilXXXXLeavingTemp | Heating Coil Leaving Temperature | Heating Coil XX Leaving Temperature |  | heatingCoil(\d{0,4})LeavingTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | heat,coil,water,leaving,temp,sensor | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilPower | heatingCoilXXXXPower | Heating Coil Power | Heating Coil XX Power |  | heatingCoil(\d{0,4})Power | Yes | Yes | No | Number |  |  | kilobtus_per_hour | kilobtus_per_hour | 1 | 1 |  |  | heat,coil,water,power,common,sensor | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilPumpAlarm | heatingCoilXXXXPumpAlarm | Heating Coil Pump Alarm | Heating Coil XX Pump Alarm |  | heatingCoil(\d{0,4})PumpAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | heat,coil,water,pump,common,alarm | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilPumpAlarmReset | heatingCoilXXXXPumpAlarmReset | Heating Coil Pump Alarm Reset | Heating Coil XX Pump Alarm Reset |  | heatingCoil(\d{0,4})PumpAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | heat,coil,water,pump,reset,alarm | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,FPB,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilPump | heatingCoilXXXXPump | Heating Coil Pump Command | Heating Coil XX Pump Command |  | heatingCoil(\d{0,4})Pump | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | heat,coil,water,pump,status,cmd | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,FPB,MAU,RTU,UV,VAV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilPumpCurrent | heatingCoilXXXXPumpCurrent | Heating Coil Pump Current | Heating Coil XX Pump Current |  | heatingCoil(\d{0,4})PumpCurrent | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | heat,coil,water,pump,current,sensor | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilPumpEnable | heatingCoilXXXXPumpEnable | Heating Coil Pump Enable | Heating Coil XX Pump Enable |  | heatingCoil(\d{0,4})PumpEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | heat,coil,water,pump,enable,cmd | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilPumpEnableDb | heatingCoilXXXXPumpEnableDb | Heating Coil Pump Enable Deadband | Heating Coil XX Pump Enable Deadband |  | heatingCoil(\d{0,4})PumpEnableDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | heat,coil,water,pump,enable,deadband,sp | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,FPB,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilPumpEnableSp | heatingCoilXXXXPumpEnableSp | Heating Coil Pump Enable Setpoint | Heating Coil XX Pump Enable Setpoint |  | heatingCoil(\d{0,4})PumpEnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | heat,coil,water,pump,enable,common,sp | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilPumpEnteringPressure | heatingCoilXXXXPumpEnteringPressure | Heating Coil Pump Entering Pressure | Heating Coil XX Pump Entering Pressure |  | heatingCoil(\d{0,4})PumpEnteringPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | heat,coil,water,pump,entering,pressure,sensor | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilPumpFault | heatingCoilXXXXPumpFault | Heating Coil Pump Fault | Heating Coil XX Pump Fault |  | heatingCoil(\d{0,4})PumpFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | heat,coil,water,pump,fault,common | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilPumpLagDisableSp | heatingCoilXXXXPumpLagDisableSp | Heating Coil Pump Lag Disable Setpoint | Heating Coil XX Pump Lag Disable Setpoint |  | heatingCoil(\d{0,4})PumpLagDisableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | heat,coil,water,pump,lag,disable,sp | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilPumpLagEnableSp | heatingCoilXXXXPumpLagEnableSp | Heating Coil Pump Lag Enable Setpoint | Heating Coil XX Pump Lag Enable Setpoint |  | heatingCoil(\d{0,4})PumpLagEnableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | heat,coil,water,pump,lag,enable,sp | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilPumpLagReq | heatingCoilXXXXPumpLagReq | Heating Coil Pump Lag Request | Heating Coil XX Pump Lag Request |  | heatingCoil(\d{0,4})PumpLagReq | No | No | No | Bool | Request/No Request | Request/No Request | [6 empty] | heat,coil,water,pump,lag,request,cmd | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilPumpLead | heatingCoilPumpLead | Heating Coil Pump Lead | Heating Coil Pump Lead |  | heatingCoilPumpLead | Yes | Yes | No | Bool | Lead 1/Lead 2 | Lead 1/Lead 2 | [6 empty] | heat,coil,water,pump,lead,sp | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,FPB,MAU,RTU,UV,VAV,FCU | 2.15 (Released),2.16 (Pre-Release)
heatingCoilPumpLeadXor | heatingCoilPumpLeadXor | Heating Coil Pump Lead Change Over | Heating Coil Pump Lead Change Over |  | heatingCoilPumpLeadXor | No | No | No | Bool | On/Off | On/Off | [6 empty] | heat,coil,water,pump,lead,changeOver,cmd | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,FPB,MAU,RTU,UV,VAV,FCU | 2.15 (Released),2.16 (Pre-Release)
heatingCoilPumpLeadXorRuntimeSp | heatingCoilPumpLeadXorRuntimeSp | Heating Coil Pump Lead Change Over Runtime Setpoint | Heating Coil Pump Lead Change Over Runtime Setpoint |  | heatingCoilPumpLeadXorRuntimeSp | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,FPB,MAU,RTU,UV,VAV,FCU | 2.15 (Released),2.16 (Pre-Release)
heatingCoilPumpLeavingPressure | heatingCoilXXXXPumpLeavingPressure | Heating Coil Pump Leaving Pressure | Heating Coil XX Pump Leaving Pressure |  | heatingCoil(\d{0,4})PumpLeavingPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | heat,coil,water,pump,leaving,pressure,sensor | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilPumpMaintSwitch | heatingCoilXXXXPumpMaintSwitch | Heating Coil Pump Maintenance Switch | Heating Coil XX Pump Maintenance Switch |  | heatingCoil(\d{0,4})PumpMaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | heat,coil,water,pump,maintenance,switch,cmd | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,FPB,MAU,RTU,UV,VAV,FCU | 2.15 (Released),2.16 (Pre-Release)
heatingCoilPumpOvr | heatingCoilXXXXPumpOvr | Heating Coil Pump Override | Heating Coil XX Pump Override |  | heatingCoil(\d{0,4})PumpOvr | No | No | No | Bool | On/Off | On/Off | [6 empty] | heat,coil,water,pump,status,ovr | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilPumpPressureDelta | heatingCoilXXXXPumpPressureDelta | Heating Coil Pump Pressure Delta | Heating Coil XX Pump Pressure Delta |  | heatingCoil(\d{0,4})PumpPressureDelta | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | heat,coil,water,pump,common,pressure,delta,sensor | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilPumpPressureHiAlarm | heatingCoilXXXXPumpPressureHiAlarm | Heating Coil Pump Pressure High Alarm | Heating Coil XX Pump Pressure High Alarm |  | heatingCoil(\d{0,4})PumpPressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | heat,coil,water,pump,pressure,high,alarm | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilPumpPressureHiSp | heatingCoilXXXXPumpPressureHiSp | Heating Coil Pump Pressure High Setpoint | Heating Coil XX Pump Pressure High Setpoint |  | heatingCoil(\d{0,4})PumpPressureHiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | heat,coil,water,pump,pressure,high,sp | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilPumpPressureLoAlarm | heatingCoilXXXXPumpPressureLoAlarm | Heating Coil Pump Pressure Low Alarm | Heating Coil XX Pump Pressure Low Alarm |  | heatingCoil(\d{0,4})PumpPressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | heat,coil,water,pump,pressure,low,alarm | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilPumpPressureLoSp | heatingCoilXXXXPumpPressureLoSp | Heating Coil Pump Pressure Low Setpoint | Heating Coil XX Pump Pressure Low Setpoint |  | heatingCoil(\d{0,4})PumpPressureLoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | heat,coil,water,pump,pressure,low,sp | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilPumpRuntime | heatingCoilXXXXPumpRuntime | Heating Coil Pump Runtime | Heating Coil XX Pump Runtime |  | heatingCoil(\d{0,4})PumpRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.15 (Released),2.16 (Pre-Release)
heatingCoilPumpSpeed | heatingCoilXXXXPumpSpeed | Heating Coil Pump Speed | Heating Coil XX Pump Speed |  | heatingCoil(\d{0,4})PumpSpeed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | heat,coil,water,pump,speed,cmd | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilPumpSpeedFb | heatingCoilXXXXPumpSpeedFb | Heating Coil Pump Speed Feedback | Heating Coil XX Pump Speed Feedback |  | heatingCoil(\d{0,4})PumpSpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | heat,coil,water,pump,speed,sensor | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilPumpSpeedMaxSp | heatingCoilXXXXPumpSpeedMaxSp | Heating Coil Pump Speed Max Setpoint | Heating Coil XX Pump Speed Max Setpoint |  | heatingCoil(\d{0,4})PumpSpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | heat,coil,water,pump,speed,max,sp | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilPumpSpeedMinSp | heatingCoilXXXXPumpSpeedMinSp | Heating Coil Pump Speed Min Setpoint | Heating Coil XX Pump Speed Min Setpoint |  | heatingCoil(\d{0,4})PumpSpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | heat,coil,water,pump,speed,min,sp | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilPumpSpeedOvr | heatingCoilXXXXPumpSpeedOvr | Heating Coil Pump Speed Override | Heating Coil XX Pump Speed Override |  | heatingCoil(\d{0,4})PumpSpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | heat,coil,water,pump,speed,ovr | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilPumpSpeedSp | heatingCoilXXXXPumpSpeedSp | Heating Coil Pump Speed Setpoint | Heating Coil XX Pump Speed Setpoint |  | heatingCoil(\d{0,4})PumpSpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | heat,coil,water,pump,speed,effective,sp | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilPumpStatus | heatingCoilXXXXPumpStatus | Heating Coil Pump Status | Heating Coil XX Pump Status |  | heatingCoil(\d{0,4})PumpStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | heat,coil,water,pump,status,sensor | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,FPB,MAU,RTU,UV,VAV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilStrainerAlarm | heatingCoilXXXXStrainerAlarm | Heating Coil Strainer Alarm | Heating Coil XX Strainer Alarm |  | heatingCoil(\d{0,4})StrainerAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | heat,water,strainer,common,alarm | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingCoilStrainerEnable | heatingCoilXXXXStrainerEnable | Heating Coil Strainer Enable | Heating Coil XX Strainer Enable |  | heatingCoil(\d{0,4})StrainerEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | heat,water,strainer,enable,cmd | AHU,ATU,CRAC,CRAH,CUH,DHU,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingDemand | heatingDemand | Heating Demand | Heating Demand |  | heatingDemand | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | heat,common,load,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,FCU,FPB,MAU,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingEnable | heatingEnable | Heating Enable Command | Heating Enable Command |  | heatingEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | heat,enable,common,cmd | AHU,ATU,BLR,CRAC,CRAH,CUH,DH,DHU,DOAS,FCU,FPB,HP,HWS,MAU,PH,PIU,RP,RPC,RPF,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingEnableDb | heatingEnableDb | Heating Enable Deadband | Heating Enable Deadband |  | heatingEnableDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | heat,enable,common,deadband,sp | AHU,ATU,BLR,CRAC,CRAH,CUH,DH,DHU,DOAS,FCU,FPB,HP,HWS,MAU,PH,PIU,RP,RPC,RPF,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingEnableSp | heatingEnableSp | Heating Enable Setpoint | Heating Enable Setpoint |  | heatingEnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | heat,enable,effective,sp | AHU,ATU,BLR,CRAC,CRAH,CUH,DH,DHU,DOAS,FCU,FPB,HP,HWS,MAU,PH,PIU,RP,RPC,RPF,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingStageAlarm | heatingStageXXXXAlarm | Heating Stage Alarm | Heating Stage XX Alarm |  | heatingStage(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal |  |  |  |  | XX |  | heat,status,alarm | AHU,ATU,BLR,CRAC,CRAH,CUH,DH,DHU,DOAS,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingStageAlarmReset | heatingStageXXXXAlarmReset | Heating Stage Alarm Reset | Heating Stage XX Alarm Reset |  | heatingStage(\d{0,4})AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal |  |  |  |  | XX |  | heat,reset,alarm | AHU,ATU,BLR,CRAC,CRAH,CUH,DH,DHU,DOAS,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingStage | heatingStageXXXX | Heating Stage Command | Heating Stage XX Command |  | heatingStage(\d{0,4}) | Yes | Yes | No | Bool | On/Off | On/Off |  |  |  |  | XX |  | heat,status,cmd | AHU,ATU,BLR,CRAC,CRAH,CUH,DH,DHU,DOAS,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingStageEnable | heatingStageXXXXEnable | Heating Stage Enable | Heating Stage XX Enable |  | heatingStage(\d{0,4})Enable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled |  |  |  |  | XX |  | heat,lockout,cmd | AHU,ATU,BLR,CRAC,CRAH,CUH,DH,DHU,DOAS,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingStageEnableSp | heatingStageXXXXEnableSp | Heating Stage Enable Setpoint | Heating Stage XX Enable Setpoint |  | heatingStage(\d{0,4})EnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 | XX |  | heat,enable,sp | AHU,ATU,BLR,CRAC,CRAH,CUH,DH,DHU,DOAS,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingStageLead | heatingStageLead | Heating Stage Lead | Heating Stage Lead |  | heatingStageLead | Yes | Yes | No | Bool | Lead 1/Lead 2 | Lead 1/Lead 2 | [6 empty] | heat,lead,cmd | AHU,ATU,BLR,CRAC,CRAH,CUH,DH,DHU,DOAS,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingStageMinOffSp | heatingStageXXXXMinOffSp | Heating Stage Min Off Time Setpoint | Heating Stage XX Min Off Time Setpoint |  | heatingStage(\d{0,4})MinOffSp | No | No | No | Number |  |  | second | second | 0 | 0 | XX |  | heat,min,off,sp | AHU,ATU,BLR,CRAC,CRAH,CUH,DH,DHU,DOAS,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingStageMinOnSp | heatingStageXXXXMinOnSp | Heating Stage Min On Time Setpoint | Heating Stage XX Min On Time Setpoint |  | heatingStage(\d{0,4})MinOnSp | No | No | No | Number |  |  | second | second | 0 | 0 | XX |  | heat,min,on,sp | AHU,ATU,BLR,CRAC,CRAH,CUH,DH,DHU,DOAS,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingStageMod | heatingStageXXXXMod | Heating Stage Modulation Command | Heating Stage XX Modulation Command |  | heatingStage(\d{0,4})Mod | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 | XX |  | heat,modulation,cmd | AHU,ATU,BLR,CRAC,CRAH,CUH,DH,DHU,DOAS,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingStageModOvr | heatingStageXXXXModOvr | Heating Stage Modulation Override | Heating Stage XX Modulation Override |  | heatingStage(\d{0,4})ModOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 | XX |  | heat,modulation,ovr | AHU,ATU,BLR,CRAC,CRAH,CUH,DH,DHU,DOAS,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingStageOvr | heatingStageXXXXOvr | Heating Stage Override | Heating Stage XX Override |  | heatingStage(\d{0,4})Ovr | No | No | No | Bool | On/Off | On/Off |  |  |  |  | XX |  | heat,status,ovr | AHU,ATU,BLR,CRAC,CRAH,CUH,DH,DHU,DOAS,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingStageRuntime | heatingStageXXXXRuntime | Heating Stage Runtime | Heating Stage XX Runtime |  | heatingStage(\d{0,4})Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 | XX |  | blacklist | AHU,ATU,BLR,CRAC,CRAH,CUH,DH,DHU,DOAS,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.15 (Released),2.16 (Pre-Release)
heatingStageStatus | heatingStageXXXXStatus | Heating Stage Status | Heating Stage XX Status |  | heatingStage(\d{0,4})Status | Yes | Yes | No | Bool | On/Off | On/Off |  |  |  |  | XX |  | heat,status,sensor | AHU,ATU,BLR,CRAC,CRAH,CUH,DH,DHU,DOAS,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingStageTempHiAlarm | heatingStageXXXXTempHiAlarm | Heating Stage Temperature High Alarm | Heating Stage XX Temperature High Alarm |  | heatingStage(\d{0,4})TempHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal |  |  |  |  | XX |  | heat,temp,high,alarm | AHU,ATU,BLR,CRAC,CRAH,CUH,DH,DHU,DOAS,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingValveOneThird | heatingValveOneThird | Heating Valve 1/3 Command | Heating Valve 1/3 Command |  | heatingValveOneThird | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | heat,valve,position,oneThird,cmd | AHU,CRAC,CRAH,DHU,DOAS,MAU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingValveOneThirdFb | heatingValveOneThirdFb | Heating Valve 1/3 Feedback | Heating Valve 1/3 Feedback |  | heatingValveOneThirdFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | heat,valve,position,oneThird,sensor | AHU,CRAC,CRAH,DHU,DOAS,MAU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingValveOneThirdOvr | heatingValveOneThirdOvr | Heating Valve 1/3 Override | Heating Valve 1/3 Override |  | heatingValveOneThirdOvr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | heat,valve,position,oneThird,ovr | AHU,CRAC,CRAH,DHU,DOAS,MAU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingValveTwoThird | heatingValveTwoThird | Heating Valve 2/3 Command | Heating Valve 2/3 Command |  | heatingValveTwoThird | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | heat,valve,position,twoThird,cmd | AHU,CRAC,CRAH,DHU,DOAS,MAU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingValveTwoThirdFb | heatingValveTwoThirdFb | Heating Valve 2/3 Feedback | Heating Valve 2/3 Feedback |  | heatingValveTwoThirdFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | heat,valve,position,twoThird,sensor | AHU,CRAC,CRAH,DHU,DOAS,MAU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingValveTwoThirdOvr | heatingValveTwoThirdOvr | Heating Valve 2/3 Override | Heating Valve 2/3 Override |  | heatingValveTwoThirdOvr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | heat,valve,position,twoThird,ovr | AHU,CRAC,CRAH,DHU,DOAS,MAU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingValve | heatingValveXXXX | Heating Valve Command | Heating Valve XX Command |  | heatingValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 | XX |  | heat,valve,position,cmd | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingValveFb | heatingValveXXXXFb | Heating Valve Feedback | Heating Valve XX Feedback |  | heatingValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 | XX |  | heat,valve,position,sensor | AHU,ATU,CRAC,CRAH,DH,DHU,DOAS,FCU,FPB,MAU,RTU,UV,VAV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
heatingValveOvr | heatingValveXXXXOvr | Heating Valve Override | Heating Valve XX Override |  | heatingValve(\d{0,4})Ovr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 | XX |  | heat,valve,position,ovr | AHU,ATU,CRAC,CRAH,DH,DHU,DOAS,FCU,FPB,MAU,RTU,UV,VAV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
highLimitAlarm | highLimitAlarm | High Limit Thermostat | High Limit Thermostat |  | highLimitAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | high,limit,alarm | AHU,ATU,CRAC,CRAH,DOAS,FCU,MAU,RTU,UV,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanAlarm | hvhsFanXXXXAlarm | High Velocity High Speed Fan Alarm | High Velocity High Speed Fan XX Alarm |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | hvhs,air,fan,common,alarm | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanAlarmReset | hvhsFanXXXXAlarmReset | High Velocity High Speed Fan Alarm Reset | High Velocity High Speed Fan XX Alarm Reset |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | hvhs,air,fan,alarm,reset | HVHS | 2.15 (Released),2.16 (Pre-Release)
hvhsFan | hvhsFanXXXX | High Velocity High Speed Fan Command | High Velocity High Speed Fan XX Command |  | hvhsFan((?:(?!Ovr)\w){0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | hvhs,air,fan,status,cmd | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanCurrent | hvhsFanXXXXCurrent | High Velocity High Speed Fan Current | High Velocity High Speed Fan XX Current |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))Current | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  |  | hvhs,air,fan,current,sensor | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanDCVoltage | hvhsFanXXXXDCVoltage | High Velocity High Speed Fan DC Voltage | High Velocity High Speed Fan XX DC Voltage |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))DCVoltage | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  |  | hvhs,air,fan,dcVolt,sensor | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanDirection | hvhsFanXXXXDirection | High Velocity High Speed Fan Direction | High Velocity High Speed Fan XX Direction |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))Direction | Yes | Yes | No | Bool | Upflow/Downflow | Upflow/Downflow | [6 empty] | hvhs,air,fan,direction,cmd | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanDirectionOvr | hvhsFanXXXXDirectionOvr | High Velocity High Speed Fan Direction Override | High Velocity High Speed Fan XX Direction Override |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))DirectionOvr | No | No | No | Bool | Upflow/Downflow | Upflow/Downflow | [6 empty] | hvhs,air,fan,direction,ovr | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanDirectionStatus | hvhsFanXXXXDirectionStatus | High Velocity High Speed Fan Direction Status | High Velocity High Speed Fan XX Direction Status |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))DirectionStatus | Yes | Yes | No | Bool | Upflow/Downflow | Upflow/Downflow | [6 empty] | hvhs,air,fan,direction,status | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanDriveAlarm | hvhsFanXXXXDriveAlarm | High Velocity High Speed Fan Drive Alarm | High Velocity High Speed Fan XX Drive Alarm |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))DriveAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | hvhs,air,fan,drive,alarm | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanDriveTemp | hvhsFanXXXXDriveTemp | High Velocity High Speed Fan Drive Temperature | High Velocity High Speed Fan XX Drive Temperature |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))DriveTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | hvhs,air,fan,driveTemp,sensor | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanEnergy | hvhsFanXXXXEnergy | High Velocity High Speed Fan Energy | High Velocity High Speed Fan XX Energy |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))Energy | Yes | Yes | No | Number |  |  | kilowatt_hour | kilowatt_hour | 0 | 0 |  |  | hvhs,air,fan,energy,sensor | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanFault | hvhsFanXXXXFault | High Velocity High Speed Fan Fault | High Velocity High Speed Fan XX Fault |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | hvhs,air,fan,fault,common | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanFaultCode | hvhsFanXXXXFaultCode | High Velocity High Speed Fan Fault Code | High Velocity High Speed Fan XX Fault Code |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))FaultCode | Yes | Yes | No | Str | [8 empty] | hvhs,air,fan,fault,code | HVHS | 2.15 (Released)
hvhsFanFaultReset | hvhsFanXXXXFaultReset | High Velocity High Speed Fan Fault Reset | High Velocity High Speed Fan XX Fault Reset |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))FaultReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | hvhs,air,fan,fault,reset | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanFrequency | hvhsFanXXXXFrequency | High Velocity High Speed Fan Frequency | High Velocity High Speed Fan XX Frequency |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))Frequency | Yes | Yes | No | Number |  |  | hertz | hertz | 1 | 1 |  |  | hvhs,air,fan,freq,sensor | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanHandMode | hvhsFanXXXXHandMode | High Velocity High Speed Fan Hand Mode | High Velocity High Speed Fan XX Hand Mode |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))HandMode | Yes | Yes | No | Bool | Hand/Auto | Hand/Auto | [6 empty] | hvhs,air,fan,handMode,sensor | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanMaintSwitch | hvhsFanXXXXMaintSwitch | High Velocity High Speed Fan Maintenance Switch | High Velocity High Speed Fan XX Maintenance Switch |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))MaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | hvhs,air,fan,maintenance,switch,cmd | HVHS | 2.15 (Released),2.16 (Pre-Release)
hvhsFanMotorSpeed | hvhsFanXXXXMotorSpeed | High Velocity High Speed Fan Motor Speed | High Velocity High Speed Fan XX Motor Speed |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))MotorSpeed | Yes | Yes | No | Number |  |  | revolutions_per_minute | revolutions_per_minute | 0 | 0 |  |  | hvhs,air,fan,motorSpeed,sensor | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanMotorTemp | hvhsFanXXXXMotorTemp | High Velocity High Speed Fan Motor Temperature | High Velocity High Speed Fan XX Motor Temperature |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))MotorTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | hvhs,air,fan,motorTemp,sensor | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanOvr | hvhsFanXXXXOvr | High Velocity High Speed Fan Override | High Velocity High Speed Fan XX Override |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))Ovr | No | No | No | Bool | On/Off | On/Off | [6 empty] | hvhs,air,fan,status,ovr | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanPowerReal | hvhsFanXXXXPowerReal | High Velocity High Speed Fan Real Power | High Velocity High Speed Fan XX Real Power |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))PowerReal | Yes | Yes | No | Number |  |  | kilowatt | kilowatt | 1 | 1 |  | N | hvhs,air,fan,power,real,sensor | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanRuntime | hvhsFanXXXXRuntime | High Velocity High Speed Fan Runtime | High Velocity High Speed Fan XX Runtime |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | HVHS | 2.15 (Released),2.16 (Pre-Release)
hvhsFanShutdownSwitch | hvhsFanXXXXShutdownSwitch | High Velocity High Speed Fan Shutdown Switch | High Velocity High Speed Fan XX Shutdown Switch |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))ShutdownSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | hvhs,air,fan,shutdown,switch,cmd | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanSpeed | hvhsFanXXXXSpeed | High Velocity High Speed Fan Speed | High Velocity High Speed Fan XX Speed |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))Speed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | hvhs,air,fan,speed,cmd | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanSpeedFb | hvhsFanXXXXSpeedFb | High Velocity High Speed Fan Speed Feedback | High Velocity High Speed Fan XX Speed Feedback |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))SpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | hvhs,air,fan,speed,sensor | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanSpeedMaxSp | hvhsFanXXXXSpeedMaxSp | High Velocity High Speed Fan Speed Max Setpoint | High Velocity High Speed Fan XX Speed Max Setpoint |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))SpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | hvhs,air,fan,speed,max,sp | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanSpeedMinSp | hvhsFanXXXXSpeedMinSp | High Velocity High Speed Fan Speed Min Setpoint | High Velocity High Speed Fan XX Speed Min Setpoint |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))SpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | hvhs,air,fan,speed,min,sp | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanSpeedMode | hvhsFanXXXXSpeedMode | High Velocity High Speed Fan Speed Mode | High Velocity High Speed Fan XX Speed Mode |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))SpeedMode | Yes | No | No | Str | Fixed Speed/Temperature Controlled | Fixed Speed/Temperature Controlled | [6 empty] | hvhs,air,fan,speed,mode,sp | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanSpeedOccSp | hvhsFanXXXXSpeedOccSp | High Velocity High Speed Fan Speed Occupied Setpoint | High Velocity High Speed Fan XX Speed Occupied Setpoint |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))SpeedOccSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | hvhs,air,fan,speed,occupied,sp | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanSpeedOvr | hvhsFanXXXXSpeedOvr | High Velocity High Speed Fan Speed Override | High Velocity High Speed Fan XX Speed Override |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))SpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | hvhs,air,fan,speed,ovr | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanSpeedSp | hvhsFanXXXXSpeedSp | High Velocity High Speed Fan Speed Setpoint | High Velocity High Speed Fan XX Speed Setpoint |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))SpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | hvhs,air,fan,speed,effective,sp | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanSpeedStage | hvhsFanXXXXSpeedStage | High Velocity High Speed Fan Speed Stage | High Velocity High Speed Fan XX Speed Stage |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))SpeedStage | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | hvhs,air,fan,speed,stage | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanSpeedUnoccSp | hvhsFanXXXXSpeedUnoccSp | High Velocity High Speed Fan Speed Unoccupied Setpoint | High Velocity High Speed Fan XX Speed Unoccupied Setpoint |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))SpeedUnoccSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | hvhs,air,fan,speed,unoccupied,sp | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanStageSp | hvhsFanXXXXStageSp | High Velocity High Speed Fan Stage Setpoint | High Velocity High Speed Fan XX Stage Setpoint |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))StageSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | hvhs,air,fan,stage,sp | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanStatus | hvhsFanXXXXStatus | High Velocity High Speed Fan Status | High Velocity High Speed Fan XX Status |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | hvhs,air,fan,status,sensor | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanTorque | hvhsFanXXXXTorque | High Velocity High Speed Fan Torque | High Velocity High Speed Fan XX Torque |  | hvhsFan(\w{0,4}(?=[A-Z]¦$))Torque | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | hvhs,air,fan,torque,sensor | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvhsFanVoltage | hvhsFanXXXXVoltage | High Velocity High Speed Fan Voltage | High Velocity High Speed Fan XX Voltage |  | hvhsFan((?:(?!DC)\w){0,4}(?=[A-Z]¦$))Voltage | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  |  | hvhs,air,fan,volt,sensor | HVHS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanAlarm | hvlsFanXXXXAlarm | High Velocity Low Speed Fan Alarm | High Velocity Low Speed Fan XX Alarm |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | hvls,air,fan,common,alarm | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanAlarmReset | hvlsFanXXXXAlarmReset | High Velocity Low Speed Fan Alarm Reset | High Velocity Low Speed Fan XX Alarm Reset |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | hvls,air,fan,alarm,reset | HVLS | 2.15 (Released),2.16 (Pre-Release)
hvlsFan | hvlsFanXXXX | High Velocity Low Speed Fan Command | High Velocity Low Speed Fan XX Command |  | hvlsFan((?:(?!Ovr)\w){0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | hvls,air,fan,status,cmd | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanCurrent | hvlsFanXXXXCurrent | High Velocity Low Speed Fan Current | High Velocity Low Speed Fan XX Current |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))Current | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  |  | hvls,air,fan,current,sensor | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanDCVoltage | hvlsFanXXXXDCVoltage | High Velocity Low Speed Fan DC Voltage | High Velocity Low Speed Fan XX DC Voltage |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))DCVoltage | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  |  | hvls,air,fan,dcVolt,sensor | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanDirection | hvlsFanXXXXDirection | High Velocity Low Speed Fan Direction | High Velocity Low Speed Fan XX Direction |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))Direction | Yes | Yes | No | Bool | Upflow/Downflow | Upflow/Downflow | [6 empty] | hvls,air,fan,direction,cmd | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanDirectionOvr | hvlsFanXXXXDirectionOvr | High Velocity Low Speed Fan Direction Override | High Velocity Low Speed Fan XX Direction Override |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))DirectionOvr | No | No | No | Bool | Upflow/Downflow | Upflow/Downflow | [6 empty] | hvls,air,fan,direction,ovr | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanDirectionStatus | hvlsFanXXXXDirectionStatus | High Velocity Low Speed Fan Direction Status | High Velocity Low Speed Fan XX Direction Status |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))DirectionStatus | Yes | Yes | No | Bool | Upflow/Downflow | Upflow/Downflow | [6 empty] | hvls,air,fan,direction,status | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanDriveAlarm | hvlsFanXXXXDriveAlarm | High Velocity Low Speed Fan Drive Alarm | High Velocity Low Speed Fan XX Drive Alarm |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))DriveAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | hvls,air,fan,drive,alarm | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanDriveTemp | hvlsFanXXXXDriveTemp | High Velocity Low Speed Fan Drive Temperature | High Velocity Low Speed Fan XX Drive Temperature |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))DriveTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | hvls,air,fan,driveTemp,sensor | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanEnergy | hvlsFanXXXXEnergy | High Velocity Low Speed Fan Energy | High Velocity Low Speed Fan XX Energy |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))Energy | Yes | Yes | No | Number |  |  | kilowatt_hour | kilowatt_hour | 0 | 0 |  |  | hvls,air,fan,energy,sensor | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanFault | hvlsFanXXXXFault | High Velocity Low Speed Fan Fault | High Velocity Low Speed Fan XX Fault |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | hvls,air,fan,fault,common | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanFaultCode | hvlsFanXXXXFaultCode | High Velocity Low Speed Fan Fault Code | High Velocity Low Speed Fan XX Fault Code |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))FaultCode | Yes | Yes | No | Str | [8 empty] | hvls,air,fan,fault,code | HVLS | 2.15 (Released)
hvlsFanFaultReset | hvlsFanXXXXFaultReset | High Velocity Low Speed Fan Fault Reset | High Velocity Low Speed Fan XX Fault Reset |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))FaultReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | hvls,air,fan,fault,reset | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanFrequency | hvlsFanXXXXFrequency | High Velocity Low Speed Fan Frequency | High Velocity Low Speed Fan XX Frequency |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))Frequency | Yes | Yes | No | Number |  |  | hertz | hertz | 1 | 1 |  |  | hvls,air,fan,freq,sensor | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanHandMode | hvlsFanXXXXHandMode | High Velocity Low Speed Fan Hand Mode | High Velocity Low Speed Fan XX Hand Mode |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))HandMode | Yes | Yes | No | Bool | Hand/Auto | Hand/Auto | [6 empty] | hvls,air,fan,handMode,sensor | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanMaintSwitch | hvlsFanXXXXMaintSwitch | High Velocity Low Speed Fan Maintenance Switch | High Velocity Low Speed Fan XX Maintenance Switch |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))MaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | hvls,air,fan,maintenance,switch,cmd | HVLS | 2.15 (Released),2.16 (Pre-Release)
hvlsFanMotorSpeed | hvlsFanXXXXMotorSpeed | High Velocity Low Speed Fan Motor Speed | High Velocity Low Speed Fan XX Motor Speed |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))MotorSpeed | Yes | Yes | No | Number |  |  | revolutions_per_minute | revolutions_per_minute | 0 | 0 |  |  | hvls,air,fan,motorSpeed,sensor | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanMotorTemp | hvlsFanXXXXMotorTemp | High Velocity Low Speed Fan Motor Temperature | High Velocity Low Speed Fan XX Motor Temperature |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))MotorTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | hvls,air,fan,motorTemp,sensor | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanOvr | hvlsFanXXXXOvr | High Velocity Low Speed Fan Override | High Velocity Low Speed Fan XX Override |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))Ovr | No | No | No | Bool | On/Off | On/Off | [6 empty] | hvls,air,fan,status,ovr | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanPowerReal | hvlsFanXXXXPowerReal | High Velocity Low Speed Fan Real Power | High Velocity Low Speed Fan XX Real Power |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))PowerReal | Yes | Yes | No | Number |  |  | kilowatt | kilowatt | 1 | 1 |  | N | hvls,air,fan,power,real,sensor | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanRuntime | hvlsFanXXXXRuntime | High Velocity Low Speed Fan Runtime | High Velocity Low Speed Fan XX Runtime |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | HVLS | 2.15 (Released),2.16 (Pre-Release)
hvlsFanShutdownSwitch | hvlsFanXXXXShutdownSwitch | High Velocity Low Speed Fan Shutdown Switch | High Velocity Low Speed Fan XX Shutdown Switch |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))ShutdownSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | hvls,air,fan,shutdown,switch,cmd | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanSpeed | hvlsFanXXXXSpeed | High Velocity Low Speed Fan Speed | High Velocity Low Speed Fan XX Speed |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))Speed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | hvls,air,fan,speed,cmd | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanSpeedFb | hvlsFanXXXXSpeedFb | High Velocity Low Speed Fan Speed Feedback | High Velocity Low Speed Fan XX Speed Feedback |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))SpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | hvls,air,fan,speed,sensor | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanSpeedMaxSp | hvlsFanXXXXSpeedMaxSp | High Velocity Low Speed Fan Speed Max Setpoint | High Velocity Low Speed Fan XX Speed Max Setpoint |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))SpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | hvls,air,fan,speed,max,sp | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanSpeedMinSp | hvlsFanXXXXSpeedMinSp | High Velocity Low Speed Fan Speed Min Setpoint | High Velocity Low Speed Fan XX Speed Min Setpoint |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))SpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | hvls,air,fan,speed,min,sp | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanSpeedMode | hvlsFanXXXXSpeedMode | High Velocity Low Speed Fan Speed Mode | High Velocity Low Speed Fan XX Speed Mode |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))SpeedMode | Yes | No | No | Str | Fixed Speed/Temperature Controlled | Fixed Speed/Temperature Controlled | [6 empty] | hvls,air,fan,speed,mode,sp | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanSpeedOccSp | hvlsFanXXXXSpeedOccSp | High Velocity Low Speed Fan Speed Occupied Setpoint | High Velocity Low Speed Fan XX Speed Occupied Setpoint |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))SpeedOccSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | hvls,air,fan,speed,occupied,sp | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanSpeedOvr | hvlsFanXXXXSpeedOvr | High Velocity Low Speed Fan Speed Override | High Velocity Low Speed Fan XX Speed Override |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))SpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | hvls,air,fan,speed,ovr | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanSpeedSp | hvlsFanXXXXSpeedSp | High Velocity Low Speed Fan Speed Setpoint | High Velocity Low Speed Fan XX Speed Setpoint |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))SpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | hvls,air,fan,speed,effective,sp | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanSpeedStage | hvlsFanXXXXSpeedStage | High Velocity Low Speed Fan Speed Stage | High Velocity Low Speed Fan XX Speed Stage |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))SpeedStage | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | hvls,air,fan,speed,stage | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanSpeedUnoccSp | hvlsFanXXXXSpeedUnoccSp | High Velocity Low Speed Fan Speed Unoccupied Setpoint | High Velocity Low Speed Fan XX Speed Unoccupied Setpoint |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))SpeedUnoccSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | hvls,air,fan,speed,unoccupied,sp | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanStageSp | hvlsFanXXXXStageSp | High Velocity Low Speed Fan Stage Setpoint | High Velocity Low Speed Fan XX Stage Setpoint |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))StageSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | hvls,air,fan,stage,sp | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanStatus | hvlsFanXXXXStatus | High Velocity Low Speed Fan Status | High Velocity Low Speed Fan XX Status |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | hvls,air,fan,status,sensor | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanTorque | hvlsFanXXXXTorque | High Velocity Low Speed Fan Torque | High Velocity Low Speed Fan XX Torque |  | hvlsFan(\w{0,4}(?=[A-Z]¦$))Torque | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | hvls,air,fan,torque,sensor | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvlsFanVoltage | hvlsFanXXXXVoltage | High Velocity Low Speed Fan Voltage | High Velocity Low Speed Fan XX Voltage |  | hvlsFan((?:(?!DC)\w){0,4}(?=[A-Z]¦$))Voltage | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  |  | hvls,air,fan,volt,sensor | HVLS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
horn | hornXXXX | Horn Command | Horn XX Command |  | horn(\d{0,4}) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | horn,status,cmd | FP,GDS,HDS,LDS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hornSilence | hornSilence | Horn Silence | Horn Silence |  | hornSilence | Yes | Yes | No | Bool | Silence/Normal | Silence/Normal | [6 empty] | horn,silence,cmd | FP,MSC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDamper | hotDeckDamperXXXX | Hot Deck Damper Command | Hot Deck Damper XX Command |  | hotDeckDamper(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | hotDeck,air,damper,position,cmd | AHU,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDamperFb | hotDeckDamperXXXXFb | Hot Deck Damper Feedback | Hot Deck Damper XX Feedback |  | hotDeckDamper(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | hotDeck,air,damper,position,sensor | AHU,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDamperOvr | hotDeckDamperXXXXOvr | Hot Deck Damper Override | Hot Deck Damper XX Override |  | hotDeckDamper(\d{0,4})Ovr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | hotDeck,air,damper,position,ovr | AHU,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeFlow | hotDeckDischargeFlowXXXX | Hot Deck Discharge Airflow | Hot Deck Discharge Airflow XX |  | hotDeckDischargeFlow(\d{0,4}) | Yes | Yes | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | hotDeck,discharge,air,flow,sensor | AFMS,AHU,CU,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeFlowHiSp | hotDeckDischargeFlowXXXXHiSp | Hot Deck Discharge Airflow High Setpoint | Hot Deck Discharge Airflow XX High Setpoint |  | hotDeckDischargeFlow(\d{0,4})HiSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | hotDeck,discharge,air,flow,high,sp | AHU,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeFlowLoSp | hotDeckDischargeFlowXXXXLoSp | Hot Deck Discharge Airflow Low Setpoint | Hot Deck Discharge Airflow XX Low Setpoint |  | hotDeckDischargeFlow(\d{0,4})LoSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | hotDeck,discharge,air,flow,low,sp | AHU,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeFlowMaxSp | hotDeckDischargeFlowXXXXMaxSp | Hot Deck Discharge Airflow Max Setpoint | Hot Deck Discharge Airflow XX Max Setpoint |  | hotDeckDischargeFlow(\d{0,4})MaxSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | hotDeck,discharge,air,flow,max,sp | AHU,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeFlowMinSp | hotDeckDischargeFlowXXXXMinSp | Hot Deck Discharge Airflow Min Setpoint | Hot Deck Discharge Airflow XX Min Setpoint |  | hotDeckDischargeFlow(\d{0,4})MinSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | hotDeck,discharge,air,flow,min,sp | AHU,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeFlowSp | hotDeckDischargeFlowXXXXSp | Hot Deck Discharge Airflow Setpoint | Hot Deck Discharge Airflow XX Setpoint |  | hotDeckDischargeFlow(\d{0,4})Sp | Yes | Yes | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | hotDeck,discharge,air,flow,effective,sp | AHU,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeDehumidMaxSp | hotDeckDischargeDehumidXXXXMaxSp | Hot Deck Discharge Dehumidification Max Reset Setpoint | Hot Deck Discharge Dehumidification XX Max Reset Setpoint |  | hotDeckDischargeDehumid(\d{0,4})MaxSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | hotDeck,discharge,air,dehumid,max,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeDehumidMinSp | hotDeckDischargeDehumidXXXXMinSp | Hot Deck Discharge Dehumidification Min Reset Setpoint | Hot Deck Discharge Dehumidification XX Min Reset Setpoint |  | hotDeckDischargeDehumid(\d{0,4})MinSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | hotDeck,discharge,air,dehumid,min,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeDehumidSp | hotDeckDischargeDehumidXXXXSp | Hot Deck Discharge Dehumidification Setpoint | Hot Deck Discharge Dehumidification XX Setpoint |  | hotDeckDischargeDehumid(\d{0,4})Sp | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | hotDeck,discharge,air,dehumid,effective,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeEnthalpy | hotDeckDischargeEnthalpyXXXX | Hot Deck Discharge Enthalpy | Hot Deck Discharge Enthalpy XX |  | hotDeckDischargeEnthalpy(\d{0,4}) | Yes | Yes | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | hotDeck,discharge,air,enthalpy,sensor | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeEnthalpyDb | hotDeckDischargeEnthalpyXXXXDb | Hot Deck Discharge Enthalpy Deadband | Hot Deck Discharge Enthalpy XX Deadband |  | hotDeckDischargeEnthalpy(\d{0,4})Db | No | No | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | hotDeck,discharge,air,enthalpy,deadband,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeEnthalpyHiSp | hotDeckDischargeEnthalpyXXXXHiSp | Hot Deck Discharge Enthalpy High Setpoint | Hot Deck Discharge Enthalpy XX High Setpoint |  | hotDeckDischargeEnthalpy(\d{0,4})HiSp | No | No | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | hotDeck,discharge,air,enthalpy,high,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeEnthalpyLoSp | hotDeckDischargeEnthalpyXXXXLoSp | Hot Deck Discharge Enthalpy Low Setpoint | Hot Deck Discharge Enthalpy XX Low Setpoint |  | hotDeckDischargeEnthalpy(\d{0,4})LoSp | No | No | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | hotDeck,discharge,air,enthalpy,low,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeEnthalpyMaxSp | hotDeckDischargeEnthalpyXXXXMaxSp | Hot Deck Discharge Enthalpy Max Setpoint | Hot Deck Discharge Enthalpy XX Max Setpoint |  | hotDeckDischargeEnthalpy(\d{0,4})MaxSp | No | No | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | hotDeck,discharge,air,enthalpy,max,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeEnthalpyMinSp | hotDeckDischargeEnthalpyXXXXMinSp | Hot Deck Discharge Enthalpy Min Setpoint | Hot Deck Discharge Enthalpy XX Min Setpoint |  | hotDeckDischargeEnthalpy(\d{0,4})MinSp | No | No | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | hotDeck,discharge,air,enthalpy,min,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeEnthalpySp | hotDeckDischargeEnthalpyXXXXSp | Hot Deck Discharge Enthalpy Setpoint | Hot Deck Discharge Enthalpy XX Setpoint |  | hotDeckDischargeEnthalpy(\d{0,4})Sp | Yes | Yes | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | hotDeck,discharge,air,enthalpy,effective,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeFlowDb | hotDeckDischargeFlowXXXXDb | Hot Deck Discharge Flow Deadband | Hot Deck Discharge Flow XX Deadband |  | hotDeckDischargeFlow(\d{0,4})Db | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | hotDeck,discharge,air,flow,deadband,sp | AHU,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeHumidMaxSp | hotDeckDischargeHumidXXXXMaxSp | Hot Deck Discharge Humidification Max Setpoint | Hot Deck Discharge Humidification XX Max Setpoint |  | hotDeckDischargeHumid(\d{0,4})MaxSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | hotDeck,discharge,air,humid,max,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeHumidMinSp | hotDeckDischargeHumidXXXXMinSp | Hot Deck Discharge Humidification Min Setpoint | Hot Deck Discharge Humidification XX Min Setpoint |  | hotDeckDischargeHumid(\d{0,4})MinSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | hotDeck,discharge,air,humid,min,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeHumidSp | hotDeckDischargeHumidXXXXSp | Hot Deck Discharge Humidification Setpoint | Hot Deck Discharge Humidification XX Setpoint |  | hotDeckDischargeHumid(\d{0,4})Sp | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | hotDeck,discharge,air,humid,effective,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeHumidity | hotDeckDischargeHumidityXXXX | Hot Deck Discharge Humidity | Hot Deck Discharge Humidity XX |  | hotDeckDischargeHumidity(\d{0,4}) | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | hotDeck,discharge,air,humidity,sensor | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeHumidityDb | hotDeckDischargeHumidityXXXXDb | Hot Deck Discharge Humidity Deadband | Hot Deck Discharge Humidity XX Deadband |  | hotDeckDischargeHumidity(\d{0,4})Db | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | hotDeck,discharge,air,humidity,deadband,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeHumidityHiSp | hotDeckDischargeHumidityXXXXHiSp | Hot Deck Discharge Humidity High Setpoint | Hot Deck Discharge Humidity XX High Setpoint |  | hotDeckDischargeHumidity(\d{0,4})HiSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | hotDeck,discharge,air,humidity,high,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeHumidityLoSp | hotDeckDischargeHumidityXXXXLoSp | Hot Deck Discharge Humidity Low Setpoint | Hot Deck Discharge Humidity XX Low Setpoint |  | hotDeckDischargeHumidity(\d{0,4})LoSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | hotDeck,discharge,air,humidity,low,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeHumidityMaxSp | hotDeckDischargeHumidityXXXXMaxSp | Hot Deck Discharge Humidity Max Reset Setpoint | Hot Deck Discharge Humidity XX Max Reset Setpoint |  | hotDeckDischargeHumidity(\d{0,4})MaxSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | hotDeck,discharge,air,humidity,max,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeHumidityMinSp | hotDeckDischargeHumidityXXXXMinSp | Hot Deck Discharge Humidity Min Reset Setpoint | Hot Deck Discharge Humidity XX Min Reset Setpoint |  | hotDeckDischargeHumidity(\d{0,4})MinSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | hotDeck,discharge,air,humidity,min,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeHumiditySp | hotDeckDischargeHumidityXXXXSp | Hot Deck Discharge Humidity Setpoint | Hot Deck Discharge Humidity XX Setpoint |  | hotDeckDischargeHumidity(\d{0,4})Sp | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | hotDeck,discharge,air,humidity,effective,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargePressure | hotDeckDischargePressureXXXX | Hot Deck Discharge Pressure | Hot Deck Discharge Pressure XX |  | hotDeckDischargePressure(\d{0,4}) | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | hotDeck,discharge,air,static,pressure,sensor | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargePressureDb | hotDeckDischargePressureXXXXDb | Hot Deck Discharge Pressure Deadband | Hot Deck Discharge Pressure XX Deadband |  | hotDeckDischargePressure(\d{0,4})Db | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | hotDeck,discharge,air,static,pressure,deadband,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargePressureHiAlarm | hotDeckDischargePressureXXXXHiAlarm | Hot Deck Discharge Pressure High Alarm | Hot Deck Discharge Pressure XX High Alarm |  | hotDeckDischargePressure(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | hotDeck,discharge,air,static,pressure,high,alarm | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargePressureHiSp | hotDeckDischargePressureXXXXHiSp | Hot Deck Discharge Pressure High Setpoint | Hot Deck Discharge Pressure XX High Setpoint |  | hotDeckDischargePressure(\d{0,4})HiSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | hotDeck,discharge,air,static,pressure,high,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargePressureLoAlarm | hotDeckDischargePressureXXXXLoAlarm | Hot Deck Discharge Pressure Low Alarm | Hot Deck Discharge Pressure XX Low Alarm |  | hotDeckDischargePressure(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | hotDeck,discharge,air,static,pressure,low,alarm | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargePressureLoSp | hotDeckDischargePressureXXXXLoSp | Hot Deck Discharge Pressure Low Setpoint | Hot Deck Discharge Pressure XX Low Setpoint |  | hotDeckDischargePressure(\d{0,4})LoSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | hotDeck,discharge,air,static,pressure,low,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargePressureMaxSp | hotDeckDischargePressureXXXXMaxSp | Hot Deck Discharge Pressure Max Reset Setpoint | Hot Deck Discharge Pressure XX Max Reset Setpoint |  | hotDeckDischargePressure(\d{0,4})MaxSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | hotDeck,discharge,air,static,pressure,max,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargePressureMinSp | hotDeckDischargePressureXXXXMinSp | Hot Deck Discharge Pressure Min Reset Setpoint | Hot Deck Discharge Pressure XX Min Reset Setpoint |  | hotDeckDischargePressure(\d{0,4})MinSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | hotDeck,discharge,air,static,pressure,min,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargePressureSp | hotDeckDischargePressureXXXXSp | Hot Deck Discharge Pressure Setpoint | Hot Deck Discharge Pressure XX Setpoint |  | hotDeckDischargePressure(\d{0,4})Sp | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | hotDeck,discharge,air,static,pressure,effective,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeTemp | hotDeckDischargeTempXXXX | Hot Deck Discharge Temperature | Hot Deck Discharge Temperature XX |  | hotDeckDischargeTemp(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | hotDeck,discharge,air,temp,sensor | AFMS,AHU,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeTempDb | hotDeckDischargeTempXXXXDb | Hot Deck Discharge Temperature Deadband | Hot Deck Discharge Temperature XX Deadband |  | hotDeckDischargeTemp(\d{0,4})Db | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | hotDeck,discharge,air,temp,deadband,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeTempHiSp | hotDeckDischargeTempXXXXHiSp | Hot Deck Discharge Temperature High Setpoint | Hot Deck Discharge Temperature XX High Setpoint |  | hotDeckDischargeTemp(\d{0,4})HiSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | hotDeck,discharge,air,temp,high,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeTempLoSp | hotDeckDischargeTempXXXXLoSp | Hot Deck Discharge Temperature Low Setpoint | Hot Deck Discharge Temperature XX Low Setpoint |  | hotDeckDischargeTemp(\d{0,4})LoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | hotDeck,discharge,air,temp,low,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeTempMaxSp | hotDeckDischargeTempXXXXMaxSp | Hot Deck Discharge Temperature Max Setpoint | Hot Deck Discharge Temperature XX Max Setpoint |  | hotDeckDischargeTemp(\d{0,4})MaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | hotDeck,discharge,air,temp,max,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeTempMinSp | hotDeckDischargeTempXXXXMinSp | Hot Deck Discharge Temperature Min Setpoint | Hot Deck Discharge Temperature XX Min Setpoint |  | hotDeckDischargeTemp(\d{0,4})MinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | hotDeck,discharge,air,temp,min,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeTempSp | hotDeckDischargeTempXXXXSp | Hot Deck Discharge Temperature Setpoint | Hot Deck Discharge Temperature XX Setpoint |  | hotDeckDischargeTemp(\d{0,4})Sp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | hotDeck,discharge,air,temp,effective,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckDischargeTempSpOvr | hotDeckDischargeTempXXXXSpOvr | Hot Deck Discharge Temperature Setpoint Override | Hot Deck Discharge Temperature XX Setpoint Override |  | hotDeckDischargeTemp(\d{0,4})SpOvr | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | hotDeck,discharge,air,temp,effective,spOvr | AHU | 2.12,2.13,2.14,2.15 (Released)
hotDeckFanAlarm | hotDeckFanXXXXAlarm | Hot Deck Fan Alarm | Hot Deck Fan XX Alarm |  | hotDeckFan(\w{0,4}(?=[A-Z]¦$))Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | hotDeck,air,fan,general,common,alarm | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckFanAlarmReset | hotDeckFanXXXXAlarmReset | Hot Deck Fan Alarm Reset | Hot Deck Fan XX Alarm Reset |  | hotDeckFan(\w{0,4}(?=[A-Z]¦$))AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | hotDeck,air,fan,common,reset,alarm | AHU | 2.15 (Released),2.16 (Pre-Release)
hotDeckFan | hotDeckFanXXXX | Hot Deck Fan Command | Hot Deck Fan XX Command |  | hotDeckFan((?:(?!Ovr)\w){0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | hotDeck,air,fan,status,cmd | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckFanCurrent | hotDeckFanXXXXCurrent | Hot Deck Fan Current | Hot Deck Fan XX Current |  | hotDeckFan(\w{0,4}(?=[A-Z]¦$))Current | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | hotDeck,air,fan,current,sensor | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckFanEnteringPressure | hotDeckFanXXXXEnteringPressure | Hot Deck Fan Entering Pressure | Hot Deck Fan XX Entering Pressure |  | hotDeckFan(\w{0,4}(?=[A-Z]¦$))EnteringPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | hotDeck,air,fan,entering,pressure,sensor | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckFanFault | hotDeckFanXXXXFault | Hot Deck Fan Fault | Hot Deck Fan XX Fault |  | hotDeckFan(\w{0,4}(?=[A-Z]¦$))Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | hotDeck,air,fan,fault | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckFanFilterAlarm | hotDeckFanXXXXFilterAlarm | Hot Deck Fan Filter Alarm | Hot Deck Fan XX Filter Alarm |  | hotDeckFan(\w{0,4}(?=[A-Z]¦$))FilterAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | hotDeck,air,fan,filter,common,alarm | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckFanFilterAlarmReset | hotDeckFanXXXXFilterAlarmReset | Hot Deck Fan Filter Alarm Reset | Hot Deck Fan XX Filter Alarm Reset |  | hotDeckFan(\w{0,4}(?=[A-Z]¦$))FilterAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | hotDeck,air,fan,filter,reset,alarm | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckFanFilterPressureDelta | hotDeckFanXXXXFilterPressureDelta | Hot Deck Fan Filter Pressure Delta | Hot Deck Fan XX Filter Pressure Delta |  | hotDeckFan(\w{0,4}(?=[A-Z]¦$))FilterPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | hotDeck,air,fan,filter,pressure,delta,sensor | AHU | 2.12,2.13,2.14,2.15 (Released)
hotDeckFanFilterRuntime | hotDeckFanXXXXFilterRuntime | Hot Deck Fan Filter Runtime | Hot Deck Fan XX Filter Runtime |  | hotDeckFan(\w{0,4}(?=[A-Z]¦$))FilterRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU | 2.15 (Released),2.16 (Pre-Release)
hotDeckFanLeavingPressure | hotDeckFanXXXXLeavingPressure | Hot Deck Fan Leaving Pressure | Hot Deck Fan XX Leaving Pressure |  | hotDeckFan(\w{0,4}(?=[A-Z]¦$))LeavingPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | hotDeck,air,fan,leaving,pressure,sensor | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckFanMaintSwitch | hotDeckFanXXXXMaintSwitch | Hot Deck Fan Maintenance Switch | Hot Deck Fan XX Maintenance Switch |  | hotDeckFan(\w{0,4}(?=[A-Z]¦$))MaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | hotDeck,air,fan,maintenance,switch,cmd | AHU | 2.15 (Released),2.16 (Pre-Release)
hotDeckFanOvr | hotDeckFanXXXXOvr | Hot Deck Fan Override | Hot Deck Fan XX Override |  | hotDeckFan(\w{0,4}(?=[A-Z]¦$))Ovr | No | No | No | Bool | On/Off | On/Off | [6 empty] | hotDeck,air,fan,status,ovr | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckFanPressureDelta | hotDeckFanXXXXPressureDelta | Hot Deck Fan Pressure Delta | Hot Deck Fan XX Pressure Delta |  | hotDeckFan(\w{0,4}(?=[A-Z]¦$))PressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | hotDeck,air,fan,common,pressure,delta,sensor | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckFanPressureHiAlarm | hotDeckFanXXXXPressureHiAlarm | Hot Deck Fan Pressure High Alarm | Hot Deck Fan XX Pressure High Alarm |  | hotDeckFan(\w{0,4}(?=[A-Z]¦$))PressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | hotDeck,air,fan,pressure,high,alarm | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckFanPressureHiSp | hotDeckFanXXXXPressureHiSp | Hot Deck Fan Pressure High Setpoint | Hot Deck Fan XX Pressure High Setpoint |  | hotDeckFan(\w{0,4}(?=[A-Z]¦$))PressureHiSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | hotDeck,air,fan,pressure,high,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckFanPressureLoAlarm | hotDeckFanXXXXPressureLoAlarm | Hot Deck Fan Pressure Low Alarm | Hot Deck Fan XX Pressure Low Alarm |  | hotDeckFan(\w{0,4}(?=[A-Z]¦$))PressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | hotDeck,air,fan,pressure,low,alarm | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckFanPressureLoSp | hotDeckFanXXXXPressureLoSp | Hot Deck Fan Pressure Low Setpoint | Hot Deck Fan XX Pressure Low Setpoint |  | hotDeckFan(\w{0,4}(?=[A-Z]¦$))PressureLoSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | hotDeck,air,fan,pressure,low,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckFanRuntime | hotDeckFanXXXXRuntime | Hot Deck Fan Runtime | Hot Deck Fan XX Runtime |  | hotDeckFan(\w{0,4}(?=[A-Z]¦$))Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU | 2.15 (Released),2.16 (Pre-Release)
hotDeckFanSpeed | hotDeckFanXXXXSpeed | Hot Deck Fan Speed | Hot Deck Fan XX Speed |  | hotDeckFan(\w{0,4}(?=[A-Z]¦$))Speed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | hotDeck,air,fan,speed,cmd | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckFanSpeedFb | hotDeckFanXXXXSpeedFb | Hot Deck Fan Speed Feedback | Hot Deck Fan XX Speed Feedback |  | hotDeckFan(\w{0,4}(?=[A-Z]¦$))SpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | hotDeck,air,fan,speed,sensor | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckFanSpeedMaxSp | hotDeckFanXXXXSpeedMaxSp | Hot Deck Fan Speed Max Setpoint | Hot Deck Fan XX Speed Max Setpoint |  | hotDeckFan(\w{0,4}(?=[A-Z]¦$))SpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | hotDeck,air,fan,speed,max,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckFanSpeedMinSp | hotDeckFanXXXXSpeedMinSp | Hot Deck Fan Speed Min Setpoint | Hot Deck Fan XX Speed Min Setpoint |  | hotDeckFan(\w{0,4}(?=[A-Z]¦$))SpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | hotDeck,air,fan,speed,min,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckFanSpeedOvr | hotDeckFanXXXXSpeedOvr | Hot Deck Fan Speed Override | Hot Deck Fan XX Speed Override |  | hotDeckFan(\w{0,4}(?=[A-Z]¦$))SpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | hotDeck,air,fan,speed,ovr | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckFanSpeedSp | hotDeckFanXXXXSpeedSp | Hot Deck Fan Speed Setpoint | Hot Deck Fan XX Speed Setpoint |  | hotDeckFan(\w{0,4}(?=[A-Z]¦$))SpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | hotDeck,air,fan,speed,effective,sp | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotDeckFanStatus | hotDeckFanXXXXStatus | Hot Deck Fan Status | Hot Deck Fan XX Status |  | hotDeckFan(\w{0,4}(?=[A-Z]¦$))Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | hotDeck,air,fan,status,sensor | AHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotGasBypassValve | hotGasBypassValveXXXX | Hot Gas Bypass Valve Command | Hot Gas Bypass Valve XX Command |  | hotGasBypassValve(\d{0,4}) | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | hotGas,bypass,valve,position,cmd | AHU,DHU,MAU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hotGasBypassValveFb | hotGasBypassValveXXXXFb | Hot Gas Bypass Valve Feedback | Hot Gas Bypass Valve XX Feedback |  | hotGasBypassValve(\d{0,4})Fb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | hotGas,bypass,valve,position,sensor | AHU,DHU,MAU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierValveOneThird | humidifierValveOneThird | Humidifier 1/3 Valve Command | Humidifier 1/3 Valve Command |  | humidifierValveOneThird | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | humidifier,valve,position,oneThird,cmd | AHU,CRAC,CRAH,DHU,DOAS,HP,HUM,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierValveOneThirdFb | humidifierValveOneThirdFb | Humidifier 1/3 Valve Feedback | Humidifier 1/3 Valve Feedback |  | humidifierValveOneThirdFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | humidifier,valve,position,oneThird,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,HUM,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierValveOneThirdOvr | humidifierValveOneThirdOvr | Humidifier 1/3 Valve Override | Humidifier 1/3 Valve Override |  | humidifierValveOneThirdOvr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | humidifier,valve,position,oneThird,ovr | AHU,CRAC,CRAH,DHU,DOAS,HP,HUM,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierValveTwoThird | humidifierValveTwoThird | Humidifier 2/3 Valve Command | Humidifier 2/3 Valve Command |  | humidifierValveTwoThird | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | humidifier,valve,position,twoThird,cmd | AHU,CRAC,CRAH,DHU,DOAS,HP,HUM,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierValveTwoThirdFb | humidifierValveTwoThirdFb | Humidifier 2/3 Valve Feedback | Humidifier 2/3 Valve Feedback |  | humidifierValveTwoThirdFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | humidifier,valve,position,twoThird,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,HUM,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierValveTwoThirdOvr | humidifierValveTwoThirdOvr | Humidifier 2/3 Valve Override | Humidifier 2/3 Valve Override |  | humidifierValveTwoThirdOvr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | humidifier,valve,position,twoThird,ovr | AHU,CRAC,CRAH,DHU,DOAS,HP,HUM,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierAlarm | humidifierXXXXAlarm | Humidifier Alarm | Humidifier XX Alarm |  | humidifier(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | humidifier,general,common,alarm | AHU,CRAC,CRAH,DHU,DOAS,FPB,HP,HUM,MAU,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierCapacity | humidifierXXXXCapacity | Humidifier Capacity | Humidifier XX Capacity |  | humidifier(\d{0,4})Capacity | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | humidifier,demand,sensor | AHU,CRAC,CRAH,DHU,DOAS,FPB,HP,HUM,MAU,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierCapacityMaxSp | humidifierXXXXCapacityMaxSp | Humidifier Capacity Max Setpoint | Humidifier XX Capacity Max Setpoint |  | humidifier(\d{0,4})CapacityMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | humidifier,demand,max,sp | AHU,CRAC,CRAH,DHU,DOAS,FPB,HP,HUM,MAU,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifier | humidifierXXXX | Humidifier Command | Humidifier XX Command |  | humidifier(\d{0,4}) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | humidifier,general,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,FPB,HP,HUM,MAU,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierCurrent | humidifierXXXXCurrent | Humidifier Current | Humidifier XX Current |  | humidifier(\d{0,4})Current | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  |  | humidifier,current,sensor | AHU,CRAC,CRAH,DHU,DOAS,FPB,HP,HUM,MAU,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierCurrentHiAlarm | humidifierXXXXCurrentHiAlarm | Humidifier Current High Alarm | Humidifier XX Current High Alarm |  | humidifier(\d{0,4})CurrentHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | humidifier,current,high,alarm | AHU,CRAC,CRAH,DHU,DOAS,FPB,HP,HUM,MAU,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierCurrentLoAlarm | humidifierXXXXCurrentLoAlarm | Humidifier Current Low Alarm | Humidifier XX Current Low Alarm |  | humidifier(\d{0,4})CurrentLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | humidifier,current,low,alarm | AHU,CRAC,CRAH,DHU,DOAS,FPB,HP,HUM,MAU,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierDemand | humidifierXXXXDemand | Humidifier Demand | Humidifier XX Demand |  | humidifier(\d{0,4})Demand | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | humidifier,load,sp | AHU,CRAC,CRAH,DHU,DOAS,FPB,HP,HUM,MAU,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierEnable | humidifierXXXXEnable | Humidifier Enable Command | Humidifier XX Enable Command |  | humidifier(\d{0,4})Enable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | humidifier,enable,common,cmd | AHU,CRAC,CRAH,DHU,DOAS,FPB,HP,HUM,MAU,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierEnableDb | humidifierXXXXEnableDb | Humidifier Enable Deadband | Humidifier XX Enable Deadband |  | humidifier(\d{0,4})EnableDb | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | humidifier,enable,deadband,sp | AHU,CRAC,CRAH,DHU,DOAS,FPB,HP,HUM,MAU,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierEnableSp | humidifierXXXXEnableSp | Humidifier Enable Setpoint | Humidifier XX Enable Setpoint |  | humidifier(\d{0,4})EnableSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | humidifier,enable,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,FPB,HP,HUM,MAU,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierEnteringIsoValve | humidifierEnteringIsoValve | Humidifier Entering Isolation Valve Command | Humidifier Entering Isolation Valve Command |  | humidifierEnteringIsoValve | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | humidifier,entering,iso,valve,postition,cmd | AHU,CRAC,CRAH,DHU,DOAS,FPB,HP,HUM,MAU,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierEnteringIsoValveFb | humidifierEnteringIsoValveFb | Humidifier Entering Isolation Valve Feedback | Humidifier Entering Isolation Valve Feedback |  | humidifierEnteringIsoValveFb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | humidifier,entering,iso,valve,postition,sensor | AHU,CRAC,CRAH,DHU,DOAS,FPB,HP,HUM,MAU,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierEnteringIsoValveOvr | humidifierEnteringIsoValveOvr | Humidifier Entering Isolation Valve Override | Humidifier Entering Isolation Valve Override |  | humidifierEnteringIsoValveOvr | No | No | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | humidifier,entering,iso,valve,postition,ovr | AHU,CRAC,CRAH,DHU,DOAS,FPB,HP,HUM,MAU,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierFault | humidifierXXXXFault | Humidifier Fault | Humidifier XX Fault |  | humidifier(\d{0,4})Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | humidifier,fault | AHU,CRAC,CRAH,DHU,DOAS,FPB,HP,HUM,MAU,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierFilterAlarm | humidifierXXXXFilterAlarm | Humidifier Filter Alarm | Humidifier XX Filter Alarm |  | humidifier(\d{0,4})FilterAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | humidifier,filter,common,alarm | AHU,CRAC,CRAH,DHU,DOAS,FPB,HP,HUM,MAU,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierFilterAlarmReset | humidifierXXXXFilterAlarmReset | Humidifier Filter Alarm Reset | Humidifier XX Filter Alarm Reset |  | humidifier(\d{0,4})FilterAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | humidifier,filter,reset,alarm | AHU,CRAC,CRAH,DHU,DOAS,HP,HUM,MAU,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierFilterPressureDelta | humidifierXXXXFilterPressureDelta | Humidifier Filter Pressure Delta | Humidifier XX Filter Pressure Delta |  | humidifier(\d{0,4})FilterPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | humidifier,filter,pressure,delta,sensor | AHU,CRAC,CRAH,DHU,DOAS,FPB,HP,HUM,MAU,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released)
humidifierFilterRuntime | humidifierXXXXFilterRuntime | Humidifier Filter Runtime | Humidifier XX Filter Runtime |  | humidifier(\d{0,4})FilterRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,FPB,HP,HUM,MAU,RTU,VAV,HP | 2.15 (Released),2.16 (Pre-Release)
humidifierLeavingIsoValve | humidifierLeavingIsoValve | Humidifier Leaving Isolation Valve Command | Humidifier Leaving Isolation Valve Command |  | humidifierLeavingIsoValve | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | humidifier,leaving,iso,valve,postition,cmd | AHU,CRAC,CRAH,DHU,DOAS,FPB,HP,HUM,MAU,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierLeavingIsoValveFb | humidifierLeavingIsoValveFb | Humidifier Leaving Isolation Valve Feedback | Humidifier Leaving Isolation Valve Feedback |  | humidifierLeavingIsoValveFb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | humidifier,leaving,iso,valve,postition,sensor | AHU,CRAC,CRAH,DHU,DOAS,FPB,HP,HUM,MAU,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierLeavingIsoValveOvr | humidifierLeavingIsoValveOvr | Humidifier Leaving Isolation Valve Override | Humidifier Leaving Isolation Valve Override |  | humidifierLeavingIsoValveOvr | No | No | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | humidifier,leaving,iso,valve,postition,ovr | AHU,CRAC,CRAH,DHU,DOAS,FPB,HP,HUM,MAU,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierPumpAlarm | humidifierPumpXXXXAlarm | Humidifier Pump Alarm | Humidifier Pump XX Alarm |  | humidifierPump(\w{0,4}(?=[A-Z]¦$))Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | humidifier,water,pump,common,alarm | AHU,CRAC,CRAH,DHU,DOAS,FPB,HP,HUM,MAU,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierPumpAlarmReset | humidifierPumpXXXXAlarmReset | Humidifier Pump Alarm Reset | Humidifier Pump Alarm Reset |  | humidifierPump(\w{0,4}(?=[A-Z]¦$))AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | humidifier,water,pump,reset,alarm | AHU,CRAC,CRAH,DHU,DOAS,HP,HUM,MAU,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierPump | humidifierPumpXXXX | Humidifier Pump Command | Humidifier Pump XX Command |  | humidifierPump(\w{0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | humidifier,water,pump,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,FPB,HP,HUM,MAU,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierPumpStatus | humidifierPumpXXXXStatus | Humidifier Pump Status | Humidifier Pump XX Status |  | humidifierPump(\w{0,4}(?=[A-Z]¦$))Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | humidifier,water,pump,status,sensor | AHU,CRAC,CRAH,DHU,DOAS,FPB,HP,HUM,MAU,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierRuntime | humidifierXXXXRuntime | Humidifier Runtime | Humidifier XX Runtime |  | humidifier(\d{0,4})Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,HP,HUM,MAU,RTU,HP | 2.15 (Released),2.16 (Pre-Release)
humidifierStatus | humidifierXXXXStatus | Humidifier Status | Humidifier XX Status |  | humidifier(\d{0,4})Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | humidifier,general,status,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,HUM,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierStrainerAlarm | humidifierXXXXStrainerAlarm | Humidifier Strainer Alarm | Humidifier XX Strainer Alarm |  | humidifier(\d{0,4})StrainerAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | humidifier,water,strainer,alarm | AHU,CRAC,CRAH,DHU,DOAS,HP,HUM,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierStrainerEnable | humidifierXXXXStrainerEnable | Humidifier Strainer Enable | Humidifier XX Strainer Enable |  | humidifier(\d{0,4})StrainerEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | humidifier,water,strainer,enable,cmd | AHU,CRAC,CRAH,DHU,DOAS,HP,HUM,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierValve | humidifierValveXXXX | Humidifier Valve Command | Humidifier Valve XX Command |  | humidifierValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 | XX |  | humidifier,valve,position,cmd | AHU,CRAC,CRAH,DHU,DOAS,HP,HUM,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierValveFb | humidifierValveXXXXFb | Humidifier Valve Feedback | Humidifier Valve XX Feedback |  | humidifierValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 | XX |  | humidifier,valve,position,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,HUM,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
humidifierValveOvr | humidifierValveXXXXOvr | Humidifier Valve Override | Humidifier Valve XX Override |  | humidifierValve(\d{0,4})Ovr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 | XX |  | humidifier,valve,position,ovr | AHU,CRAC,CRAH,DHU,DOAS,HP,HUM,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
hvacMode | hvacMode | HVAC Mode | HVAC Mode |  | hvacMode | Yes | No | No | Str | Cooling/Heating | Firing/Cooling/Economizing/Heating | [6 empty] | hvacMode,mode,common,sp | AC,AHU,ATU,BLR,CLR,CMP,CRAC,CRAH,CUH,CWS,DAC,DCWS,DH,DHU,DHWS,DOAS,DRY,EC,EF,ERU,FCU,FPB,GEN,GEO,HP,HRU,HUM,HVHS,HVLS,HWS,MAU,PH,PIU,RP,RPC,RPF,RTU,SMEX,SMP,SMS,TWR,UV,VAV,WS,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
hvacModeBAS | hvacModeBAS | HVAC Mode BAS | HVAC Mode BAS |  | hvacModeBAS | No | No | No | Str | Cooling/Heating | Firing/Cooling/Economizing/Heating | [6 empty] | hvacMode,mode,bas,sp | AC,AHU,ATU,BLR,CLR,CMP,CRAC,CRAH,CUH,CWS,DAC,DCWS,DH,DHU,DHWS,DOAS,DRY,EC,EF,ERU,FCU,FPB,GEN,GEO,HP,HRU,HUM,HVHS,HVLS,HWS,MAU,PH,PIU,RP,RPC,RPF,RTU,SMEX,SMP,SMS,TWR,UV,VAV,WS,FCU,HP,HX | 2.14,2.15 (Released),2.16 (Pre-Release)
hvacModeOvr | hvacModeOvr | HVAC Mode Override | HVAC Mode Override |  | hvacModeOvr | No | No | No | Str | Cooling/Heating | Firing/Cooling/Economizing/Heating | [6 empty] | hvacMode,mode,ovr | AC,AHU,ATU,BLR,CLR,CMP,CRAC,CRAH,CUH,CWS,DAC,DCWS,DH,DHU,DHWS,DOAS,DRY,EC,EF,ERU,FCU,FPB,GEN,GEO,HP,HRU,HUM,HVHS,HVLS,HWS,MAU,PH,PIU,RP,RPC,RPF,RTU,SMEX,SMP,SMS,TWR,UV,VAV,WS,FCU,HP,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
powerInductive | powerInductive | Inductive Power (Average) | Inductive Power (Average) |  | powerInductive | Yes | Yes | No | Number |  |  | kilovolt_ampere_reactive | kilovolt_ampere_reactive | 1 | 1 |  | N | common,power,inductive,sensor | ATS,BRK,CU,INV,PDU,PFC,PM,PRLY,PV,RECT,RPP,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
powerInductivePhaseA | powerInductivePhaseA | Inductive Power (Phase A) | Inductive Power (Phase A) |  | powerInductivePhaseA | Yes | Yes | No | Number |  |  | kilovolt_ampere_reactive | kilovolt_ampere_reactive | 1 | 1 |  | A | common,power,inductive,sensor | ATS,BRK,CU,INV,PDU,PFC,PM,PRLY,PV,RECT,RPP,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
powerInductivePhaseB | powerInductivePhaseB | Inductive Power (Phase B) | Inductive Power (Phase B) |  | powerInductivePhaseB | Yes | Yes | No | Number |  |  | kilovolt_ampere_reactive | kilovolt_ampere_reactive | 1 | 1 |  | B | common,power,inductive,sensor | ATS,BRK,CU,INV,PDU,PFC,PM,PRLY,PV,RECT,RPP,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
powerInductivePhaseC | powerInductivePhaseC | Inductive Power (Phase C) | Inductive Power (Phase C) |  | powerInductivePhaseC | Yes | Yes | No | Number |  |  | kilovolt_ampere_reactive | kilovolt_ampere_reactive | 1 | 1 |  | C | common,power,inductive,sensor | ATS,BRK,CU,INV,PDU,PFC,PM,PRLY,PV,RECT,RPP,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inletTemp | inletTemp | Inlet Temperature | Inlet Temperature |  | inletTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | inlet,temp,sensor | BLR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inEnergyApparent | inXXXXEnergyApparent | Input Apparent Energy | Input XX Apparent Energy |  | in(\d{0,4})EnergyApparent | Yes | Yes | No | Number |  |  | kilovolt_ampere_hour | kilovolt_ampere_hour | 0 | 0 |  |  | input,apparent,energy,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inPowerApparent | inXXXXPowerApparent | Input Apparent Power | Input XX Apparent Power |  | in(\d{0,4})PowerApparent | Yes | Yes | No | Number |  |  | kilovolt_ampere | kilovolt_ampere | 1 | 1 |  | N | input,power,apparent,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inPowerApparentPhaseA | inXXXXPowerApparentPhaseA | Input Apparent Power (Phase A) | Input XX Apparent Power (Phase A) |  | in(\d{0,4})PowerApparentPhaseA | Yes | Yes | No | Number |  |  | kilovolt_ampere | kilovolt_ampere | 1 | 1 |  | A | input,power,apparent,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inPowerApparentPhaseB | inXXXXPowerApparentPhaseB | Input Apparent Power (Phase B) | Input XX Apparent Power (Phase B) |  | in(\d{0,4})PowerApparentPhaseB | Yes | Yes | No | Number |  |  | kilovolt_ampere | kilovolt_ampere | 1 | 1 |  | B | input,power,apparent,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inPowerApparentPhaseC | inXXXXPowerApparentPhaseC | Input Apparent Power (Phase C) | Input XX Apparent Power (Phase C) |  | in(\d{0,4})PowerApparentPhaseC | Yes | Yes | No | Number |  |  | kilovolt_ampere | kilovolt_ampere | 1 | 1 |  | C | input,power,apparent,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inBreakerStatus | inXXXXBreakerStatus | Input Breaker Status | Input XX Breaker Status |  | in(\d{0,4})BreakerStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | input,breaker,status,sensor | PDU,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inCurrent | inXXXXCurrent | Input Current (Average) | Input XX Current (Average) |  | in(\d{0,4})Current | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  |  | input,current,avg,calc | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inCurrentPhaseA | inXXXXCurrentPhaseA | Input Current (Phase A) | Input XX Current (Phase A) |  | in(\d{0,4})CurrentPhaseA | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | A | input,current,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inCurrentPhaseB | inXXXXCurrentPhaseB | Input Current (Phase B) | Input XX Current (Phase B) |  | in(\d{0,4})CurrentPhaseB | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | B | input,current,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inCurrentPhaseC | inXXXXCurrentPhaseC | Input Current (Phase C) | Input XX Current (Phase C) |  | in(\d{0,4})CurrentPhaseC | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | C | input,current,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inCurrentPhaseN | inXXXXCurrentPhaseN | Input Current (Phase N) | Input XX Current (Phase N) |  | in(\d{0,4})CurrentPhaseN | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | input,current,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inEnergy | inXXXXEnergy | Input Energy | Input XX Energy |  | in(\d{0,4})Energy | Yes | Yes | No | Number |  |  | kilowatt_hour | kilowatt_hour | 0 | 0 |  |  | input,common,energy,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inFrequency | inXXXXFrequency | Input Frequency | Input XX Frequency |  | in(\d{0,4})Frequency | Yes | Yes | No | Number |  |  | hertz | hertz | 1 | 1 |  | N | input,freq,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inFrequencyPhaseA | inXXXXFrequencyPhaseA | Input Frequency (Phase A) | Input XX Frequency (Phase A) |  | in(\d{0,4})FrequencyPhaseA | Yes | Yes | No | Number |  |  | hertz | hertz | 1 | 1 |  | A | input,freq,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inFrequencyPhaseB | inXXXXFrequencyPhaseB | Input Frequency (Phase B) | Input XX Frequency (Phase B) |  | in(\d{0,4})FrequencyPhaseB | Yes | Yes | No | Number |  |  | hertz | hertz | 1 | 1 |  | B | input,freq,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inFrequencyPhaseC | inXXXXFrequencyPhaseC | Input Frequency (Phase C) | Input XX Frequency (Phase C) |  | in(\d{0,4})FrequencyPhaseC | Yes | Yes | No | Number |  |  | hertz | hertz | 1 | 1 |  | C | input,freq,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inName | inXXXXName | Input Name | Input XX Name |  | in(\d{0,4})Name | No | No | No | Str | [8 empty] | input,alias,sp | MSC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inPowerAlarm | inXXXXPowerAlarm | Input Power Alarm | Input XX Power Alarm |  | in(\d{0,4})PowerAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | input,power,alarm | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inPowerFactor | inXXXXPowerFactor | Input Power Factor | Input XX Power Factor |  | in(\d{0,4})PowerFactor | Yes | Yes | No | Number |  |  | power_factor | power_factor | 2 | 2 |  | N | input,pf,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inPowerFactorPhaseA | inXXXXPowerFactorPhaseA | Input Power Factor (Phase A) | Input XX Power Factor (Phase A) |  | in(\d{0,4})PowerFactorPhaseA | Yes | Yes | No | Number |  |  | power_factor | power_factor | 2 | 2 |  | A | input,pf,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inPowerFactorPhaseB | inXXXXPowerFactorPhaseB | Input Power Factor (Phase B) | Input XX Power Factor (Phase B) |  | in(\d{0,4})PowerFactorPhaseB | Yes | Yes | No | Number |  |  | power_factor | power_factor | 2 | 2 |  | B | input,pf,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inPowerFactorPhaseC | inXXXXPowerFactorPhaseC | Input Power Factor (Phase C) | Input XX Power Factor (Phase C) |  | in(\d{0,4})PowerFactorPhaseC | Yes | Yes | No | Number |  |  | power_factor | power_factor | 2 | 2 |  | C | input,pf,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inEnergyReactive | inXXXXEnergyReactive | Input Reactive Energy | Input XX Reactive Energy |  | in(\d{0,4})EnergyReactive | Yes | Yes | No | Number |  |  | kilovolt_ampere_reactive_hour | kilovolt_ampere_reactive_hour | 0 | 0 |  |  | input,reactive,energy,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inPowerReactive | inXXXXPowerReactive | Input Reactive Power | Input XX Reactive Power |  | in(\d{0,4})PowerReactive | Yes | Yes | No | Number |  |  | kilovolt_ampere_reactive | kilovolt_ampere_reactive | 1 | 1 |  | N | input,power,reactive,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inPowerReactivePhaseA | inXXXXPowerReactivePhaseA | Input Reactive Power (Phase A) | Input XX Reactive Power (Phase A) |  | in(\d{0,4})PowerReactivePhaseA | Yes | Yes | No | Number |  |  | kilovolt_ampere_reactive | kilovolt_ampere_reactive | 1 | 1 |  | A | input,power,reactive,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inPowerReactivePhaseB | inXXXXPowerReactivePhaseB | Input Reactive Power (Phase B) | Input XX Reactive Power (Phase B) |  | in(\d{0,4})PowerReactivePhaseB | Yes | Yes | No | Number |  |  | kilovolt_ampere_reactive | kilovolt_ampere_reactive | 1 | 1 |  | B | input,power,reactive,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inPowerReactivePhaseC | inXXXXPowerReactivePhaseC | Input Reactive Power (Phase C) | Input XX Reactive Power (Phase C) |  | in(\d{0,4})PowerReactivePhaseC | Yes | Yes | No | Number |  |  | kilovolt_ampere_reactive | kilovolt_ampere_reactive | 1 | 1 |  | C | input,power,reactive,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inReadyToLoad | inXXXXReadyToLoad | Input Ready To Load | Input XX Ready To Load |  | in(\d{0,4})ReadyToLoad | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | input,ready,load,cmd | ATS,INV,PDU,PFC,RECT,RPP,STS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inPowerReal | inXXXXPowerReal | Input Real Power | Input XX Real Power |  | in(\d{0,4})PowerReal | Yes | Yes | No | Number |  |  | kilowatt | kilowatt | 1 | 1 |  | N | input,power,real,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inPowerRealPhaseA | inXXXXPowerRealPhaseA | Input Real Power (Phase A) | Input XX Real Power (Phase A) |  | in(\d{0,4})PowerRealPhaseA | Yes | Yes | No | Number |  |  | kilowatt | kilowatt | 1 | 1 |  | A | input,power,real,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inPowerRealPhaseB | inXXXXPowerRealPhaseB | Input Real Power (Phase B) | Input XX Real Power (Phase B) |  | in(\d{0,4})PowerRealPhaseB | Yes | Yes | No | Number |  |  | kilowatt | kilowatt | 1 | 1 |  | B | input,power,real,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inPowerRealPhaseC | inXXXXPowerRealPhaseC | Input Real Power (Phase C) | Input XX Real Power (Phase C) |  | in(\d{0,4})PowerRealPhaseC | Yes | Yes | No | Number |  |  | kilowatt | kilowatt | 1 | 1 |  | C | input,power,real,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inStatus | inStatus | Input Status | Input Status |  | inStatus | Yes | Yes | No | Bool | in01/in02 | in01/in02 | [6 empty] | input,common,status,sensor | ATS,INV,PDU,PFC,RECT,RPP,STS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inUnitMode | inXXXXUnitMode | Input Unit Mode | Input XX Unit Mode |  | in(\d{0,4})UnitMode | Yes | Yes | No | Str |  | Other/None/PrimaryUtility/BypassFeed/SecondaryUtility/Generator/Flywheel/Fuelcell | [6 empty] | input,unitMode,cmd | ATS,INV,PDU,PFC,RECT,RPP,STS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inVoltage | inXXXXVoltage | Input Voltage (Average) | Input XX Voltage (Average) |  | in(\d{0,4})Voltage | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  |  | input,volt,avg,calc | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inVoltageLL | inXXXXVoltageLL | Input Voltage Line-to-Line (Average) | Input XX Voltage Line-to-Line (Average) |  | in(\d{0,4})VoltageLL | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  | LL | input,volt,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inVoltagePhaseAB | inXXXXVoltagePhaseAB | Input Voltage Line-to-Line (Phase AB) | Input XX Voltage Line-to-Line (Phase AB) |  | in(\d{0,4})VoltagePhaseAB | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  | AB | input,volt,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inVoltagePhaseBC | inXXXXVoltagePhaseBC | Input Voltage Line-to-Line (Phase BC) | Input XX Voltage Line-to-Line (Phase BC) |  | in(\d{0,4})VoltagePhaseBC | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  | BC | input,volt,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inVoltagePhaseCA | inXXXXVoltagePhaseCA | Input Voltage Line-to-Line (Phase CA) | Input XX Voltage Line-to-Line (Phase CA) |  | in(\d{0,4})VoltagePhaseCA | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  | CA | input,volt,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inVoltageLN | inXXXXVoltageLN | Input Voltage Line-to-Neutral (Average) | Input XX Voltage Line-to-Neutral (Average) |  | in(\d{0,4})VoltageLN | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  | N | input,volt,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inVoltagePhaseAN | inXXXXVoltagePhaseAN | Input Voltage Line-to-Neutral (Phase A) | Input XX Voltage Line-to-Neutral (Phase A) |  | in(\d{0,4})VoltagePhaseAN | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  | A | input,volt,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inVoltagePhaseBN | inXXXXVoltagePhaseBN | Input Voltage Line-to-Neutral (Phase B) | Input XX Voltage Line-to-Neutral (Phase B) |  | in(\d{0,4})VoltagePhaseBN | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  | B | input,volt,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inVoltagePhaseCN | inXXXXVoltagePhaseCN | Input Voltage Line-to-Neutral (Phase C) | Input XX Voltage Line-to-Neutral (Phase C) |  | in(\d{0,4})VoltagePhaseCN | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  | C | input,volt,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
intakeDamper | intakeDamper | Intake Damper Command | Intake Damper Command |  | intakeDamper | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | intake,air,damper,position,cmd | INTK,MSC,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
intakeDamperFb | intakeDamperFb | Intake Damper Feedback | Intake Damper Feedback |  | intakeDamperFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | intake,air,damper,position,sensor | INTK,MSC,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
intakeDamperOvr | intakeDamperOvr | Intake Damper Override | Intake Damper Override |  | intakeDamperOvr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | intake,air,damper,position,ovr | INTK,MSC,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
intrusionAlarm | intrusionAlarm | Intrusion Alarm | Intrusion Alarm |  | intrusionAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | intrusion,alarm | GBL | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
intrusionArm | intrusionArm | Intrusion Arm | Intrusion Arm |  | intrusionArm | Yes | Yes | No | Bool | Arm/Disarm | Arm/Disarm | [6 empty] | intrusion,arm,cmd | SEC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
intrusionArmedOccupied | intrusionArmedOccupied | Intrusion Occupied Armed | Intrusion Occupied Armed |  | intrusionArmedOccupied | Yes | Yes | No | Bool | Armed/Disarmed | Armed/Disarmed | [6 empty] | intrusion,occupied,armed,cmd | SEC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
intrusionArmedUnoccupied | intrusionArmedUnoccupied | Intrusion Unoccupied Armed | Intrusion Unoccupied Armed |  | intrusionArmedUnoccupied | Yes | Yes | No | Bool | Armed/Disarmed | Armed/Disarmed | [6 empty] | intrusion,unoccupied,armed,cmd | SEC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inverterAlarm | inverterXXXXAlarm | Inverter Alarm | Inverter XX Alarm |  | inverter(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | inverter,alarm | INV,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inverter | inverterXXXX | Inverter Command | Inverter XX Command |  | inverter(\d{0,4}) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | inverter,status,cmd | INV,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
inverterStatus | inverterXXXXStatus | Inverter Status | Inverter XX Status |  | inverter(\d{0,4})Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | inverter,status,sensor | INV,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
ionFilterAlarm | ionFilterXXXXAlarm | Ion Filter Alarm | Ion Filter XX Alarm |  | ionFilter(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | ion,filter,common,alarm | ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
ionFilterAlarmReset | ionFilterXXXXAlarmReset | Ion Filter Alarm Reset | Ion Filter XX Alarm Reset |  | ionFilter(\d{0,4})AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | ion,filter,reset,alarm | ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
ionFilter | ionFilterXXXX | Ion Filter Command | Ion Filter XX Command |  | ionFilter(\d{0,4}) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | ion,filter,status,cmd | ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
ionFilterRuntime | ionFilterXXXXRuntime | Ion Filter Runtime | Ion Filter XX Runtime |  | ionFilter(\d{0,4})Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.15 (Released),2.16 (Pre-Release)
ionFilterStatus | ionFilterXXXXStatus | Ion Filter Status | Ion Filter XX Status |  | ionFilter(\d{0,4})Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | ion,filter,status,sensor | ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
jockeyPump | jockeyPumpXXXX | Jockey Pump | Jockey Pump XX |  | jockeyPump(\w{0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | jockey,water,pump,status,cmd | FP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
jockeyPumpAlarm | jockeyPumpXXXXAlarm | Jockey Pump Alarm | Jockey Pump XX Alarm |  | jockeyPump(\w{0,4}(?=[A-Z]¦$))Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | jockey,water,pump,common,alarm | FP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
jockeyPumpAlarmReset | jockeyPumpXXXXAlarmReset | Jockey Pump Alarm Reset | Jockey Pump XX Alarm Reset |  | jockeyPump(\w{0,4}(?=[A-Z]¦$))AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | jockey,water,pump,reset,alarm | FP,FSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
jockeyPumpFault | jockeyPumpXXXXFault | Jockey Pump Fault | Jockey Pump XX Fault |  | jockeyPump(\w{0,4}(?=[A-Z]¦$))Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | jockey,water,pump,fault | FP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
jockeyPumpHandMode | jockeyPumpXXXXHandMode | Jockey Pump Hand Mode | Jockey Pump XX Hand Mode |  | jockeyPump(\w{0,4}(?=[A-Z]¦$))HandMode | Yes | Yes | No | Bool | Hand/Auto | Hand/Auto | [6 empty] | jockey,water,pump,handMode,sensor | FP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
jockeyPumpRuntime | jockeyPumpXXXXRuntime | Jockey Pump Runtime | Jockey Pump XX Runtime |  | jockeyPump(\w{0,4}(?=[A-Z]¦$))Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | FP,FSS | 2.15 (Released),2.16 (Pre-Release)
jockeyPumpStarts | jockeyPumpXXXXStarts | Jockey Pump Starts | Jockey Pump XX Starts |  | jockeyPump(\w{0,4}(?=[A-Z]¦$))Starts | Yes | No | No | Number |  |  |  |  | 0 | 0 |  |  | jockey,water,pump,starts,common,sensor | FP,FSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
jockeyPumpStartsDay | jockeyPumpXXXXStartsDay | Jockey Pump Starts Day | Jockey Pump XX Starts Day |  | jockeyPump(\w{0,4}(?=[A-Z]¦$))StartsDay | Yes | No | No | Number |  |  |  |  | 0 | 0 |  |  | jockey,water,pump,starts,day,sensor | FP,FSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
jockeyPumpStartsDayHiSp | jockeyPumpXXXXStartsDayHiSp | Jockey Pump Starts Day High Setpoint | Jockey Pump XX Starts Day High Setpoint |  | jockeyPump(\w{0,4}(?=[A-Z]¦$))StartsDayHiSp | No | No | No | Number |  |  |  |  | 0 | 0 |  |  | jockey,water,pump,starts,day,high,sp | FP,FSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
jockeyPumpStartsHour | jockeyPumpXXXXStartsHour | Jockey Pump Starts Hour | Jockey Pump XX Starts Hour |  | jockeyPump(\w{0,4}(?=[A-Z]¦$))StartsHour | Yes | No | No | Number |  |  |  |  | 0 | 0 |  |  | jockey,water,pump,starts,hour,sensor | FP,FSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
jockeyPumpStartsHourHiSp | jockeyPumpXXXXStartsHourHiSp | Jockey Pump Starts Hour High Setpoint | Jockey Pump XX Starts Hour High Setpoint |  | jockeyPump(\w{0,4}(?=[A-Z]¦$))StartsHourHiSp | No | No | No | Number |  |  |  |  | 0 | 0 |  |  | jockey,water,pump,starts,hour,high,sp | FP,FSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
jockeyPumpStatus | jockeyPumpXXXXStatus | Jockey Pump Status | Jockey Pump XX Status |  | jockeyPump(\w{0,4}(?=[A-Z]¦$))Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | jockey,water,pump,status,sensor | FP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
liquidLineSolenoid | liquidLineSolenoidXXXX | Liquid Line Solenoid | Liquid Line Solenoid XX |  | liquidLineSolenoid(\d{0,4}) | Yes | Yes | No | Bool | Open/Closed | Open/Closed | [6 empty] | liquidLine,valve,position,cmd | RFG | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
loadEnteringTemp | loadEnteringTempXXXX | Load Entering Temperature | Load Entering Temperature XX |  | loadEnteringTemp(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | load,entering,temp,sensor | CLR,HP,HP,HX | 2.14,2.15 (Released),2.16 (Pre-Release)
loadFlowStatus | loadFlowXXXXStatus | Load Flow Status | Load Flow XX Status |  | loadFlow(\d{0,4})Status | Yes | Yes | No | Bool | Flow/No Flow | Flow/No Flow | [6 empty] | load,flow,status,sensor | CLR,HP,HP,HX | 2.14,2.15 (Released),2.16 (Pre-Release)
loadLeavingTemp | loadLeavingTempXXXX | Load Leaving Temperature | Load Leaving Temperature XX |  | loadLeavingTemp(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | load,leaving,temp,sensor | CLR,HP,HP,HX | 2.14,2.15 (Released),2.16 (Pre-Release)
loadShedding | loadShedding | Load Shedding | Load Shedding |  | loadShedding | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | loadShed,status,cmd | GBL | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
loadSheddingEnable | loadSheddingEnable | Load Shedding Enable | Load Shedding Enable |  | loadSheddingEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | loadShed,enable,cmd | GBL | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
loadSheddingSp | loadSheddingSp | Load Shedding Setpoint | Load Shedding Setpoint |  | loadSheddingSp | Yes | Yes | No | Number |  |  | kilowatt | kilowatt | 1 | 1 |  |  | loadShed,sp | GBL | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
lowLimitAlarm | lowLimitAlarm | Low Limit Thermostat | Low Limit Thermostat |  | lowLimitAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | common,low,limit,alarm | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,MAU,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
maintSwitch | maintSwitch | Maintenance Switch | Maintenance Switch |  | maintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | common,maintenance,switch,general,cmd | AC,AHU,ATS,ATU,BLR,CLR,CMP,CRAC,CRAH,CUH,CWS,DAC,DCWS,DH,DHU,DHWS,DOAS,DRY,EC,EF,ERU,FC,FCU,FPB,GEN,GEO,HP,HRU,HUM,HWS,MAU,PH,PIU,REC,RFG,RTU,SMEX,TWR,UH,UV,VAV,VRF,WH,WS,ZD,FCU,HP,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
makeupAlarm | makeupAlarmXXXX | Makeup Alarm | Makeup Alarm XX |  | makeupAlarm(\w{0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | makeup,water,general,common,alarm | CWS,HWS,ROS,TWR,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
makeupFlow | makeupFlowXXXX | Makeup Flow | Makeup Flow XX |  | makeupFlow(\w{0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | makeup,water,flow,sensor | CWS,HWS,ROS,TWR,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
makeupFlowTotalizer | makeupFlowTotalizer | Makeup Flow Totalizer | Makeup Flow Totalizer |  | makeupFlowTotalizer | Yes | Yes | Yes | Number |  |  | gallon | liter | 0 | 0 |  |  | makeup,water,flowConsumption,sensor | CWS,HWS,ROS,TWR,WS | 2.15 (Released),2.16 (Pre-Release)
makeupFlowTotalizerReset | makeupFlowTotalizerReset | Makeup Flow Totalizer Reset | Makeup Flow Totalizer Reset |  | makeupFlowTotalizerReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | makeup,water,flowConsumption,reset | CWS,HWS,ROS,TWR,WS | 2.15 (Released),2.16 (Pre-Release)
makeupPressure | makeupPressureXXXX | Makeup Pressure | Makeup Pressure XX |  | makeupPressure(\w{0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | makeup,water,pressure,common,sensor | CWS,HWS,ROS,TWR,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
makeupPumpAlarm | makeupPumpXXXXAlarm | Makeup Pump Alarm | Makeup Pump XX Alarm |  | makeupPump(\w{0,4}(?=[A-Z]¦$))Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | makeup,water,pump,common,alarm | CWS,HWS,ROS,TWR,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
makeupPumpAlarmReset | makeupPumpXXXXAlarmReset | Makeup Pump Alarm Reset | Makeup Pump XX Alarm Reset |  | makeupPump(\w{0,4}(?=[A-Z]¦$))AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | makeup,water,pump,reset,alarm | CWS,DCWS,DHWS,HWS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
makeupPump | makeupPumpXXXX | Makeup Pump Command | Makeup Pump XX Command |  | makeupPump((?:(?!Lead)(?!Ovr)\w){0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | makeup,water,pump,status,cmd | CWS,HWS,ROS,TWR,WS | 2.15 (Released),2.16 (Pre-Release)
makeupPumpCurrent | makeupPumpXXXXCurrent | Makeup Pump Current | Makeup Pump XX Current |  | makeupPump(\w{0,4}(?=[A-Z]¦$))Current | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | makeup,water,pump,current,sensor | CWS,HWS,ROS,TWR,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
makeupPumpEnable | makeupPumpXXXXEnable | Makeup Pump Enable | Makeup Pump XX Enable |  | makeupPump(\w{0,4}(?=[A-Z]¦$))Enable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | makeup,water,pump,enable,cmd | CWS,HWS,ROS,TWR,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
makeupPumpEnableDb | makeupPumpXXXXEnableDb | Makeup Pump Enable Deadband | Makeup Pump XX Enable Deadband |  | makeupPump(\w{0,4}(?=[A-Z]¦$))EnableDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | makeup,water,pump,enable,deadband,sp | CWS,HWS,ROS,TWR,WS | 2.15 (Released),2.16 (Pre-Release)
makeupPumpEnableSp | makeupPumpXXXXEnableSp | Makeup Pump Enable Setpoint | Makeup Pump XX Enable Setpoint |  | makeupPump((?:(?!Lag)\w){0,4}(?=[A-Z]¦$))EnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | makeup,water,pump,enable,effective,sp | CWS,HWS,ROS,TWR,WS | 2.15 (Released),2.16 (Pre-Release)
makeupPumpEnteringPressure | makeupPumpXXXXEnteringPressure | Makeup Pump Entering Pressure | Makeup Pump XX Entering Pressure |  | makeupPump(\w{0,4}(?=[A-Z]¦$))EnteringPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | makeup,water,pump,entering,pressure,sensor | CWS,HWS,ROS,TWR,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
makeupPumpFault | makeupPumpXXXXFault | Makeup Pump Fault | Makeup Pump XX Fault |  | makeupPump(\w{0,4}(?=[A-Z]¦$))Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | makeup,water,pump,fault | CWS,HWS,ROS,TWR,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
makeupPumpLagDisableSp | makeupPumpXXXXLagDisableSp | Makeup Pump Lag Disable Setpoint | Makeup Pump XX Lag Disable Setpoint |  | makeupPump(\w{0,4}(?=[A-Z]¦$))LagDisableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | makeup,water,pump,lag,disable,sp | CWS,HWS,ROS,TWR,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
makeupPumpLagEnableSp | makeupPumpXXXXLagEnableSp | Makeup Pump Lag Enable Setpoint | Makeup Pump XX Lag Enable Setpoint |  | makeupPump(\w{0,4}(?=[A-Z]¦$))LagEnableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | makeup,water,pump,lag,enable,sp | CWS,HWS,ROS,TWR,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
makeupPumpLagReq | makeupPumpXXXXLagReq | Makeup Pump Lag Request | Makeup Pump XX Lag Request |  | makeupPump(\w{0,4}(?=[A-Z]¦$))LagReq | No | No | No | Bool | Request/No Request | Request/No Request | [6 empty] | makeup,water,pump,lag,request,cmd | CWS,HWS,ROS,TWR,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
makeupPumpLead | makeupPumpLead | Makeup Pump Lead | Makeup Pump Lead |  | makeupPumpLead | Yes | Yes | No | Bool | Lead 1/Lead 2 | Lead 1/Lead 2 | [6 empty] | makeup,water,pump,lead,sp | CWS,HWS,ROS,TWR,WS | 2.15 (Released),2.16 (Pre-Release)
makeupPumpLeadXor | makeupPumpLeadXor | Makeup Pump Lead Change Over | Makeup Pump Lead Change Over |  | makeupPumpLeadXor | No | No | No | Bool | On/Off | On/Off | [6 empty] | makeup,water,pump,lead,changeOver,cmd | CWS,HWS,ROS,TWR,WS | 2.15 (Released),2.16 (Pre-Release)
makeupPumpLeadXorRuntimeSp | makeupPumpLeadXorRuntimeSp | Makeup Pump Lead Change Over Runtime Setpoint | Makeup Pump Lead Change Over Runtime Setpoint |  | makeupPumpLeadXorRuntimeSp | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | CWS,HWS,ROS,TWR,WS | 2.15 (Released),2.16 (Pre-Release)
makeupPumpLeavingPressure | makeupPumpXXXXLeavingPressure | Makeup Pump Leaving Pressure | Makeup Pump XX Leaving Pressure |  | makeupPump(\w{0,4}(?=[A-Z]¦$))LeavingPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | makeup,water,pump,leaving,pressure,sensor | CWS,HWS,ROS,TWR,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
makeupPumpMaintSwitch | makeupPumpXXXXMaintSwitch | Makeup Pump Maintenance Switch | Makeup Pump XX Maintenance Switch |  | makeupPump(\w{0,4}(?=[A-Z]¦$))MaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | makeup,water,pump,maintenance,switch,cmd | CWS,HWS,ROS,TWR,WS | 2.15 (Released),2.16 (Pre-Release)
makeupPumpOvr | makeupPumpXXXXOvr | Makeup Pump Override | Makeup Pump XX Override |  | makeupPump(\w{0,4}(?=[A-Z]¦$))Ovr | No | No | No | Bool | On/Off | On/Off | [6 empty] | makeup,water,pump,status,ovr | CWS,HWS,ROS,TWR,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
makeupPumpPressureDelta | makeupPumpXXXXPressureDelta | Makeup Pump Pressure Delta | Makeup Pump XX Pressure Delta |  | makeupPump(\w{0,4}(?=[A-Z]¦$))PressureDelta | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | makeup,water,pump,pressure,delta,sensor | CWS,HWS,ROS,TWR,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
makeupPumpPressureHiAlarm | makeupPumpXXXXPressureHiAlarm | Makeup Pump Pressure High Alarm | Makeup Pump XX Pressure High Alarm |  | makeupPump(\w{0,4}(?=[A-Z]¦$))PressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | makeup,water,pump,pressure,high,alarm | CWS,HWS,ROS,TWR,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
makeupPumpPressureHiSp | makeupPumpXXXXPressureHiSp | Makeup Pump Pressure High Setpoint | Makeup Pump XX Pressure High Setpoint |  | makeupPump(\w{0,4}(?=[A-Z]¦$))PressureHiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | makeup,water,pump,pressure,high,sp | CWS,HWS,ROS,TWR,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
makeupPumpPressureLoAlarm | makeupPumpXXXXPressureLoAlarm | Makeup Pump Pressure Low Alarm | Makeup Pump XX Pressure Low Alarm |  | makeupPump(\w{0,4}(?=[A-Z]¦$))PressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | makeup,water,pump,pressure,low,alarm | CWS,HWS,ROS,TWR,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
makeupPumpPressureLoSp | makeupPumpXXXXPressureLoSp | Makeup Pump Pressure Low Setpoint | Makeup Pump XX Pressure Low Setpoint |  | makeupPump(\w{0,4}(?=[A-Z]¦$))PressureLoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | makeup,water,pump,pressure,low,sp | CWS,HWS,ROS,TWR,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
makeupPumpRuntime | makeupPumpXXXXRuntime | Makeup Pump Runtime | Makeup Pump XX Runtime |  | makeupPump(\w{0,4}(?=[A-Z]¦$))Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | CWS,HWS,ROS,TWR,WS | 2.15 (Released),2.16 (Pre-Release)
makeupPumpSpeed | makeupPumpXXXXSpeed | Makeup Pump Speed | Makeup Pump XX Speed |  | makeupPump(\w{0,4}(?=[A-Z]¦$))Speed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | makeup,water,pump,speed,cmd | CWS,HWS,ROS,TWR,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
makeupPumpSpeedFb | makeupPumpXXXXSpeedFb | Makeup Pump Speed Feedback | Makeup Pump XX Speed Feedback |  | makeupPump(\w{0,4}(?=[A-Z]¦$))SpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | makeup,water,pump,speed,sensor | CWS,HWS,ROS,TWR,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
makeupPumpSpeedMaxSp | makeupPumpXXXXSpeedMaxSp | Makeup Pump Speed Max Setpoint | Makeup Pump XX Speed Max Setpoint |  | makeupPump(\w{0,4}(?=[A-Z]¦$))SpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | makeup,water,pump,speed,max,sp | CWS,HWS,ROS,TWR,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
makeupPumpSpeedMinSp | makeupPumpXXXXSpeedMinSp | Makeup Pump Speed Min Setpoint | Makeup Pump XX Speed Min Setpoint |  | makeupPump(\w{0,4}(?=[A-Z]¦$))SpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | makeup,water,pump,speed,min,sp | CWS,HWS,ROS,TWR,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
makeupPumpSpeedOvr | makeupPumpXXXXSpeedOvr | Makeup Pump Speed Override | Makeup Pump XX Speed Override |  | makeupPump(\w{0,4}(?=[A-Z]¦$))SpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | makeup,water,pump,speed,ovr | CWS,HWS,ROS,TWR,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
makeupPumpSpeedSp | makeupPumpXXXXSpeedSp | Makeup Pump Speed Setpoint | Makeup Pump XX Speed Setpoint |  | makeupPump(\w{0,4}(?=[A-Z]¦$))SpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | makeup,water,pump,speed,effective,sp | CWS,HWS,ROS,TWR,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
makeupPumpStatus | makeupPumpXXXXStatus | Makeup Pump Status | Makeup Pump XX Status |  | makeupPump(\w{0,4}(?=[A-Z]¦$))Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | makeup,water,pump,status,sensor | CWS,HWS,ROS,TWR,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
makeupValve | makeupValve | Makeup Water Valve Command | Makeup Water Valve Command |  | makeupValve | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | makeup,water,valve,status,cmd | ROS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
makeupValveFb | makeupValveFb | Makeup Water Valve Feedback | Makeup Water Valve Feedback |  | makeupValveFb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | makeup,water,valve,status,sensor | ROS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
massFlow | massFlowXXXX | Mass Flow | Mass Flow XX |  | massFlow(\d{0,4}) | Yes | Yes | No | Number |  |  | pounds_per_hour | kilograms_per_hour | 1 | 1 |  |  | mass,flowRate,sensor | BLR,CLR,CWS,GEO,GM,HWS,SM,SMS,TWR,VGM,VWM,WM,WS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
massTotalizer | massTotalizer | Mass Totalizer | Mass Totalizer |  | massTotalizer | Yes | Yes | Yes | Number |  |  | pound | kilogram | 0 | 0 |  |  | mass,flowConsumption,sensor | BLR,CLR,CWS,GEO,GM,HWS,SM,SMS,TWR,VGM,VWM,WM,WS,HX | 2.15 (Released),2.16 (Pre-Release)
cycleMaxAlarm | cycleMaxAlarm | Maximum Cycle Switching Alarm | Maximum Cycle Switching Alarm |  | cycleMaxAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | cycle,max,alarm | PFC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideDamper | minOutsideDamper | Minimum Outside Damper Command | Minimum Outside Damper Command |  | minOutsideDamper | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | minOutside,air,damper,position,cmd | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideDamperFb | minOutsideDamperFb | Minimum Outside Damper Feedback | Minimum Outside Damper Feedback |  | minOutsideDamperFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | minOutside,air,damper,position,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideDamperMinSp | minOutsideDamperMinSp | Minimum Outside Damper Minimum Setpoint | Minimum Outside Damper Minimum Setpoint |  | minOutsideDamperMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | minOutside,air,damper,position,min,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideDamperOvr | minOutsideDamperOvr | Minimum Outside Damper Override | Minimum Outside Damper Override |  | minOutsideDamperOvr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | minOutside,air,damper,position,ovr | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideFanAlarm | minOutsideFanXXXXAlarm | Minimum Outside Fan Alarm | Minimum Outside Fan XX Alarm |  | minOutsideFan(\w{0,4}(?=[A-Z]¦$))Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | minOutside,air,fan,common,alarm | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideFanAlarmReset | minOutsideFanXXXXAlarmReset | Minimum Outside Fan Alarm Reset | Minimum Outside Fan XX Alarm Reset |  | minOutsideFan(\w{0,4}(?=[A-Z]¦$))AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | minOutside,air,fan,alarm,reset | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.15 (Released),2.16 (Pre-Release)
minOutsideFan | minOutsideFanXXXX | Minimum Outside Fan Command | Minimum Outside Fan XX Command |  | minOutsideFan((?:(?!Ovr)\w){0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | minOutside,air,fan,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideFanCurrent | minOutsideFanXXXXCurrent | Minimum Outside Fan Current | Minimum Outside Fan XX Current |  | minOutsideFan(\w{0,4}(?=[A-Z]¦$))Current | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | minOutside,air,fan,current,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideFanEnteringPressure | minOutsideFanXXXXEnteringPressure | Minimum Outside Fan Entering Pressure | Minimum Outside Fan XX Entering Pressure |  | minOutsideFan(\w{0,4}(?=[A-Z]¦$))EnteringPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | minOutside,air,fan,entering,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideFanFault | minOutsideFanXXXXFault | Minimum Outside Fan Fault | Minimum Outside Fan XX Fault |  | minOutsideFan(\w{0,4}(?=[A-Z]¦$))Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | minOutside,air,fan,fault | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideFanLeavingPressure | minOutsideFanXXXXLeavingPressure | Minimum Outside Fan Leaving Pressure | Minimum Outside Fan XX Leaving Pressure |  | minOutsideFan(\w{0,4}(?=[A-Z]¦$))LeavingPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | minOutside,air,fan,leaving,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideFanMaintSwitch | minOutsideFanXXXXMaintSwitch | Minimum Outside Fan Maintenance Switch | Minimum Outside Fan XX Maintenance Switch |  | minOutsideFan(\w{0,4}(?=[A-Z]¦$))MaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | minOutside,air,fan,maintenance,switch,cmd | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.15 (Released),2.16 (Pre-Release)
minOutsideFanOvr | minOutsideFanXXXXOvr | Minimum Outside Fan Override | Minimum Outside Fan XX Override |  | minOutsideFan(\w{0,4}(?=[A-Z]¦$))Ovr | No | No | No | Bool | On/Off | On/Off | [6 empty] | minOutside,air,fan,status,ovr | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideFanPressureDelta | minOutsideFanXXXXPressureDelta | Minimum Outside Fan Pressure Delta | Minimum Outside Fan XX Pressure Delta |  | minOutsideFan(\w{0,4}(?=[A-Z]¦$))PressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | minOutside,air,fan,common,pressure,delta,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideFanPressureHiAlarm | minOutsideFanXXXXPressureHiAlarm | Minimum Outside Fan Pressure High Alarm | Minimum Outside Fan XX Pressure High Alarm |  | minOutsideFan(\w{0,4}(?=[A-Z]¦$))PressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | minOutside,air,fan,pressure,high,alarm | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideFanPressureHiSp | minOutsideFanXXXXPressureHiSp | Minimum Outside Fan Pressure High Setpoint | Minimum Outside Fan XX Pressure High Setpoint |  | minOutsideFan(\w{0,4}(?=[A-Z]¦$))PressureHiSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | minOutside,air,fan,pressure,high,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideFanPressureLoAlarm | minOutsideFanXXXXPressureLoAlarm | Minimum Outside Fan Pressure Low Alarm | Minimum Outside Fan XX Pressure Low Alarm |  | minOutsideFan(\w{0,4}(?=[A-Z]¦$))PressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | minOutside,air,fan,pressure,low,alarm | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideFanPressureLoSp | minOutsideFanXXXXPressureLoSp | Minimum Outside Fan Pressure Low Setpoint | Minimum Outside Fan XX Pressure Low Setpoint |  | minOutsideFan(\w{0,4}(?=[A-Z]¦$))PressureLoSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | minOutside,air,fan,pressure,low,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideFanRuntime | minOutsideFanXXXXRuntime | Minimum Outside Fan Runtime | Minimum Outside Fan XX Runtime |  | minOutsideFan(\w{0,4}(?=[A-Z]¦$))Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.15 (Released),2.16 (Pre-Release)
minOutsideFanSpeed | minOutsideFanXXXXSpeed | Minimum Outside Fan Speed | Minimum Outside Fan XX Speed |  | minOutsideFan(\w{0,4}(?=[A-Z]¦$))Speed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | minOutside,air,fan,speed,cmd | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideFanSpeedFb | minOutsideFanXXXXSpeedFb | Minimum Outside Fan Speed Feedback | Minimum Outside Fan XX Speed Feedback |  | minOutsideFan(\w{0,4}(?=[A-Z]¦$))SpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | minOutside,air,fan,speed,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideFanSpeedMaxSp | minOutsideFanXXXXSpeedMaxSp | Minimum Outside Fan Speed Max Setpoint | Minimum Outside Fan XX Speed Max Setpoint |  | minOutsideFan(\w{0,4}(?=[A-Z]¦$))SpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | minOutside,air,fan,speed,max,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideFanSpeedMinSp | minOutsideFanXXXXSpeedMinSp | Minimum Outside Fan Speed Min Setpoint | Minimum Outside Fan XX Speed Min Setpoint |  | minOutsideFan(\w{0,4}(?=[A-Z]¦$))SpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | minOutside,air,fan,speed,min,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideFanSpeedOvr | minOutsideFanXXXXSpeedOvr | Minimum Outside Fan Speed Override | Minimum Outside Fan XX Speed Override |  | minOutsideFan(\w{0,4}(?=[A-Z]¦$))SpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | minOutside,air,fan,speed,ovr | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideFanSpeedSp | minOutsideFanXXXXSpeedSp | Minimum Outside Fan Speed Setpoint | Minimum Outside Fan XX Speed Setpoint |  | minOutsideFan(\w{0,4}(?=[A-Z]¦$))SpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | minOutside,air,fan,speed,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideFanStatus | minOutsideFanXXXXStatus | Minimum Outside Fan Status | Minimum Outside Fan XX Status |  | minOutsideFan(\w{0,4}(?=[A-Z]¦$))Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | minOutside,air,fan,status,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideFilterAlarm | minOutsideFilterAlarm | Minimum Outside Filter Alarm | Minimum Outside Filter Alarm |  | minOutsideFilterAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | minOutside,air,filter,common,alarm | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideFilterAlarmReset | minOutsideFilterAlarmReset | Minimum Outside Filter Alarm Reset | Minimum Outside Filter Alarm Reset |  | minOutsideFilterAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | minOutside,air,filter,reset,alarm | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideFilterPressureDelta | minOutsideFilterPressureDelta | Minimum Outside Filter Pressure Delta | Minimum Outside Filter Pressure Delta |  | minOutsideFilterPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | minOutside,air,filter,pressure,delta,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released)
minOutsideFilterRuntime | minOutsideFilterRuntime | Minimum Outside Filter Runtime | Minimum Outside Filter Runtime |  | minOutsideFilterRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.15 (Released),2.16 (Pre-Release)
minOutsideFlow | minOutsideFlow | Minimum Outside Flow | Minimum Outside Flow |  | minOutsideFlow | Yes | Yes | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | minOutside,air,flow,sensor | AFMS,AHU,CRAC,CRAH,CU,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideFlowDb | minOutsideFlowDb | Minimum Outside Flow Deadband | Minimum Outside Flow Deadband |  | minOutsideFlowDb | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | minOutside,air,flow,deadband,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideFlowHiSp | minOutsideFlowHiSp | Minimum Outside Flow High Setpoint | Minimum Outside Flow High Setpoint |  | minOutsideFlowHiSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | minOutside,air,flow,high,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideFlowLoSp | minOutsideFlowLoSp | Minimum Outside Flow Low Setpoint | Minimum Outside Flow Low Setpoint |  | minOutsideFlowLoSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | minOutside,air,flow,low,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideFlowMaxSp | minOutsideFlowMaxSp | Minimum Outside Flow Max Setpoint | Minimum Outside Flow Max Setpoint |  | minOutsideFlowMaxSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | minOutside,air,flow,max,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideFlowMinSp | minOutsideFlowMinSp | Minimum Outside Flow Min Setpoint | Minimum Outside Flow Min Setpoint |  | minOutsideFlowMinSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | minOutside,air,flow,min,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
minOutsideFlowSp | minOutsideFlowSp | Minimum Outside Flow Setpoint | Minimum Outside Flow Setpoint |  | minOutsideFlowSp | Yes | Yes | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | minOutside,air,flow,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
mixedHumidity | mixedHumidity | Mixed Humidity | Mixed Humidity |  | mixedHumidity | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | mixed,air,humidity,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
mixedPressure | mixedPressure | Mixed Pressure | Mixed Pressure |  | mixedPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | mixed,air,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
mixedPressureDb | mixedPressureDb | Mixed Pressure Deadband | Mixed Pressure Deadband |  | mixedPressureDb | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | mixed,air,pressure,deadband,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
mixedPressureHiSp | mixedPressureHiSp | Mixed Pressure High Setpoint | Mixed Pressure High Setpoint |  | mixedPressureHiSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | mixed,air,pressure,high,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
mixedPressureLoAlarm | mixedPressureLoAlarm | Mixed Pressure Low Alarm | Mixed Pressure Low Alarm |  | mixedPressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | mixed,air,pressure,low,alarm | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
mixedPressureLoSp | mixedPressureLoSp | Mixed Pressure Low Setpoint | Mixed Pressure Low Setpoint |  | mixedPressureLoSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | mixed,air,pressure,low,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
mixedPressureMaxSp | mixedPressureMaxSp | Mixed Pressure Max Setpoint | Mixed Pressure Max Setpoint |  | mixedPressureMaxSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | mixed,air,pressure,max,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
mixedPressureMinSp | mixedPressureMinSp | Mixed Pressure Min Setpoint | Mixed Pressure Min Setpoint |  | mixedPressureMinSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | mixed,air,pressure,min,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
mixedPressureSp | mixedPressureSp | Mixed Pressure Setpoint | Mixed Pressure Setpoint |  | mixedPressureSp | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | mixed,air,pressure,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
mixedTemp | mixedTempXXXX | Mixed Temperature | Mixed Temperature XX |  | mixedTemp(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | mixed,air,temp,sensor | AFMS,AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
mixedTempDb | mixedTempXXXXDb | Mixed Temperature Deadband | Mixed Temperature XX Deadband |  | mixedTemp(\d{0,4})Db | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | mixed,air,temp,deadband,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
mixedTempFault | mixedTempXXXXFault | Mixed Temperature Fault | Mixed Temperature XX Fault |  | mixedTemp(\d{0,4})Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | mixed,air,temp,fault | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
mixedTempHiAlarm | mixedTempXXXXHiAlarm | Mixed Temperature High Alarm | Mixed Temperature XX High Alarm |  | mixedTemp(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | mixed,air,temp,high,alarm | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
mixedTempHiSp | mixedTempXXXXHiSp | Mixed Temperature High Setpoint | Mixed Temperature XX High Setpoint |  | mixedTemp(\d{0,4})HiSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | mixed,air,temp,high,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
mixedTempLevelAlarm | mixedTempXXXXLevelYYYYAlarm | Mixed Temperature Level Alarm | Mixed Temperature XX Level YY Alarm |  | mixedTemp(\d{0,4})Level(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | mixed,air,temp,level,alarm | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
mixedTempLoAlarm | mixedTempXXXXLoAlarm | Mixed Temperature Low Alarm | Mixed Temperature XX Low Alarm |  | mixedTemp(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | mixed,air,temp,low,alarm | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
mixedTempLoSp | mixedTempXXXXLoSp | Mixed Temperature Low Setpoint | Mixed Temperature XX Low Setpoint |  | mixedTemp(\d{0,4})LoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | mixed,air,temp,low,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
mixedTempMaxSp | mixedTempXXXXMaxSp | Mixed Temperature Max Reset Setpoint | Mixed Temperature XX Max Reset Setpoint |  | mixedTemp(\d{0,4})MaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | mixed,air,temp,max,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
mixedTempMinSp | mixedTempXXXXMinSp | Mixed Temperature Min Reset Setpoint | Mixed Temperature XX Min Reset Setpoint |  | mixedTemp(\d{0,4})MinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | mixed,air,temp,min,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
mixedTempSp | mixedTempXXXXSp | Mixed Temperature Setpoint | Mixed Temperature XX Setpoint |  | mixedTemp(\d{0,4})Sp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | mixed,air,temp,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
mixedTempUnoccSp | mixedTempXXXXUnoccSp | Mixed Temperature Unoccupied Setpoint | Mixed Temperature XX Unoccupied Setpoint |  | mixedTemp(\d{0,4})UnoccSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | mixed,air,temp,unoccupied,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
mixingValve | mixingValveXXXX | Mixing Valve Command | Mixing Valve XX Command |  | mixingValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | common,water,mixing,valve,general,position,cmd | BLR,CLR,CWS,GEO,HWS,TWR,WS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
mixingValveFb | mixingValveXXXXFb | Mixing Valve Feedback | Mixing Valve XX Feedback |  | mixingValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | common,water,mixing,valve,general,position,sensor | BLR,CLR,CWS,GEO,HWS,TWR,WS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
mixingValveOvr | mixingValveXXXXOvr | Mixing Valve Override | Mixing Valve XX Override |  | mixingValve(\d{0,4})Ovr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | common,water,mixing,valve,general,position,ovr | BLR,CLR,CWS,GEO,HWS,TWR,WS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
morningCoolDown | morningCoolDown | Morning Cool Down Command | Morning Cool Down Command |  | morningCoolDown | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | morning,coolDown,cmd | AHU,CRAC,CRAH,DHU,DOAS,EC,HP,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
morningFreeCooling | morningFreeCooling | Morning Free Cooling Command | Morning Free Cooling Command |  | morningFreeCooling | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | morning,freeCooling,cmd | AHU,CRAC,CRAH,DHU,DOAS,EC,HP,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
morningMode | morningMode | Morning Mode | Morning Mode |  | morningMode | Yes | Yes | No | Str | On/Off | Normal/Warmup/Cooldown/Coast | [6 empty] | morning,mode,cmd | AHU,CRAC,CRAH,DHU,DOAS,EC,HP,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
morningWarmUp | morningWarmUp | Morning Warm Up Command | Morning Warm Up Command |  | morningWarmUp | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | morning,warmUp,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
morningWarmUpDb | morningWarmUpDb | Morning Warm Up Deadband | Morning Warm Up Deadband |  | morningWarmUpDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | morning,warmUp,deadband,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
morningWarmUpEnable | morningWarmUpEnable | Morning Warm Up Enable Command | Morning Warm Up Enable Command |  | morningWarmUpEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | morning,warmUp,enable,cmd | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
morningWarmUpSp | morningWarmUpSp | Morning Warm Up Setpoint | Morning Warm Up Setpoint |  | morningWarmUpSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | morning,warmUp,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
motorSpeed | motorSpeed | Motor Speed | Motor Speed |  | motorSpeed | Yes | Yes | No | Number |  |  | revolutions_per_minute | revolutions_per_minute | 0 | 0 |  |  | motor,speed,cmd | MSC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
nightPurge | nightPurge | Night Purge Command | Night Purge Command |  | nightPurge | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | night,purge,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
nightPurgeEnable | nightPurgeEnable | Night Purge Enable Command | Night Purge Enable Command |  | nightPurgeEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | night,purge,enable,cmd | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
nightPurgeEnableSp | nightPurgeEnableSp | Night Purge Enable Setpoint | Night Purge Enable Setpoint |  | nightPurgeEnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | night,purge,enable,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
nightPurgeOutsideLoSp | nightPurgeOutsideLoSp | Night Purge Outside Low Setpoint | Night Purge Outside Low Setpoint |  | nightPurgeOutsideLoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | night,purge,outside,low,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
nightPurgeZoneTempDb | nightPurgeZoneTempDb | Night Purge Zone Temperature Deadband | Night Purge Zone Temperature Deadband |  | nightPurgeZoneTempDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | night,purge,zone,temp,deadband | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
nightPurgeZoneTempSp | nightPurgeZoneTempSp | Night Purge Zone Temperature Setpoint | Night Purge Zone Temperature Setpoint |  | nightPurgeZoneTempSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | night,purge,zone,temp,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
occupancySensor | occupancySensorXXXX | Occupancy Sensor | Occupancy Sensor XX |  | occupancySensor(\d{0,4}) | Yes | Yes | No | Bool | Occupied/Unoccupied | Occupied/Unoccupied | [6 empty] | occupancy,mode,sensor | AHU,ATU,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,FCU,FPB,HP,HVHS,HVLS,MAU,RP,RPC,RPF,RTU,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
occCount | occCount | Occupant Count | Occupant Count |  | occCount | Yes | Yes | No | Number |  |  |  |  | 0 | 0 |  |  | occupant,count,effective | TRN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
occCountReset | occCountReset | Occupant Count Reset | Occupant Count Reset |  | occCountReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | occupant,count,reset | TRN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
occCountEnter | occCountEnter | Occupant Enter Count | Occupant Enter Count |  | occCountEnter | Yes | Yes | No | Number |  |  |  |  | 0 | 0 |  |  | occupant,count,entering | TRN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
occCountExit | occCountExit | Occupant Exit Count | Occupant Exit Count |  | occCountExit | Yes | Yes | No | Number |  |  |  |  | 0 | 0 |  |  | occupant,count,leaving | TRN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
occupiedCoolDb | occupiedCoolDb | Occupied Cool Deadband | Occupied Cool Deadband |  | occupiedCoolDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | occupied,cool,deadband,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,HVHS,HVLS,MAU,RP,RPC,RPF,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
occupiedCoolSp | occupiedCoolSp | Occupied Cool Setpoint | Occupied Cool Setpoint |  | occupiedCoolSp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,temp,occupied,cool,common,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,HVHS,HVLS,MAU,RP,RPC,RPF,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
occupiedCoolSpLocal | occupiedCoolSpLocal | Occupied Cool Setpoint Local | Occupied Cool Setpoint Local |  | occupiedCoolSpLocal | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,temp,occupied,cool,local,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,HVHS,HVLS,MAU,RP,RPC,RPF,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
occupiedCoolSpOffset | occupiedCoolSpOffset | Occupied Cool Setpoint Offset | Occupied Cool Setpoint Offset |  | occupiedCoolSpOffset | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | zone,air,temp,occupied,cool,offset,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,HVHS,HVLS,MAU,RP,RPC,RPF,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
occupiedDehumidSp | occupiedDehumidSp | Occupied Dehumidification Setpoint | Occupied Dehumidification Setpoint |  | occupiedDehumidSp | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | zone,air,dehumid,occupied,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
occupiedDimLevelSp | occupiedDimLevelSp | Occupied Dimming Level Setpoint | Occupied Dimming Level Setpoint |  | occupiedDimLevelSp | No | No | No | Number |  |  | footcandle | lux | 0 | 0 |  |  | occupied,lightLevel,dimming,sp | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
occupiedHeatDb | occupiedHeatDb | Occupied Heat Deadband | Occupied Heat Deadband |  | occupiedHeatDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | occupied,heat,deadband,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,HVHS,HVLS,MAU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
occupiedHeatSp | occupiedHeatSp | Occupied Heat Setpoint | Occupied Heat Setpoint |  | occupiedHeatSp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,temp,occupied,heat,common,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,HVHS,HVLS,MAU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
occupiedHeatSpLocal | occupiedHeatSpLocal | Occupied Heat Setpoint Local | Occupied Heat Setpoint Local |  | occupiedHeatSpLocal | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,temp,occupied,heat,local,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,HVHS,HVLS,MAU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
occupiedHeatSpOffset | occupiedHeatSpOffset | Occupied Heat Setpoint Offset | Occupied Heat Setpoint Offset |  | occupiedHeatSpOffset | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | zone,air,temp,occupied,heat,offset,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,HVHS,HVLS,MAU,RP,RPC,RPF,RTU,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
occupiedHumidSp | occupiedHumidSp | Occupied Humidification Setpoint | Occupied Humidification Setpoint |  | occupiedHumidSp | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | zone,air,humid,occupied,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
occupiedLevelSp | occupiedLevelSp | Occupied Light Level Setpoint | Occupied Light Level Setpoint |  | occupiedLevelSp | No | No | No | Number |  |  | footcandle | lux | 0 | 0 |  |  | occupied,lightLevel,effective,sp | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
occupancyMode | occupancyMode | Occupied Mode | Occupied Mode |  | occupancyMode | Yes | Yes | No | Bool | Occupied/Unoccupied | Occupied/Unoccupied/Standby/Bypass | [6 empty] | occupancy,mode,cmd | AC,AHU,ATU,BLR,CLR,CMP,CRAC,CRAH,CUH,CWS,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,GBL,GEO,HP,HRU,HUM,HVHS,HVLS,HWS,MAU,MSC,RP,RPC,RPF,RTU,SMP,SMS,TWR,UV,VAV,WS,ZD,ZN,FCU,HP,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
occupancyModeOvr | occupancyModeOvr | Occupied Mode Override | Occupied Mode Override |  | occupancyModeOvr | No | No | No | Bool | Occupied/Unoccupied | Occupied/Unoccupied/Standby/Bypass | [6 empty] | occupancy,mode,ovr | AC,AHU,ATU,BLR,CLR,CMP,CRAC,CRAH,CUH,CWS,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,GBL,GEO,HP,HRU,HUM,HVHS,HVLS,HWS,MAU,MSC,RP,RPC,RPF,RTU,SMP,SMS,TWR,UV,VAV,WS,ZD,ZN,FCU,HP,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
occupiedTempDb | occupiedTempDb | Occupied Temperature Deadband | Occupied Temperature Deadband |  | occupiedTempDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | zone,air,temp,occupied,deadband,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,EF,FCU,FPB,HP,HVHS,HVLS,MAU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
occupiedTempSp | occupiedTempSp | Occupied Temperature Setpoint | Occupied Temperature Setpoint |  | occupiedTempSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,temp,occupied,effective,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,EF,FCU,FPB,HP,HVHS,HVLS,MAU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
oilFeedPressure | oilFeedPressure | Oil Feed Pressure | Oil Feed Pressure |  | oilFeedPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | oil,feed,pressure,sensor | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
oilFeedPressureHiAlarm | oilFeedPressureHiAlarm | Oil Feed Pressure High Alarm | Oil Feed Pressure High Alarm |  | oilFeedPressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | oil,feed,pressure,high,alarm | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
oilFeedPressureLoAlarm | oilFeedPressureLoAlarm | Oil Feed Pressure Low Alarm | Oil Feed Pressure Low Alarm |  | oilFeedPressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | oil,feed,pressure,low,alarm | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
oilFeedTemp | oilFeedTemp | Oil Feed Temperature | Oil Feed Temperature |  | oilFeedTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | oil,feed,temp,sensor | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
oilSumpLevelHiAlarm | oilSumpLevelHiAlarm | Oil Sump Level High Alarm | Oil Sump Level High Alarm |  | oilSumpLevelHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | oil,sump,level,high,alarm | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
oilSumpLevelLoAlarm | oilSumpLevelLoAlarm | Oil Sump Level Low Alarm | Oil Sump Level Low Alarm |  | oilSumpLevelLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | oil,sump,level,low,alarm | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
oilSumpPressure | oilSumpPressure | Oil Sump Pressure | Oil Sump Pressure |  | oilSumpPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | oil,sump,pressure,sensor | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
oilSumpPressureLoAlarm | oilSumpPressureLoAlarm | Oil Sump Pressure Low Alarm | Oil Sump Pressure Low Alarm |  | oilSumpPressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | oil,sump,pressure,low,alarm | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
oilSumpTemp | oilSumpTemp | Oil Sump Temperature | Oil Sump Temperature |  | oilSumpTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | oil,sump,temp,sensor | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
oilThicknessAlarm | oilThicknessAlarm | Oil Thickness Alarm | Oil Thickness Alarm |  | oilThicknessAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | oil,thickness,alarm | GINT,PINT | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
optimalStartMode | optimalStartMode | Optimal Start Mode | Optimal Start Mode |  | optimalStartMode | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | optimal,start,mode,cmd | AHU,ATU,CRAC,CRAH,CUH,CWS,DH,DHU,DOAS,EC,EF,FCU,FPB,GEO,HP,HWS,MAU,RTU,SMS,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
optimalStopMode | optimalStopMode | Optimal Stop Mode | Optimal Stop Mode |  | optimalStopMode | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | optimal,stop,mode,cmd | AHU,ATU,CRAC,CRAH,CUH,CWS,DH,DHU,DOAS,EC,EF,FCU,FPB,GEO,HP,HWS,MAU,RTU,SMS,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outEnergyApparent | outXXXXEnergyApparent | Output Apparent Energy | Output XX Apparent Energy |  | out(\d{0,4})EnergyApparent | Yes | Yes | No | Number |  |  | kilovolt_ampere_hour | kilovolt_ampere_hour | 0 | 0 |  |  | output,apparent,energy,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outPowerApparent | outXXXXPowerApparent | Output Apparent Power | Output XX Apparent Power |  | out(\d{0,4})PowerApparent | Yes | Yes | No | Number |  |  | kilovolt_ampere | kilovolt_ampere | 1 | 1 |  | N | output,power,apparent,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outPowerApparentPhaseA | outXXXXPowerApparentPhaseA | Output Apparent Power (Phase A) | Output XX Apparent Power (Phase A) |  | out(\d{0,4})PowerApparentPhaseA | Yes | Yes | No | Number |  |  | kilovolt_ampere | kilovolt_ampere | 1 | 1 |  | A | output,power,apparent,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outPowerApparentPhaseB | outXXXXPowerApparentPhaseB | Output Apparent Power (Phase B) | Output XX Apparent Power (Phase B) |  | out(\d{0,4})PowerApparentPhaseB | Yes | Yes | No | Number |  |  | kilovolt_ampere | kilovolt_ampere | 1 | 1 |  | B | output,power,apparent,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outPowerApparentPhaseC | outXXXXPowerApparentPhaseC | Output Apparent Power (Phase C) | Output XX Apparent Power (Phase C) |  | out(\d{0,4})PowerApparentPhaseC | Yes | Yes | No | Number |  |  | kilovolt_ampere | kilovolt_ampere | 1 | 1 |  | C | output,power,apparent,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outCurrent | outXXXXCurrent | Output Current (Average) | Output XX Current (Average) |  | out(\d{0,4})Current | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  |  | output,current,avg,calc | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outCurrentPhaseA | outXXXXCurrentPhaseA | Output Current (Phase A) | Output XX Current (Phase A) |  | out(\d{0,4})CurrentPhaseA | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | A | output,current,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outCurrentPhaseB | outXXXXCurrentPhaseB | Output Current (Phase B) | Output XX Current (Phase B) |  | out(\d{0,4})CurrentPhaseB | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | B | output,current,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outCurrentPhaseC | outXXXXCurrentPhaseC | Output Current (Phase C) | Output XX Current (Phase C) |  | out(\d{0,4})CurrentPhaseC | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | C | output,current,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outCurrentPhaseN | outXXXXCurrentPhaseN | Output Current (Phase N) | Output XX Current (Phase N) |  | out(\d{0,4})CurrentPhaseN | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | output,current,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outEnergy | outXXXXEnergy | Output Energy | Output XX Energy |  | out(\d{0,4})Energy | Yes | Yes | No | Number |  |  | kilowatt_hour | kilowatt_hour | 0 | 0 |  |  | output,common,energy,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outFrequency | outXXXXFrequency | Output Frequency | Output XX Frequency |  | out(\d{0,4})Frequency | Yes | Yes | No | Number |  |  | hertz | hertz | 1 | 1 |  | N | output,freq,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outFrequencyPhaseA | outXXXXFrequencyPhaseA | Output Frequency (Phase A) | Output XX Frequency (Phase A) |  | out(\d{0,4})FrequencyPhaseA | Yes | Yes | No | Number |  |  | hertz | hertz | 1 | 1 |  | A | output,freq,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outFrequencyPhaseB | outXXXXFrequencyPhaseB | Output Frequency (Phase B) | Output XX Frequency (Phase B) |  | out(\d{0,4})FrequencyPhaseB | Yes | Yes | No | Number |  |  | hertz | hertz | 1 | 1 |  | B | output,freq,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outFrequencyPhaseC | outXXXXFrequencyPhaseC | Output Frequency (Phase C) | Output XX Frequency (Phase C) |  | out(\d{0,4})FrequencyPhaseC | Yes | Yes | No | Number |  |  | hertz | hertz | 1 | 1 |  | C | output,freq,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outLoad | outXXXXLoad | Output Load | Output XX Load |  | out(\d{0,4})Load | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  | N | output,load,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outLoadPhaseA | outXXXXLoadPhaseA | Output Load Phase A | Output XX Load Phase A |  | out(\d{0,4})LoadPhaseA | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  | A | output,load,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outLoadPhaseB | outXXXXLoadPhaseB | Output Load Phase B | Output XX Load Phase B |  | out(\d{0,4})LoadPhaseB | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  | B | output,load,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outLoadPhaseC | outXXXXLoadPhaseC | Output Load Phase C | Output XX Load Phase C |  | out(\d{0,4})LoadPhaseC | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  | C | output,load,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outPowerFactor | outXXXXPowerFactor | Output Power Factor | Output XX Power Factor |  | out(\d{0,4})PowerFactor | Yes | Yes | No | Number |  |  | power_factor | power_factor | 2 | 2 |  | N | output,pf,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outPowerFactorPhaseA | outXXXXPowerFactorPhaseA | Output Power Factor (Phase A) | Output XX Power Factor (Phase A) |  | out(\d{0,4})PowerFactorPhaseA | Yes | Yes | No | Number |  |  | power_factor | power_factor | 2 | 2 |  | A | output,pf,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outPowerFactorPhaseB | outXXXXPowerFactorPhaseB | Output Power Factor (Phase B) | Output XX Power Factor (Phase B) |  | out(\d{0,4})PowerFactorPhaseB | Yes | Yes | No | Number |  |  | power_factor | power_factor | 2 | 2 |  | B | output,pf,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outPowerFactorPhaseC | outXXXXPowerFactorPhaseC | Output Power Factor (Phase C) | Output XX Power Factor (Phase C) |  | out(\d{0,4})PowerFactorPhaseC | Yes | Yes | No | Number |  |  | power_factor | power_factor | 2 | 2 |  | C | output,pf,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outEnergyReactive | outXXXXEnergyReactive | Output Reactive Energy | Output XX Reactive Energy |  | out(\d{0,4})EnergyReactive | Yes | Yes | No | Number |  |  | kilovolt_ampere_reactive_hour | kilovolt_ampere_reactive_hour | 0 | 0 |  |  | output,reactive,energy,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outPowerReactive | outXXXXPowerReactive | Output Reactive Power | Output XX Reactive Power |  | out(\d{0,4})PowerReactive | Yes | Yes | No | Number |  |  | kilovolt_ampere_reactive | kilovolt_ampere_reactive | 1 | 1 |  | N | output,power,reactive,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outPowerReactivePhaseA | outXXXXPowerReactivePhaseA | Output Reactive Power (Phase A) | Output XX Reactive Power (Phase A) |  | out(\d{0,4})PowerReactivePhaseA | Yes | Yes | No | Number |  |  | kilovolt_ampere_reactive | kilovolt_ampere_reactive | 1 | 1 |  | A | output,power,reactive,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outPowerReactivePhaseB | outXXXXPowerReactivePhaseB | Output Reactive Power (Phase B) | Output XX Reactive Power (Phase B) |  | out(\d{0,4})PowerReactivePhaseB | Yes | Yes | No | Number |  |  | kilovolt_ampere_reactive | kilovolt_ampere_reactive | 1 | 1 |  | B | output,power,reactive,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outPowerReactivePhaseC | outXXXXPowerReactivePhaseC | Output Reactive Power (Phase C) | Output XX Reactive Power (Phase C) |  | out(\d{0,4})PowerReactivePhaseC | Yes | Yes | No | Number |  |  | kilovolt_ampere_reactive | kilovolt_ampere_reactive | 1 | 1 |  | C | output,power,reactive,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outPowerReal | outXXXXPowerReal | Output Real Power | Output XX Real Power |  | out(\d{0,4})PowerReal | Yes | Yes | No | Number |  |  | kilowatt | kilowatt | 1 | 1 |  | N | output,power,real,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outPowerRealPhaseA | outXXXXPowerRealPhaseA | Output Real Power (Phase A) | Output XX Real Power (Phase A) |  | out(\d{0,4})PowerRealPhaseA | Yes | Yes | No | Number |  |  | kilowatt | kilowatt | 1 | 1 |  | A | output,power,real,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outPowerRealPhaseB | outXXXXPowerRealPhaseB | Output Real Power (Phase B) | Output XX Real Power (Phase B) |  | out(\d{0,4})PowerRealPhaseB | Yes | Yes | No | Number |  |  | kilowatt | kilowatt | 1 | 1 |  | B | output,power,real,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outPowerRealPhaseC | outXXXXPowerRealPhaseC | Output Real Power (Phase C) | Output XX Real Power (Phase C) |  | out(\d{0,4})PowerRealPhaseC | Yes | Yes | No | Number |  |  | kilowatt | kilowatt | 1 | 1 |  | C | output,power,real,sensor | ATS,BRK,INV,PDU,PFC,RECT,RPP,STS,TVS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outUnitMode | outXXXXUnitMode | Output Unit Mode | Output XX Unit Mode |  | out(\d{0,4})UnitMode | Yes | Yes | No | Str |  | Other/None/PrimaryUtility/BypassFeed/SecondaryUtility/Generator/Flywheel/Fuelcell | [6 empty] | output,unitMode,cmd | ATS,INV,PDU,PFC,RECT,RPP,STS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outVoltage | outXXXXVoltage | Output Voltage (Average) | Output XX Voltage (Average) |  | out(\d{0,4})Voltage | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  |  | output,volt,avg,calc | PDU,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outVoltageLL | outXXXXVoltageLL | Output Voltage Line-to-Line (Average) | Output XX Voltage Line-to-Line (Average) |  | out(\d{0,4})VoltageLL | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  | LL | output,volt,sensor | PDU,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outVoltagePhaseAB | outXXXXVoltagePhaseAB | Output Voltage Line-to-Line (Phase AB) | Output XX Voltage Line-to-Line (Phase AB) |  | out(\d{0,4})VoltagePhaseAB | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  | AB | output,volt,sensor | PDU,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outVoltagePhaseBC | outXXXXVoltagePhaseBC | Output Voltage Line-to-Line (Phase BC) | Output XX Voltage Line-to-Line (Phase BC) |  | out(\d{0,4})VoltagePhaseBC | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  | BC | output,volt,sensor | PDU,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outVoltagePhaseCA | outXXXXVoltagePhaseCA | Output Voltage Line-to-Line (Phase CA) | Output XX Voltage Line-to-Line (Phase CA) |  | out(\d{0,4})VoltagePhaseCA | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  | CA | output,volt,sensor | PDU,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outVoltageLN | outXXXXVoltageLN | Output Voltage Line-to-Neutral (Average) | Output XX Voltage Line-to-Neutral (Average) |  | out(\d{0,4})VoltageLN | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  | N | output,volt,sensor | PDU,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outVoltagePhaseAN | outXXXXVoltagePhaseAN | Output Voltage Line-to-Neutral (Phase A) | Output XX Voltage Line-to-Neutral (Phase A) |  | out(\d{0,4})VoltagePhaseAN | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  | A | output,volt,sensor | PDU,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outVoltagePhaseBN | outXXXXVoltagePhaseBN | Output Voltage Line-to-Neutral (Phase B) | Output XX Voltage Line-to-Neutral (Phase B) |  | out(\d{0,4})VoltagePhaseBN | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  | B | output,volt,sensor | PDU,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outVoltagePhaseCN | outXXXXVoltagePhaseCN | Output Voltage Line-to-Neutral (Phase C) | Output XX Voltage Line-to-Neutral (Phase C) |  | out(\d{0,4})VoltagePhaseCN | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  | C | output,volt,sensor | PDU,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideAirQuality | outsideAirQuality | Outside Air Quality | Outside Air Quality |  | outsideAirQuality | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | outside,air,quality,sensor | AHU,CRAC,CRAH,DHU,DOAS,WTHR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideFlow | outsideFlowXXXX | Outside Airflow | Outside Airflow XX |  | outsideFlow(\d{0,4}) | Yes | Yes | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | outside,air,flow,general,sensor | AFMS,AHU,CRAC,CRAH,CU,DOAS,HP,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideFlowDb | outsideFlowXXXXDb | Outside Airflow Deadband | Outside Airflow XX Deadband |  | outsideFlow(\d{0,4})Db | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | outside,air,flow,deadband,sp | AHU,CRAC,CRAH,DOAS,HP,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideFlowHiSp | outsideFlowXXXXHiSp | Outside Airflow High Setpoint | Outside Airflow XX High Setpoint |  | outsideFlow(\d{0,4})HiSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | outside,air,flow,high,sp | AHU,CRAC,CRAH,DOAS,HP,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideFlowLoSp | outsideFlowXXXXLoSp | Outside Airflow Low Setpoint | Outside Airflow XX Low Setpoint |  | outsideFlow(\d{0,4})LoSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | outside,air,flow,low,sp | AHU,CRAC,CRAH,DOAS,HP,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideFlowMaxSp | outsideFlowXXXXMaxSp | Outside Airflow Max Setpoint | Outside Airflow XX Max Setpoint |  | outsideFlow(\d{0,4})MaxSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | outside,air,flow,max,sp | AHU,CRAC,CRAH,DOAS,HP,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideFlowMinSp | outsideFlowXXXXMinSp | Outside Airflow Min Setpoint | Outside Airflow XX Min Setpoint |  | outsideFlow(\d{0,4})MinSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | outside,air,flow,min,sp | AHU,CRAC,CRAH,DOAS,HP,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideFlowSp | outsideFlowXXXXSp | Outside Airflow Setpoint | Outside Airflow XX Setpoint |  | outsideFlow(\d{0,4})Sp | Yes | Yes | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | outside,air,flow,effective,sp | AHU,CRAC,CRAH,DOAS,HP,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideFlowStatus | outsideFlowXXXXStatus | Outside Airflow Status | Outside Airflow XX Status |  | outsideFlow(\d{0,4})Status | Yes | Yes | No | Bool | Flow/No Flow | Flow/No Flow | [6 empty] | outside,air,flow,status,sensor | AHU,CRAC,CRAH,DOAS,HP,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideCO | outsideCO | Outside CO | Outside CO |  | outsideCO | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | outside,air,co,sensor | AHU,CRAC,CRAH,DHU,DOAS,WTHR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideCO2 | outsideCO2XXXX | Outside CO2 | Outside CO2 XX |  | outsideCO2(\d{0,4}) | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | outside,air,co2,sensor | AHU,CRAC,CRAH,DHU,DOAS,GBL,HP,MAU,RTU,UV,WTHR,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideDamper | outsideDamperXXXX | Outside Damper | Outside Damper XX |  | outsideDamper(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | outside,air,damper,position,cmd | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,MAU,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideDamperAlarm | outsideDamperXXXXAlarm | Outside Damper Alarm | Outside Damper XX Alarm |  | outsideDamper(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | outside,air,damper,alarm | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,MAU,RTU,UV,HP | 2.14,2.15 (Released),2.16 (Pre-Release)
outsideDamperFb | outsideDamperXXXXFb | Outside Damper Feedback | Outside Damper XX Feedback |  | outsideDamper(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | outside,air,damper,position,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideDamperMaintSwitch | outsideDamperXXXXMaintSwitch | Outside Damper Maintenance Switch | Outside Damper XX Maintenance Switch |  | outsideDamper(\d{0,4})MaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | outside,air,damper,maintenance,switch,cmd | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideDamperMaxSp | outsideDamperXXXXMaxSp | Outside Damper Max Reset Setpoint | Outside Damper XX Max Reset Setpoint |  | outsideDamper(\d{0,4})MaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | outside,air,damper,position,max,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideDamperMinMaxSp | outsideDamperXXXXMinMaxSp | Outside Damper Min Max Setpoint | Outside Damper XX Min Max Setpoint |  | outsideDamper(\d{0,4})MinMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | outside,air,damper,position,minMax,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideDamperMinMinSp | outsideDamperXXXXMinMinSp | Outside Damper Min Min Setpoint | Outside Damper XX Min Min Setpoint |  | outsideDamper(\d{0,4})MinMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | outside,air,damper,position,minMin,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideDamperMinSp | outsideDamperXXXXMinSp | Outside Damper Min Reset Setpoint | Outside Damper XX Min Reset Setpoint |  | outsideDamper(\d{0,4})MinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | outside,air,damper,position,min,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideDamperMinSpOvr | outsideDamperXXXXMinSpOvr | Outside Damper Min Reset Setpoint Override | Outside Damper XX Min Reset Setpoint Override |  | outsideDamper(\d{0,4})MinSpOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | outside,air,damper,position,min,spOvr | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideDamperOvr | outsideDamperXXXXOvr | Outside Damper Override | Outside Damper XX Override |  | outsideDamper(\d{0,4})Ovr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | outside,air,damper,position,ovr | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideDamperSp | outsideDamperXXXXSp | Outside Damper Setpoint | Outside Damper XX Setpoint |  | outsideDamper(\d{0,4})Sp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | outside,air,damper,position,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,UV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideDewpoint | outsideDewpoint | Outside Dewpoint | Outside Dewpoint |  | outsideDewpoint | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | outside,air,dewpoint,sensor | AHU,CRAC,CRAH,DHU,DOAS,GBL,HP,MAU,RTU,UV,WTHR,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideEnthalpy | outsideEnthalpy | Outside Enthalpy | Outside Enthalpy |  | outsideEnthalpy | Yes | Yes | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | outside,air,enthalpy,sensor | AHU,CRAC,CRAH,DHU,DOAS,GBL,HP,MAU,RTU,UV,WTHR,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideFanAlarm | outsideFanXXXXAlarm | Outside Fan Alarm | Outside Fan XX Alarm |  | outsideFan(\w{0,4}(?=[A-Z]¦$))Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | outside,air,fan,general,common,alarm | AHU,CRAC,CRAH,DHU,DOAS,HP,OF,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
outsideFanAlarmReset | outsideFanXXXXAlarmReset | Outside Fan Alarm Reset | Outside Fan XX Alarm Reset |  | outsideFan(\w{0,4}(?=[A-Z]¦$))AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | outside,air,fan,general,alarm,reset | AHU,CRAC,CRAH,DHU,DOAS,HP,OF,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
outsideFan | outsideFanXXXX | Outside Fan Command | Outside Fan XX Command |  | outsideFan((?:(?!Ovr)\w){0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | outside,air,fan,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,HP,OF,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
outsideFanCurrent | outsideFanXXXXCurrent | Outside Fan Current | Outside Fan XX Current |  | outsideFan(\w{0,4}(?=[A-Z]¦$))Current | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | outside,air,fan,current,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,OF,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
outsideFanEnteringPressure | outsideFanXXXXEnteringPressure | Outside Fan Entering Pressure | Outside Fan XX Entering Pressure |  | outsideFan(\w{0,4}(?=[A-Z]¦$))EnteringPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | outside,air,fan,entering,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,OF,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
outsideFanFault | outsideFanXXXXFault | Outside Fan Fault | Outside Fan XX Fault |  | outsideFan(\w{0,4}(?=[A-Z]¦$))Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | outside,air,fan,fault | AHU,CRAC,CRAH,DHU,DOAS,HP,OF,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
outsideFanFilterAlarm | outsideFanXXXXFilterAlarm | Outside Fan Filter Alarm | Outside Fan XX Filter Alarm |  | outsideFan(\w{0,4}(?=[A-Z]¦$))FilterAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | outside,air,fan,filter,common,alarm | AHU,CRAC,CRAH,DHU,DOAS,HP,OF,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
outsideFanFilterAlarmReset | outsideFanXXXXFilterAlarmReset | Outside Fan Filter Alarm Reset | Outside Fan XX Filter Alarm Reset |  | outsideFan(\w{0,4}(?=[A-Z]¦$))FilterAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | outside,air,fan,filter,reset,alarm | AHU,CRAC,CRAH,DHU,DOAS,HP,OF,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
outsideFanFilterPressureDelta | outsideFanXXXXFilterPressureDelta | Outside Fan Filter Pressure Delta | Outside Fan XX Filter Pressure Delta |  | outsideFan(\w{0,4}(?=[A-Z]¦$))FilterPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | outside,air,fan,filter,pressure,delta,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,OF,RTU,HP,ODU | 2.15 (Released)
outsideFanFilterRuntime | outsideFanXXXXFilterRuntime | Outside Fan Filter Runtime | Outside Fan XX Filter Runtime |  | outsideFan(\w{0,4}(?=[A-Z]¦$))FilterRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,HP,OF,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
outsideFanLeavingPressure | outsideFanXXXXLeavingPressure | Outside Fan Leaving Pressure | Outside Fan XX Leaving Pressure |  | outsideFan(\w{0,4}(?=[A-Z]¦$))LeavingPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | outside,air,fan,leaving,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,OF,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
outsideFanMaintSwitch | outsideFanXXXXMaintSwitch | Outside Fan Maintenance Switch | Outside Fan XX Maintenance Switch |  | outsideFan(\w{0,4}(?=[A-Z]¦$))MaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | outside,air,fan,maintenance,switch,cmd | AHU,CRAC,CRAH,DHU,DOAS,HP,OF,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
outsideFanOvr | outsideFanXXXXOvr | Outside Fan Override | Outside Fan XX Override |  | outsideFan(\w{0,4}(?=[A-Z]¦$))Ovr | No | No | No | Bool | On/Off | On/Off | [6 empty] | outside,air,fan,status,ovr | AHU,CRAC,CRAH,DHU,DOAS,HP,OF,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
outsideFanPressureDelta | outsideFanXXXXPressureDelta | Outside Fan Pressure Delta | Outside Fan XX Pressure Delta |  | outsideFan(\w{0,4}(?=[A-Z]¦$))PressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | outside,air,fan,common,pressure,delta,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,OF,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
outsideFanPressureHiAlarm | outsideFanXXXXPressureHiAlarm | Outside Fan Pressure High Alarm | Outside Fan XX Pressure High Alarm |  | outsideFan(\w{0,4}(?=[A-Z]¦$))PressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | outside,air,fan,pressure,high,alarm | AHU,CRAC,CRAH,DHU,DOAS,HP,OF,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
outsideFanPressureHiSp | outsideFanXXXXPressureHiSp | Outside Fan Pressure High Setpoint | Outside Fan XX Pressure High Setpoint |  | outsideFan(\w{0,4}(?=[A-Z]¦$))PressureHiSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | outside,air,fan,pressure,high,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,OF,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
outsideFanPressureLoAlarm | outsideFanXXXXPressureLoAlarm | Outside Fan Pressure Low Alarm | Outside Fan XX Pressure Low Alarm |  | outsideFan(\w{0,4}(?=[A-Z]¦$))PressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | outside,air,fan,pressure,low,alarm | AHU,CRAC,CRAH,DHU,DOAS,HP,OF,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
outsideFanPressureLoSp | outsideFanXXXXPressureLoSp | Outside Fan Pressure Low Setpoint | Outside Fan XX Pressure Low Setpoint |  | outsideFan(\w{0,4}(?=[A-Z]¦$))PressureLoSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | outside,air,fan,pressure,low,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,OF,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
outsideFanRuntime | outsideFanXXXXRuntime | Outside Fan Runtime | Outside Fan XX Runtime |  | outsideFan(\w{0,4}(?=[A-Z]¦$))Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,HP,OF,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
outsideFanSpeed | outsideFanXXXXSpeed | Outside Fan Speed | Outside Fan XX Speed |  | outsideFan(\w{0,4}(?=[A-Z]¦$))Speed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | outside,air,fan,speed,cmd | AHU,CRAC,CRAH,DHU,DOAS,HP,OF,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
outsideFanSpeedFb | outsideFanXXXXSpeedFb | Outside Fan Speed Feedback | Outside Fan XX Speed Feedback |  | outsideFan(\w{0,4}(?=[A-Z]¦$))SpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | outside,air,fan,speed,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,OF,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
outsideFanSpeedMaxSp | outsideFanXXXXSpeedMaxSp | Outside Fan Speed Max Setpoint | Outside Fan XX Speed Max Setpoint |  | outsideFan(\w{0,4}(?=[A-Z]¦$))SpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | outside,air,fan,speed,max,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,OF,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
outsideFanSpeedMinSp | outsideFanXXXXSpeedMinSp | Outside Fan Speed Min Setpoint | Outside Fan XX Speed Min Setpoint |  | outsideFan(\w{0,4}(?=[A-Z]¦$))SpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | outside,air,fan,speed,min,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,OF,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
outsideFanSpeedOvr | outsideFanXXXXSpeedOvr | Outside Fan Speed Override | Outside Fan XX Speed Override |  | outsideFan(\w{0,4}(?=[A-Z]¦$))SpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | outside,air,fan,speed,ovr | AHU,CRAC,CRAH,DHU,DOAS,HP,OF,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
outsideFanSpeedSp | outsideFanXXXXSpeedSp | Outside Fan Speed Setpoint | Outside Fan XX Speed Setpoint |  | outsideFan(\w{0,4}(?=[A-Z]¦$))SpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | outside,air,fan,speed,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,HP,OF,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
outsideFanStatus | outsideFanXXXXStatus | Outside Fan Status | Outside Fan XX Status |  | outsideFan(\w{0,4}(?=[A-Z]¦$))Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | outside,air,fan,status,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,OF,RTU,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
outsideFilterAlarm | outsideFilterAlarm | Outside Filter Alarm | Outside Filter Alarm |  | outsideFilterAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | outside,air,filter,general,common,alarm | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideFilterAlarmReset | outsideFilterAlarmReset | Outside Filter Alarm Reset | Outside Filter Alarm Reset |  | outsideFilterAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | outside,air,filter,general,reset,alarm | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideFilterPressureDelta | outsideFilterPressureDelta | Outside Filter Pressure Delta | Outside Filter Pressure Delta |  | outsideFilterPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | outside,air,filter,pressure,delta,general,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released)
outsideFilterRuntime | outsideFilterRuntime | Outside Filter Runtime | Outside Filter Runtime |  | outsideFilterRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,HP,RTU,HP | 2.15 (Released),2.16 (Pre-Release)
outsideH2S | outsideH2S | Outside H2S | Outside H2S |  | outsideH2S | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | outside,air,h2s,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,WTHR,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideHeatIndex | outsideHeatIndex | Outside Heat Index | Outside Heat Index |  | outsideHeatIndex | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | outside,air,heatIndex,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,WTHR,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideHumidity | outsideHumidity | Outside Humidity | Outside Humidity |  | outsideHumidity | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | outside,air,humidity,sensor | AHU,CRAC,CRAH,DHU,DOAS,GEO,HP,MAU,RTU,SMS,WS,WTHR,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideIsoDamper | outsideIsoDamper | Outside Isolation Damper | Outside Isolation Damper |  | outsideIsoDamper | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | outside,air,damper,iso,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideIsoDamperFb | outsideIsoDamperFb | Outside Isolation Damper Feedback | Outside Isolation Damper Feedback |  | outsideIsoDamperFb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | outside,air,damper,iso,status,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideIsoDamperOvr | outsideIsoDamperOvr | Outside Isolation Damper Override | Outside Isolation Damper Override |  | outsideIsoDamperOvr | No | No | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | outside,air,damper,iso,status,ovr | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideLightLevel | outsideLightLevel | Outside Light Level | Outside Light Level |  | outsideLightLevel | Yes | Yes | No | Number |  |  | footcandle | lux | 0 | 0 |  |  | outside,light,level,sensor | GBL,LTGE,WTHR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideNO | outsideNO | Outside NO | Outside NO |  | outsideNO | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | outside,air,no,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,WTHR,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideNO2 | outsideNO2 | Outside NO2 | Outside NO2 |  | outsideNO2 | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | outside,air,no2,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,WTHR,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideO3 | outsideO3 | Outside O3 | Outside O3 |  | outsideO3 | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | outside,air,o3,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,WTHR,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsidePM25 | outsidePM25 | Outside Particulate Matter 2.5 | Outside Particulate Matter 2.5 |  | outsidePM25 | Yes | Yes | No | Number |  |  | micrograms_per_cubic_meter | micrograms_per_cubic_meter | 1 | 1 |  |  | outside,air,pm25,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,WTHR,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsidePM10 | outsidePM10 | Outside Particulate Matter 10 | Outside Particulate Matter 10 |  | outsidePM10 | Yes | Yes | No | Number |  |  | micrograms_per_cubic_meter | micrograms_per_cubic_meter | 1 | 1 |  |  | outside,air,pm10,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,WTHR,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsidePressure | outsidePressure | Outside Pressure | Outside Pressure |  | outsidePressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 2 | 1 |  |  | outside,air,static,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,WTHR,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideSO2 | outsideSO2 | Outside SO2 | Outside SO2 |  | outsideSO2 | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | outside,air,so2,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,WTHR,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideTemp | outsideTempXXXX | Outside Temperature | Outside Temperature XX |  | outsideTemp(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | outside,air,temp,sensor | AFMS,AHU,CRAC,CRAH,CWS,DCWS,DHU,DHWS,DOAS,GBL,GEO,HP,HWS,MAU,RTU,SMS,WS,WTHR,HP,ODU | 2.15 (Released),2.16 (Pre-Release)
outsideTempAvg | outsideTempAvg | Outside Temperature (Average) | Outside Temperature (Average) |  | outsideTempAvg | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | outside,air,temp,avg,calc | AFMS,AHU,CRAC,CRAH,CWS,DCWS,DHU,DHWS,DOAS,GBL,GEO,HP,HWS,MAU,RTU,SMS,WS,WTHR,HP | 2.15 (Released),2.16 (Pre-Release)
outsideTempFault | outsideTempXXXXFault | Outside Temperature Fault | Outside Temperature XX Fault |  | outsideTemp(\d{0,4})Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | outside,air,temp,fault | AHU,CRAC,CRAH,CWS,DCWS,DHU,DHWS,DOAS,GBL,GEO,HP,HWS,MAU,RTU,SMS,WS,WTHR,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideTempHiSp | outsideTempXXXXHiSp | Outside Temperature High Setpoint | Outside Temperature XX High Setpoint |  | outsideTemp(\d{0,4})HiSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | outside,air,temp,high,setpoint | AHU,CRAC,CRAH,CWS,DCWS,DHU,DHWS,DOAS,GBL,GEO,HP,HWS,MAU,RTU,SMS,WS,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideTempLoAlarm | outsideTempXXXXLoAlarm | Outside Temperature Low Alarm | Outside Temperature XX Low Alarm |  | outsideTemp(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | outside,air,temp,low,alarm | AHU,CRAC,CRAH,CWS,DCWS,DHU,DHWS,DOAS,GBL,GEO,HP,HWS,MAU,RTU,SMS,WS,WTHR,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideTempLoSp | outsideTempXXXXLoSp | Outside Temperature Low Setpoint | Outside Temperature XX Low Setpoint |  | outsideTemp(\d{0,4})LoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | outside,air,temp,low,setpoint | AHU,CRAC,CRAH,CWS,DCWS,DHU,DHWS,DOAS,GBL,GEO,HP,HWS,MAU,RTU,SMS,WS,WTHR,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideTempMaxSp | outsideTempXXXXMaxSp | Outside Temperature Max Setpoint | Outside Temperature XX Max Setpoint |  | outsideTemp(\d{0,4})MaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | outside,air,temp,max,sp | AHU,BLR,CRAC,CRAH,CWS,DCWS,DHU,DHWS,DOAS,GBL,GEO,HP,HWS,MAU,RTU,SMS,WS,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideTempMinSp | outsideTempXXXXMinSp | Outside Temperature Min Setpoint | Outside Temperature XX Min Setpoint |  | outsideTemp(\d{0,4})MinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | outside,air,temp,min,sp | AHU,BLR,CRAC,CRAH,CWS,DCWS,DHU,DHWS,DOAS,GBL,GEO,HP,HWS,MAU,RTU,SMS,WS,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideUvIndex | outsideUvIndex | Outside UV Index | Outside UV Index |  | outsideUvIndex | Yes | Yes | No | Number |  |  |  |  | 0 | 0 |  |  | outside,uv,sensor | GBL,WTHR | 2.14,2.15 (Released),2.16 (Pre-Release)
outsideVelocity | outsideVelocity | Outside Velocity | Outside Velocity |  | outsideVelocity | Yes | Yes | No | Number |  |  | feet_per_minute | meters_per_second | 1 | 1 |  |  | outside,air,velocity,sensor | AHU,CRAC,CRAH,DHU,DOAS,HP,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideVelocityPressure | outsideVelocityPressure | Outside Velocity Pressure | Outside Velocity Pressure |  | outsideVelocityPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | outside,air,dynamic,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,GBL,HP,MAU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideWetbulbTemp | outsideWetbulbTemp | Outside Wetbulb Temperature | Outside Wetbulb Temperature |  | outsideWetbulbTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | outside,wetBulb,temp,sensor | AHU,CRAC,CRAH,CWS,DHU,DOAS,GBL,GEO,HP,HWS,MAU,RTU,SMS,WS,WTHR,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideWindDegrees | outsideWindDegrees | Outside Wind Degrees | Outside Wind Degrees |  | outsideWindDegrees | Yes | Yes | No | Number |  |  | degrees_angular | degrees_angular | 1 | 1 |  |  | outside,wind,degrees,sensor | GBL,WTHR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideWindDirection | outsideWindDirection | Outside Wind Direction | Outside Wind Direction |  | outsideWindDirection | Yes | Yes | No | Str |  | N/NNE/NE/ENE/E/ESE/SE/SSE/S/SSW/SW/WSW/W/WNW/NW/NNW | [6 empty] | outside,wind,direction,sensor | GBL,WTHR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideWindSpeed | outsideWindSpeed | Outside Wind Speed | Outside Wind Speed |  | outsideWindSpeed | Yes | Yes | No | Number |  |  | miles_per_hour | meters_per_second | 1 | 1 |  |  | outside,wind,speed,sensor | GBL,WTHR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideWindSpeedHiAlarm | outsideWindSpeedHiAlarm | Outside Wind Speed High Alarm | Outside Wind Speed High Alarm |  | outsideWindSpeedHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | outside,wind,speed,high,alarm | WTHR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
outsideWindSpeedHiSp | outsideWindSpeedHiSp | Outside Wind Speed High Setpoint | Outside Wind Speed High Setpoint |  | outsideWindSpeedHiSp | No | No | No | Number |  |  | miles_per_hour | meters_per_second | 1 | 1 |  |  | outside,wind,speed,high,sp | WTHR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
panel | panel | Panel Command | Panel Command |  | panel | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | panel,status,cmd | ENC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
panelHumidity | panelHumidity | Panel Humidity | Panel Humidity |  | panelHumidity | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | panel,air,humidity,sensor | ENC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
panelOvr | panelOvr | Panel Override | Panel Override |  | panelOvr | No | No | No | Bool | On/Off | On/Off | [6 empty] | panel,status,ovr | ENC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
panelStatus | panelStatus | Panel Status | Panel Status |  | panelStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | panel,status,sensor | ENC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
panelTemp | panelTempXXXX | Panel Temperature | Panel Temperature XX |  | panelTemp(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | panel,air,temp,sensor | ENC,PV | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
panelTempHiAlarm | panelTempXXXXHiAlarm | Panel Temperature High Alarm | Panel Temperature XX High Alarm |  | panelTemp(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | panel,air,temp,high,alarm | ENC,PV | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
panelTempHiSp | panelTempXXXXHiSp | Panel Temperature High Setpoint | Panel Temperature XX High Setpoint |  | panelTemp(\d{0,4})HiSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | panel,air,temp,high,sp | ENC,PV | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
panelTempLoAlarm | panelTempXXXXLoAlarm | Panel Temperature Low Alarm | Panel Temperature XX Low Alarm |  | panelTemp(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | panel,air,temp,low,alarm | ENC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
panelTempLoSp | panelTempXXXXLoSp | Panel Temperature Low Setpoint | Panel Temperature XX Low Setpoint |  | panelTemp(\d{0,4})LoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | panel,air,temp,low,sp | ENC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
perimeterDischargeFan | perimeterDischargeFan | Perimeter Discharge Fan Command | Perimeter Discharge Fan Command |  | perimeterDischargeFan | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | perimeter,air,discharge,fan,status,cmd | DH,FPB,PH,PIU,RP,RPC,RPF,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
perimeterDischargeFanStatus | perimeterDischargeFanStatus | Perimeter Discharge Fan Status | Perimeter Discharge Fan Status |  | perimeterDischargeFanStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | perimeter,air,discharge,fan,status,sensor | DH,PH,PIU,RP,RPC,RPF,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
perimeterHeatingDisableSp | perimeterHeatingDisableSp | Perimeter Heating Disable Setpoint | Perimeter Heating Disable Setpoint |  | perimeterHeatingDisableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | perimeterHeat,disable,sp | DH,FPB,PH,PIU,RP,RPC,RPF,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
perimeterHeatingDischargeFan | perimeterHeatingDischargeFan | Perimeter Heating Discharge Fan Command | Perimeter Heating Discharge Fan Command |  | perimeterHeatingDischargeFan | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | perimeterHeat,air,discharge,fan,status,cmd | DH,FPB,PH,PIU,RP,RPC,RPF,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
perimeterHeatingDischargeFanStatus | perimeterHeatingDischargeFanStatus | Perimeter Heating Discharge Fan Status | Perimeter Heating Discharge Fan Status |  | perimeterHeatingDischargeFanStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | perimeterHeat,air,discharge,fan,status,sensor | DH,PH,PIU,RP,RPC,RPF,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
perimeterHeatingEnable | perimeterHeatingEnable | Perimeter Heating Enable Command | Perimeter Heating Enable Command |  | perimeterHeatingEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | perimeterHeat,enable,cmd | DH,FPB,PH,PIU,RP,RPC,RPF,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
perimeterHeatingEnableDb | perimeterHeatingEnableDb | Perimeter Heating Enable Deadband | Perimeter Heating Enable Deadband |  | perimeterHeatingEnableDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | perimeterHeat,enable,deadband,sp | DH,FPB,PH,PIU,RP,RPC,RPF,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
perimeterHeatingEnableSp | perimeterHeatingEnableSp | Perimeter Heating Enable Setpoint | Perimeter Heating Enable Setpoint |  | perimeterHeatingEnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | perimeterHeat,enable,effective,sp | DH,FPB,PH,PIU,RP,RPC,RPF,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
perimeterHeatingStage | perimeterHeatingStageXXXX | Perimeter Heating Stage Command | Perimeter Heating Stage XX Command |  | perimeterHeatingStage(\d{0,4}) | Yes | Yes | No | Bool | On/Off | On/Off |  |  |  |  | XX |  | perimeterHeat,status,cmd | DH,FPB,PH,PIU,RP,RPC,RPF,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
perimeterHeatingStageOvr | perimeterHeatingStageXXXXOvr | Perimeter Heating Stage Override | Perimeter Heating Stage XX Override |  | perimeterHeatingStage(\d{0,4})Ovr | No | No | No | Bool | On/Off | On/Off |  |  |  |  | XX |  | perimeterHeat,status,ovr | DH,FPB,PH,PIU,RP,RPC,RPF,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
perimeterHeatingStageStatus | perimeterHeatingStageXXXXStatus | Perimeter Heating Stage Status | Perimeter Heating Stage XX Status |  | perimeterHeatingStage(\d{0,4})Status | Yes | Yes | No | Bool | On/Off | On/Off |  |  |  |  | XX |  | perimeterHeat,status,sensor | DH,FPB,PH,PIU,RP,RPC,RPF,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
perimeterHeatingValve | perimeterHeatingValveXXXX | Perimeter Heating Valve Command | Perimeter Heating Valve XX Command |  | perimeterHeatingValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 | XX |  | perimeterHeat,valve,position,cmd | DH,FPB,PH,PIU,RP,RPC,RPF,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
perimeterHeatingValveFb | perimeterHeatingValveXXXXFb | Perimeter Heating Valve Feedback | Perimeter Heating Valve XX Feedback |  | perimeterHeatingValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 | XX |  | perimeterHeat,valve,position,sensor | DH,FPB,PH,PIU,RP,RPC,RPF,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
perimeterHeatingValveOvr | perimeterHeatingValveXXXXOvr | Perimeter Heating Valve Override | Perimeter Heating Valve XX Override |  | perimeterHeatingValve(\d{0,4})Ovr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 | XX |  | perimeterHeat,valve,position,ovr | DH,FPB,PH,PIU,RP,RPC,RPF,VAV,ZD | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
phLevel | phLevel | PH Level | PH Level |  | phLevel | Yes | Yes | No | Number |  |  | ph | ph | 2 | 2 |  |  | ph,level,sensor | CWS,DCWS,DHWS,HWS,PWS,SMP,SMS,TNK,TWR,WS,WSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
phaseLossAlarm | phaseLossAlarm | Phase Loss Alarm | Phase Loss Alarm |  | phaseLossAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | phaseLoss,alarm | AHU,CRAC,CRAH,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
airEnteringPressure | airEnteringPressure | Pneumatic Air Entering Pressure | Pneumatic Air Entering Pressure |  | airEnteringPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | air,entering,pressure,sensor | CDA,CMP | 2.15 (Released),2.16 (Pre-Release)
airLeavingPressure | airLeavingPressure | Pneumatic Air Leaving Pressure | Pneumatic Air Leaving Pressure |  | airLeavingPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | air,leaving,pressure,sensor | CDA,CMP | 2.15 (Released),2.16 (Pre-Release)
airLeavingPressureDb | airLeavingPressureDb | Pneumatic Air Leaving Pressure Deadband | Pneumatic Air Leaving Pressure Deadband |  | airLeavingPressureDb | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | air,leaving,pressure,deadband,sp | CDA,CMP | 2.15 (Released),2.16 (Pre-Release)
airLeavingPressureHiSp | airLeavingPressureHiSp | Pneumatic Air Leaving Pressure High Setpoint | Pneumatic Air Leaving Pressure High Setpoint |  | airLeavingPressureHiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | air,leaving,pressure,high,sp | CDA,CMP | 2.15 (Released),2.16 (Pre-Release)
airLeavingPressureLoSp | airLeavingPressureLoSp | Pneumatic Air Leaving Pressure Low Setpoint | Pneumatic Air Leaving Pressure Low Setpoint |  | airLeavingPressureLoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | air,leaving,pressure,low,sp | CDA,CMP | 2.15 (Released),2.16 (Pre-Release)
airLeavingPressureSp | airLeavingPressureSp | Pneumatic Air Leaving Pressure Setpoint | Pneumatic Air Leaving Pressure Setpoint |  | airLeavingPressureSp | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | air,leaving,pressure,effective,sp | CDA,CMP | 2.15 (Released),2.16 (Pre-Release)
airPressure | airPressureXXXX | Pneumatic Air Pressure | Pneumatic Air Pressure XX |  | airPressure(\d{0,4}) | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | air,pressure,static,sensor | CDA,CMP | 2.14,2.15 (Released),2.16 (Pre-Release)
airPressureDb | airPressureDb | Pneumatic Air Pressure Deadband | Pneumatic Air Pressure Deadband |  | airPressureDb | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | air,pressure,static,deadband,sp | CDA,CMP | 2.14,2.15 (Released),2.16 (Pre-Release)
airPressureDelta | airPressureDelta | Pneumatic Air Pressure Delta | Pneumatic Air Pressure Delta |  | airPressureDelta | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | air,pressure,delta,sensor | CDA,CMP | 2.14,2.15 (Released),2.16 (Pre-Release)
airPressureHiSp | airPressureHiSp | Pneumatic Air Pressure High Setpoint | Pneumatic Air Pressure High Setpoint |  | airPressureHiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | air,pressure,static,high,sp | CDA,CMP | 2.14,2.15 (Released),2.16 (Pre-Release)
airPressureLoSp | airPressureLoSp | Pneumatic Air Pressure Low Setpoint | Pneumatic Air Pressure Low Setpoint |  | airPressureLoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | air,pressure,static,low,sp | CDA,CMP | 2.14,2.15 (Released),2.16 (Pre-Release)
airPressureSp | airPressureSp | Pneumatic Air Pressure Setpoint | Pneumatic Air Pressure Setpoint |  | airPressureSp | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | air,pressure,static,effective,sp | CDA,CMP | 2.14,2.15 (Released),2.16 (Pre-Release)
power | powerXXXX | Power | Power XX |  | power(\d{0,4}) | Yes | Yes | No | Number |  |  | kilobtus_per_hour | kilobtus_per_hour | 1 | 1 |  |  | common,power,btu,sensor | AC,AHU,ATU,BLR,CLR,CMP,CRAC,CRAH,CU,CUH,CWS,DAC,DH,DOAS,EF,FCU,FPB,GEO,HP,HUM,HWS,INV,MAU,PFC,PM,PRLY,PV,RECT,RTU,SMS,TWR,UV,VAV,VPM,WS,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
powerFactor | powerFactor | Power Factor | Power Factor |  | powerFactor | Yes | Yes | No | Number |  |  | power_factor | power_factor | 2 | 2 |  | N | common,pf,sensor | ATS,BRK,CU,INV,PDU,PFC,PM,PRLY,PV,RECT,RPP,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
powerFactorPhaseA | powerFactorPhaseA | Power Factor (Phase A) | Power Factor (Phase A) |  | powerFactorPhaseA | Yes | Yes | No | Number |  |  | power_factor | power_factor | 2 | 2 |  | A | common,pf,sensor | ATS,BRK,CU,INV,PDU,PFC,PM,PRLY,PV,RECT,RPP,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
powerFactorPhaseB | powerFactorPhaseB | Power Factor (Phase B) | Power Factor (Phase B) |  | powerFactorPhaseB | Yes | Yes | No | Number |  |  | power_factor | power_factor | 2 | 2 |  | B | common,pf,sensor | ATS,BRK,CU,INV,PDU,PFC,PM,PRLY,PV,RECT,RPP,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
powerFactorPhaseC | powerFactorPhaseC | Power Factor (Phase C) | Power Factor (Phase C) |  | powerFactorPhaseC | Yes | Yes | No | Number |  |  | power_factor | power_factor | 2 | 2 |  | C | common,pf,sensor | ATS,BRK,CU,INV,PDU,PFC,PM,PRLY,PV,RECT,RPP,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
powerLossAlarm | powerLossAlarm | Power Loss Alarm | Power Loss Alarm |  | powerLossAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | power,loss,alarm | ATS,BRK,INV,MSC,PM,PRLY,PV,RECT,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
powerSource | powerSource | Power Source | Power Source |  | powerSource | Yes | Yes | No | Bool | Backup/Main | Backup/Main | [6 empty] | common,power,source,sensor | ATU,STS,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilDischargeTemp | preCoolingCoilXXXXDischargeTemp | Pre-Cooling Coil Discharge Temperature | Pre-Cooling Coil XX Discharge Temperature |  | preCoolingCoil(\d{0,4})DischargeTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | precool,coil,air,discharge,temp,sensor | AFMS,AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilDischargeTempDb | preCoolingCoilXXXXDischargeTempDb | Pre-Cooling Coil Discharge Temperature Deadband | Pre-Cooling Coil XX Discharge Temperature Deadband |  | preCoolingCoil(\d{0,4})DischargeTempDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | precool,coil,air,discharge,temp,deadband,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilDischargeTempHiSp | preCoolingCoilXXXXDischargeTempHiSp | Pre-Cooling Coil Discharge Temperature High Setpoint | Pre-Cooling Coil XX Discharge Temperature High Setpoint |  | preCoolingCoil(\d{0,4})DischargeTempHiSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | precool,coil,air,discharge,temp,high,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilDischargeTempLoSp | preCoolingCoilXXXXDischargeTempLoSp | Pre-Cooling Coil Discharge Temperature Low Setpoint | Pre-Cooling Coil XX Discharge Temperature Low Setpoint |  | preCoolingCoil(\d{0,4})DischargeTempLoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | precool,coil,air,discharge,temp,low,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilDischargeTempMaxSp | preCoolingCoilXXXXDischargeTempMaxSp | Pre-Cooling Coil Discharge Temperature Max Setpoint | Pre-Cooling Coil XX Discharge Temperature Max Setpoint |  | preCoolingCoil(\d{0,4})DischargeTempMaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | precool,coil,air,discharge,temp,max,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilDischargeTempMinSp | preCoolingCoilXXXXDischargeTempMinSp | Pre-Cooling Coil Discharge Temperature Min Setpoint | Pre-Cooling Coil XX Discharge Temperature Min Setpoint |  | preCoolingCoil(\d{0,4})DischargeTempMinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | precool,coil,air,discharge,temp,min,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilDischargeTempSp | preCoolingCoilXXXXDischargeTempSp | Pre-Cooling Coil Discharge Temperature Setpoint | Pre-Cooling Coil XX Discharge Temperature Setpoint |  | preCoolingCoil(\d{0,4})DischargeTempSp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | precool,coil,air,discharge,temp,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilEnergy | preCoolingCoilXXXXEnergy | Pre-Cooling Coil Energy (Tons Refrig) | Pre-Cooling Coil XX Energy (Tons Refrig) |  | preCoolingCoil(\d{0,4})Energy | Yes | Yes | No | Number |  |  | tons_refrigeration_hour | tons_refrigeration_hour | 0 | 0 |  |  | precool,coil,water,energy,common,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilEnteringPressure | preCoolingCoilXXXXEnteringPressure | Pre-Cooling Coil Entering Pressure | Pre-Cooling Coil XX Entering Pressure |  | preCoolingCoil(\d{0,4})EnteringPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | precool,coil,water,entering,pressure,general,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilEnteringTemp | preCoolingCoilXXXXEnteringTemp | Pre-Cooling Coil Entering Temperature | Pre-Cooling Coil XX Entering Temperature |  | preCoolingCoil(\d{0,4})EnteringTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | precool,coil,water,entering,temp,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilFilterAlarm | preCoolingCoilXXXXFilterAlarm | Pre-Cooling Coil Filter Alarm | Pre-Cooling Coil XX Filter Alarm |  | preCoolingCoil(\d{0,4})FilterAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | precool,coil,air,filter,general,alarm | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilFilterAlarmReset | preCoolingCoilXXXXFilterAlarmReset | Pre-Cooling Coil Filter Alarm Reset | Pre-Cooling Coil XX Filter Alarm Reset |  | preCoolingCoil(\d{0,4})FilterAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | precool,coil,air,filter,reset,alarm | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilFilterPressureDelta | preCoolingCoilXXXXFilterPressureDelta | Pre-Cooling Coil Filter Pressure Delta | Pre-Cooling Coil XX Filter Pressure Delta |  | preCoolingCoil(\d{0,4})FilterPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | precool,coil,air,filter,pressure,delta | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released)
preCoolingCoilFilterRuntime | preCoolingCoilXXXXFilterRuntime | Pre-Cooling Coil Filter Runtime | Pre-Cooling Coil XX Filter Runtime |  | preCoolingCoil(\d{0,4})FilterRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.15 (Released),2.16 (Pre-Release)
preCoolingCoilFlow | preCoolingCoilXXXXFlow | Pre-Cooling Coil Flow | Pre-Cooling Coil XX Flow |  | preCoolingCoil(\d{0,4})Flow | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | precool,coil,water,flow,cmd | AFMS,AHU,CRAC,CRAH,CU,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilFlowStatus | preCoolingCoilXXXXFlowStatus | Pre-Cooling Coil Flow Status | Pre-Cooling Coil XX Flow Status |  | preCoolingCoil(\d{0,4})FlowStatus | Yes | Yes | No | Bool | Flow/No Flow | Flow/No Flow | [6 empty] | precool,coil,water,flow,status | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilLeavingPressure | preCoolingCoilXXXXLeavingPressure | Pre-Cooling Coil Leaving Pressure | Pre-Cooling Coil XX Leaving Pressure |  | preCoolingCoil(\d{0,4})LeavingPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | precool,coil,water,leaving,pressure,general,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilLeavingTemp | preCoolingCoilXXXXLeavingTemp | Pre-Cooling Coil Leaving Temperature | Pre-Cooling Coil XX Leaving Temperature |  | preCoolingCoil(\d{0,4})LeavingTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | precool,coil,water,leaving,temp,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPower | preCoolingCoilXXXXPower | Pre-Cooling Coil Power | Pre-Cooling Coil XX Power |  | preCoolingCoil(\d{0,4})Power | Yes | Yes | No | Number |  |  | tons_refrigeration | tons_refrigeration | 1 | 1 |  |  | precool,coil,water,power,common,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPumpAlarm | preCoolingCoilXXXXPumpAlarm | Pre-Cooling Coil Pump Alarm | Pre-Cooling Coil XX Pump Alarm |  | preCoolingCoil(\d{0,4})PumpAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | precool,coil,water,pump,common,alarm | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPumpAlarmReset | preCoolingCoilXXXXPumpAlarmReset | Pre-Cooling Coil Pump Alarm Reset | Pre-Cooling Coil XX Pump Alarm Reset |  | preCoolingCoil(\d{0,4})PumpAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | precool,coil,water,pump,reset,alarm | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPump | preCoolingCoilXXXXPump | Pre-Cooling Coil Pump Command | Pre-Cooling Coil XX Pump Command |  | preCoolingCoil(\d{0,4})Pump | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | precool,coil,water,pump,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPumpCurrent | preCoolingCoilXXXXPumpCurrent | Pre-Cooling Coil Pump Current | Pre-Cooling Coil XX Pump Current |  | preCoolingCoil(\d{0,4})PumpCurrent | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | precool,coil,water,pump,current,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPumpEnable | preCoolingCoilXXXXPumpEnable | Pre-Cooling Coil Pump Enable | Pre-Cooling Coil XX Pump Enable |  | preCoolingCoil(\d{0,4})PumpEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | precool,coil,water,pump,enable,cmd | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPumpEnableDb | preCoolingCoilXXXXPumpEnableDb | Pre-Cooling Coil Pump Enable Deadband | Pre-Cooling Coil XX Pump Enable Deadband |  | preCoolingCoil(\d{0,4})PumpEnableDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | precool,coil,water,pump,enable,deadband,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPumpEnableSp | preCoolingCoilXXXXPumpEnableSp | Pre-Cooling Coil Pump Enable Setpoint | Pre-Cooling Coil XX Pump Enable Setpoint |  | preCoolingCoil(\d{0,4})PumpEnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | precool,coil,water,pump,enable,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPumpEnteringPressure | preCoolingCoilXXXXPumpEnteringPressure | Pre-Cooling Coil Pump Entering Pressure | Pre-Cooling Coil XX Pump Entering Pressure |  | preCoolingCoil(\d{0,4})PumpEnteringPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | precool,coil,water,pump,entering,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPumpFault | preCoolingCoilXXXXPumpFault | Pre-Cooling Coil Pump Fault | Pre-Cooling Coil XX Pump Fault |  | preCoolingCoil(\d{0,4})PumpFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | precool,coil,water,pump,fault,common | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPumpLagDisableSp | preCoolingCoilXXXXPumpLagDisableSp | Pre-Cooling Coil Pump Lag Disable Setpoint | Pre-Cooling Coil XX Pump Lag Disable Setpoint |  | preCoolingCoil(\d{0,4})PumpLagDisableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | precool,coil,water,pump,lag,disable,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPumpLagEnableSp | preCoolingCoilXXXXPumpLagEnableSp | Pre-Cooling Coil Pump Lag Enable Setpoint | Pre-Cooling Coil XX Pump Lag Enable Setpoint |  | preCoolingCoil(\d{0,4})PumpLagEnableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | precool,coil,water,pump,lag,enable,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPumpLagReq | preCoolingCoilXXXXPumpLagReq | Pre-Cooling Coil Pump Lag Request | Pre-Cooling Coil XX Pump Lag Request |  | preCoolingCoil(\d{0,4})PumpLagReq | No | No | No | Bool | Request/No Request | Request/No Request | [6 empty] | precool,coil,water,pump,lag,request,cmd | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPumpLead | preCoolingCoilPumpLead | Pre-Cooling Coil Pump Lead | Pre-Cooling Coil Pump Lead |  | preCoolingCoilPumpLead | Yes | Yes | No | Bool | Lead 1/Lead 2 | Lead 1/Lead 2 | [6 empty] | precool,coil,water,pump,lead,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPumpLeadXor | preCoolingCoilPumpLeadXor | Pre-Cooling Coil Pump Lead Change Over | Pre-Cooling Coil Pump Lead Change Over |  | preCoolingCoilPumpLeadXor | No | No | No | Bool | On/Off | On/Off | [6 empty] | precool,coil,water,pump,lead,changeOver,cmd | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPumpLeadXorRuntimeSp | preCoolingCoilPumpLeadXorRuntimeSp | Pre-Cooling Coil Pump Lead Change Over Runtime Setpoint | Pre-Cooling Coil Pump Lead Change Over Runtime Setpoint |  | preCoolingCoilPumpLeadXorRuntimeSp | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPumpLeavingPressure | preCoolingCoilXXXXPumpLeavingPressure | Pre-Cooling Coil Pump Leaving Pressure | Pre-Cooling Coil XX Pump Leaving Pressure |  | preCoolingCoil(\d{0,4})PumpLeavingPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | precool,coil,water,pump,leaving,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPumpMaintSwitch | preCoolingCoilXXXXPumpMaintSwitch | Pre-Cooling Coil Pump Maintenance Switch | Pre-Cooling Coil XX Pump Maintenance Switch |  | preCoolingCoil(\d{0,4})PumpMaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | precool,coil,water,pump,maintenance,switch,cmd | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPumpOvr | preCoolingCoilXXXXPumpOvr | Pre-Cooling Coil Pump Override | Pre-Cooling Coil XX Pump Override |  | preCoolingCoil(\d{0,4})PumpOvr | No | No | No | Bool | On/Off | On/Off | [6 empty] | precool,coil,water,pump,status,ovr | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPumpPressureDelta | preCoolingCoilXXXXPumpPressureDelta | Pre-Cooling Coil Pump Pressure Delta | Pre-Cooling Coil XX Pump Pressure Delta |  | preCoolingCoil(\d{0,4})PumpPressureDelta | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | precool,coil,water,pump,common,pressure,delta,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPumpPressureHiAlarm | preCoolingCoilXXXXPumpPressureHiAlarm | Pre-Cooling Coil Pump Pressure High Alarm | Pre-Cooling Coil XX Pump Pressure High Alarm |  | preCoolingCoil(\d{0,4})PumpPressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | precool,coil,water,pump,pressure,high,alarm | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPumpPressureHiSp | preCoolingCoilXXXXPumpPressureHiSp | Pre-Cooling Coil Pump Pressure High Setpoint | Pre-Cooling Coil XX Pump Pressure High Setpoint |  | preCoolingCoil(\d{0,4})PumpPressureHiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | precool,coil,water,pump,pressure,high,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPumpPressureLoAlarm | preCoolingCoilXXXXPumpPressureLoAlarm | Pre-Cooling Coil Pump Pressure Low Alarm | Pre-Cooling Coil XX Pump Pressure Low Alarm |  | preCoolingCoil(\d{0,4})PumpPressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | precool,coil,water,pump,pressure,low,alarm | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPumpPressureLoSp | preCoolingCoilXXXXPumpPressureLoSp | Pre-Cooling Coil Pump Pressure Low Setpoint | Pre-Cooling Coil XX Pump Pressure Low Setpoint |  | preCoolingCoil(\d{0,4})PumpPressureLoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | precool,coil,water,pump,pressure,low,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPumpRuntime | preCoolingCoilXXXXPumpRuntime | Pre-Cooling Coil Pump Runtime | Pre-Cooling Coil XX Pump Runtime |  | preCoolingCoil(\d{0,4})PumpRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPumpSpeed | preCoolingCoilXXXXPumpSpeed | Pre-Cooling Coil Pump Speed | Pre-Cooling Coil XX Pump Speed |  | preCoolingCoil(\d{0,4})PumpSpeed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | precool,coil,water,pump,speed,cmd | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPumpSpeedFb | preCoolingCoilXXXXPumpSpeedFb | Pre-Cooling Coil Pump Speed Feedback | Pre-Cooling Coil XX Pump Speed Feedback |  | preCoolingCoil(\d{0,4})PumpSpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | precool,coil,water,pump,speed,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPumpSpeedMaxSp | preCoolingCoilXXXXPumpSpeedMaxSp | Pre-Cooling Coil Pump Speed Max Setpoint | Pre-Cooling Coil XX Pump Speed Max Setpoint |  | preCoolingCoil(\d{0,4})PumpSpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | precool,coil,water,pump,speed,max,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPumpSpeedMinSp | preCoolingCoilXXXXPumpSpeedMinSp | Pre-Cooling Coil Pump Speed Min Setpoint | Pre-Cooling Coil XX Pump Speed Min Setpoint |  | preCoolingCoil(\d{0,4})PumpSpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | precool,coil,water,pump,speed,min,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPumpSpeedOvr | preCoolingCoilXXXXPumpSpeedOvr | Pre-Cooling Coil Pump Speed Override | Pre-Cooling Coil XX Pump Speed Override |  | preCoolingCoil(\d{0,4})PumpSpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | precool,coil,water,pump,speed,ovr | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPumpSpeedSp | preCoolingCoilXXXXPumpSpeedSp | Pre-Cooling Coil Pump Speed Setpoint | Pre-Cooling Coil XX Pump Speed Setpoint |  | preCoolingCoil(\d{0,4})PumpSpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | precool,coil,water,pump,speed,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilPumpStatus | preCoolingCoilXXXXPumpStatus | Pre-Cooling Coil Pump Status | Pre-Cooling Coil XX Pump Status |  | preCoolingCoil(\d{0,4})PumpStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | precool,coil,water,pump,status,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilStrainerAlarm | preCoolingCoilXXXXStrainerAlarm | Pre-Cooling Coil Strainer Alarm | Pre-Cooling Coil XX Strainer Alarm |  | preCoolingCoil(\d{0,4})StrainerAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | precool,water,strainer,alarm | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingCoilStrainerEnable | preCoolingCoilXXXXStrainerEnable | Pre-Cooling Coil Strainer Enable | Pre-Cooling Coil XX Strainer Enable |  | preCoolingCoil(\d{0,4})StrainerEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | precool,water,strainer,enable,cmd | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingMode | preCoolingMode | Pre-Cooling Mode | Pre-Cooling Mode |  | preCoolingMode | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | precool,mode,cmd | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingValve | preCoolingValve | Pre-Cooling Valve Command | Pre-Cooling Valve Command |  | preCoolingValve | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | precool,valve,position,cmd | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingValveFb | preCoolingValveFb | Pre-Cooling Valve Feedback | Pre-Cooling Valve Feedback |  | preCoolingValveFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | precool,valve,position,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preCoolingValveOvr | preCoolingValveOvr | Pre-Cooling Valve Override Commmand | Pre-Cooling Valve Override Commmand |  | preCoolingValveOvr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | precool,valve,position,ovr | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilDischargeTemp | preHeatingCoilXXXXDischargeTemp | Pre-Heating Coil Discharge Temperature | Pre-Heating Coil XX Discharge Temperature |  | preHeatingCoil(\d{0,4})DischargeTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | preheat,coil,air,discharge,temp,sensor | AFMS,AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilDischargeTempDb | preHeatingCoilXXXXDischargeTempDb | Pre-Heating Coil Discharge Temperature Deadband | Pre-Heating Coil XX Discharge Temperature Deadband |  | preHeatingCoil(\d{0,4})DischargeTempDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | preHeat,coil,air,discharge,temp,deadband,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilDischargeTempHiSp | preHeatingCoilXXXXDischargeTempHiSp | Pre-Heating Coil Discharge Temperature High Setpoint | Pre-Heating Coil XX Discharge Temperature High Setpoint |  | preHeatingCoil(\d{0,4})DischargeTempHiSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | preHeat,coil,air,discharge,temp,high,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilDischargeTempLoSp | preHeatingCoilXXXXDischargeTempLoSp | Pre-Heating Coil Discharge Temperature Low Setpoint | Pre-Heating Coil XX Discharge Temperature Low Setpoint |  | preHeatingCoil(\d{0,4})DischargeTempLoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | preHeat,coil,air,discharge,temp,low,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilDischargeTempMaxSp | preHeatingCoilXXXXDischargeTempMaxSp | Pre-Heating Coil Discharge Temperature Max Setpoint | Pre-Heating Coil XX Discharge Temperature Max Setpoint |  | preHeatingCoil(\d{0,4})DischargeTempMaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | preheat,coil,air,discharge,temp,max,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilDischargeTempMinSp | preHeatingCoilXXXXDischargeTempMinSp | Pre-Heating Coil Discharge Temperature Min Setpoint | Pre-Heating Coil XX Discharge Temperature Min Setpoint |  | preHeatingCoil(\d{0,4})DischargeTempMinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | preheat,coil,air,discharge,temp,min,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilDischargeTempSp | preHeatingCoilXXXXDischargeTempSp | Pre-Heating Coil Discharge Temperature Setpoint | Pre-Heating Coil XX Discharge Temperature Setpoint |  | preHeatingCoil(\d{0,4})DischargeTempSp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | preheat,coil,air,discharge,temp,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilEnergy | preHeatingCoilXXXXEnergy | Pre-Heating Coil Energy | Pre-Heating Coil XX Energy |  | preHeatingCoil(\d{0,4})Energy | Yes | Yes | No | Number |  |  | kilobtu | kilobtu | 0 | 0 |  |  | preheat,coil,water,energy,common,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilEnteringPressure | preHeatingCoilXXXXEnteringPressure | Pre-Heating Coil Entering Pressure | Pre-Heating Coil XX Entering Pressure |  | preHeatingCoil(\d{0,4})EnteringPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | preheat,coil,water,entering,pressure,general,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilEnteringTemp | preHeatingCoilXXXXEnteringTemp | Pre-Heating Coil Entering Temperature | Pre-Heating Coil XX Entering Temperature |  | preHeatingCoil(\d{0,4})EnteringTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | preheat,coil,water,entering,temp,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilFilterAlarm | preHeatingCoilXXXXFilterAlarm | Pre-Heating Coil Filter Alarm | Pre-Heating Coil XX Filter Alarm |  | preHeatingCoil(\d{0,4})FilterAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | preheat,coil,air,filter,common,alarm | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilFilterAlarmReset | preHeatingCoilXXXXFilterAlarmReset | Pre-Heating Coil Filter Alarm Reset | Pre-Heating Coil XX Filter Alarm Reset |  | preHeatingCoil(\d{0,4})FilterAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | preheat,coil,air,filter,reset,alarm | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilFilterPressureDelta | preHeatingCoilXXXXFilterPressureDelta | Pre-Heating Coil Filter Pressure Delta | Pre-Heating Coil XX Filter Pressure Delta |  | preHeatingCoil(\d{0,4})FilterPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | preheat,coil,air,filter,pressure,delta | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released)
preHeatingCoilFilterRuntime | preHeatingCoilXXXXFilterRuntime | Pre-Heating Coil Filter Runtime | Pre-Heating Coil XX Filter Runtime |  | preHeatingCoil(\d{0,4})FilterRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.15 (Released),2.16 (Pre-Release)
preHeatingCoilFlow | preHeatingCoilXXXXFlow | Pre-Heating Coil Flow | Pre-Heating Coil XX Flow |  | preHeatingCoil(\d{0,4})Flow | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | preheat,coil,water,flow,cmd | AFMS,AHU,CRAC,CRAH,CU,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilFlowStatus | preHeatingCoilXXXXFlowStatus | Pre-Heating Coil Flow Status | Pre-Heating Coil XX Flow Status |  | preHeatingCoil(\d{0,4})FlowStatus | Yes | Yes | No | Bool | Flow/No Flow | Flow/No Flow | [6 empty] | preheat,coil,water,flow,status | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilLeavingPressure | preHeatingCoilXXXXLeavingPressure | Pre-Heating Coil Leaving Pressure | Pre-Heating Coil XX Leaving Pressure |  | preHeatingCoil(\d{0,4})LeavingPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | preheat,coil,water,leaving,pressure,general,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilLeavingTemp | preHeatingCoilXXXXLeavingTemp | Pre-Heating Coil Leaving Temperature | Pre-Heating Coil XX Leaving Temperature |  | preHeatingCoil(\d{0,4})LeavingTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | preheat,coil,water,leaving,temp,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPower | preHeatingCoilXXXXPower | Pre-Heating Coil Power | Pre-Heating Coil XX Power |  | preHeatingCoil(\d{0,4})Power | Yes | Yes | No | Number |  |  | kilobtus_per_hour | kilobtus_per_hour | 1 | 1 |  |  | preheat,coil,water,power,common,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPumpAlarm | preHeatingCoilXXXXPumpAlarm | Pre-Heating Coil Pump Alarm | Pre-Heating Coil XX Pump Alarm |  | preHeatingCoil(\d{0,4})PumpAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | preheat,coil,water,pump,common,alarm | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPumpAlarmReset | preHeatingCoilXXXXPumpAlarmReset | Pre-Heating Coil Pump Alarm Reset | Pre-Heating Coil XX Pump Alarm Reset |  | preHeatingCoil(\d{0,4})PumpAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | preheat,coil,water,pump,reset,alarm | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPump | preHeatingCoilXXXXPump | Pre-Heating Coil Pump Command | Pre-Heating Coil XX Pump Command |  | preHeatingCoil(\d{0,4})Pump | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | preheat,coil,water,pump,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPumpCurrent | preHeatingCoilXXXXPumpCurrent | Pre-Heating Coil Pump Current | Pre-Heating Coil XX Pump Current |  | preHeatingCoil(\d{0,4})PumpCurrent | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | preheat,coil,water,pump,current,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPumpEnable | preHeatingCoilXXXXPumpEnable | Pre-Heating Coil Pump Enable | Pre-Heating Coil XX Pump Enable |  | preHeatingCoil(\d{0,4})PumpEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | preheat,coil,water,pump,enable,cmd | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPumpEnableDb | preHeatingCoilXXXXPumpEnableDb | Pre-Heating Coil Pump Enable Deadband | Pre-Heating Coil XX Pump Enable Deadband |  | preHeatingCoil(\d{0,4})PumpEnableDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | preheat,coil,water,pump,enable,deadband,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPumpEnableSp | preHeatingCoilXXXXPumpEnableSp | Pre-Heating Coil Pump Enable Setpoint | Pre-Heating Coil XX Pump Enable Setpoint |  | preHeatingCoil(\d{0,4})PumpEnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | preheat,coil,water,pump,enable,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPumpEnteringPressure | preHeatingCoilXXXXPumpEnteringPressure | Pre-Heating Coil Pump Entering Pressure | Pre-Heating Coil XX Pump Entering Pressure |  | preHeatingCoil(\d{0,4})PumpEnteringPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | preheat,coil,water,pump,entering,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPumpFault | preHeatingCoilXXXXPumpFault | Pre-Heating Coil Pump Fault | Pre-Heating Coil XX Pump Fault |  | preHeatingCoil(\d{0,4})PumpFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | preheat,coil,water,pump,fault,common | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPumpLagDisableSp | preHeatingCoilXXXXPumpLagDisableSp | Pre-Heating Coil Pump Lag Disable Setpoint | Pre-Heating Coil XX Pump Lag Disable Setpoint |  | preHeatingCoil(\d{0,4})PumpLagDisableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | preheat,coil,water,pump,lag,disable,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPumpLagEnableSp | preHeatingCoilXXXXPumpLagEnableSp | Pre-Heating Coil Pump Lag Enable Setpoint | Pre-Heating Coil XX Pump Lag Enable Setpoint |  | preHeatingCoil(\d{0,4})PumpLagEnableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | preheat,coil,water,pump,lag,enable,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPumpLagReq | preHeatingCoilXXXXPumpLagReq | Pre-Heating Coil Pump Lag Request | Pre-Heating Coil XX Pump Lag Request |  | preHeatingCoil(\d{0,4})PumpLagReq | No | No | No | Bool | Request/No Request | Request/No Request | [6 empty] | preheat,coil,water,pump,lag,request,cmd | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPumpLead | preHeatingCoilPumpLead | Pre-Heating Coil Pump Lead | Pre-Heating Coil Pump Lead |  | preHeatingCoilPumpLead | Yes | Yes | No | Bool | Lead 1/Lead 2 | Lead 1/Lead 2 | [6 empty] | preheat,coil,water,pump,lead,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPumpLeadXor | preHeatingCoilPumpLeadXor | Pre-Heating Coil Pump Lead Change Over | Pre-Heating Coil Pump Lead Change Over |  | preHeatingCoilPumpLeadXor | No | No | No | Bool | On/Off | On/Off | [6 empty] | preheat,coil,water,pump,lead,changeOver,cmd | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPumpLeadXorRuntimeSp | preHeatingCoilPumpLeadXorRuntimeSp | Pre-Heating Coil Pump Lead Change Over Runtime Setpoint | Pre-Heating Coil Pump Lead Change Over Runtime Setpoint |  | preHeatingCoilPumpLeadXorRuntimeSp | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPumpLeavingPressure | preHeatingCoilXXXXPumpLeavingPressure | Pre-Heating Coil Pump Leaving Pressure | Pre-Heating Coil XX Pump Leaving Pressure |  | preHeatingCoil(\d{0,4})PumpLeavingPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | preheat,coil,water,pump,leaving,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPumpMaintSwitch | preHeatingCoilXXXXPumpMaintSwitch | Pre-Heating Coil Pump Maintenance Switch | Pre-Heating Coil XX Pump Maintenance Switch |  | preHeatingCoil(\d{0,4})PumpMaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | preheat,coil,water,pump,maintenance,switch,cmd | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPumpOvr | preHeatingCoilXXXXPumpOvr | Pre-Heating Coil Pump Override | Pre-Heating Coil XX Pump Override |  | preHeatingCoil(\d{0,4})PumpOvr | No | No | No | Bool | On/Off | On/Off | [6 empty] | preheat,coil,water,pump,status,ovr | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPumpPressureDelta | preHeatingCoilXXXXPumpPressureDelta | Pre-Heating Coil Pump Pressure Delta | Pre-Heating Coil XX Pump Pressure Delta |  | preHeatingCoil(\d{0,4})PumpPressureDelta | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | preheat,coil,water,pump,common,pressure,delta,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPumpPressureHiAlarm | preHeatingCoilXXXXPumpPressureHiAlarm | Pre-Heating Coil Pump Pressure High Alarm | Pre-Heating Coil XX Pump Pressure High Alarm |  | preHeatingCoil(\d{0,4})PumpPressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | preheat,coil,water,pump,pressure,high,alarm | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPumpPressureHiSp | preHeatingCoilXXXXPumpPressureHiSp | Pre-Heating Coil Pump Pressure High Setpoint | Pre-Heating Coil XX Pump Pressure High Setpoint |  | preHeatingCoil(\d{0,4})PumpPressureHiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | preheat,coil,water,pump,pressure,high,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPumpPressureLoAlarm | preHeatingCoilXXXXPumpPressureLoAlarm | Pre-Heating Coil Pump Pressure Low Alarm | Pre-Heating Coil XX Pump Pressure Low Alarm |  | preHeatingCoil(\d{0,4})PumpPressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | preheat,coil,water,pump,pressure,low,alarm | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPumpPressureLoSp | preHeatingCoilXXXXPumpPressureLoSp | Pre-Heating Coil Pump Pressure Low Setpoint | Pre-Heating Coil XX Pump Pressure Low Setpoint |  | preHeatingCoil(\d{0,4})PumpPressureLoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | preheat,coil,water,pump,pressure,low,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPumpRuntime | preHeatingCoilXXXXPumpRuntime | Pre-Heating Coil Pump Runtime | Pre-Heating Coil XX Pump Runtime |  | preHeatingCoil(\d{0,4})PumpRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPumpSpeed | preHeatingCoilXXXXPumpSpeed | Pre-Heating Coil Pump Speed | Pre-Heating Coil XX Pump Speed |  | preHeatingCoil(\d{0,4})PumpSpeed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | preheat,coil,water,pump,speed,cmd | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPumpSpeedFb | preHeatingCoilXXXXPumpSpeedFb | Pre-Heating Coil Pump Speed Feedback | Pre-Heating Coil XX Pump Speed Feedback |  | preHeatingCoil(\d{0,4})PumpSpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | preheat,coil,water,pump,speed,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPumpSpeedMaxSp | preHeatingCoilXXXXPumpSpeedMaxSp | Pre-Heating Coil Pump Speed Max Setpoint | Pre-Heating Coil XX Pump Speed Max Setpoint |  | preHeatingCoil(\d{0,4})PumpSpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | preheat,coil,water,pump,speed,max,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPumpSpeedMinSp | preHeatingCoilXXXXPumpSpeedMinSp | Pre-Heating Coil Pump Speed Min Setpoint | Pre-Heating Coil XX Pump Speed Min Setpoint |  | preHeatingCoil(\d{0,4})PumpSpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | preheat,coil,water,pump,speed,min,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPumpSpeedOvr | preHeatingCoilXXXXPumpSpeedOvr | Pre-Heating Coil Pump Speed Override | Pre-Heating Coil XX Pump Speed Override |  | preHeatingCoil(\d{0,4})PumpSpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | preheat,coil,water,pump,speed,ovr | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPumpSpeedSp | preHeatingCoilXXXXPumpSpeedSp | Pre-Heating Coil Pump Speed Setpoint | Pre-Heating Coil XX Pump Speed Setpoint |  | preHeatingCoil(\d{0,4})PumpSpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | preheat,coil,water,pump,speed,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilPumpStatus | preHeatingCoilXXXXPumpStatus | Pre-Heating Coil Pump Status | Pre-Heating Coil XX Pump Status |  | preHeatingCoil(\d{0,4})PumpStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | preheat,coil,water,pump,status,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilStrainerAlarm | preHeatingCoilXXXXStrainerAlarm | Pre-Heating Coil Strainer Alarm | Pre-Heating Coil Strainer XX Alarm |  | preHeatingCoil(\d{0,4})StrainerAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | preheat,water,strainer,alarm | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingCoilStrainerEnable | preHeatingCoilXXXXStrainerEnable | Pre-Heating Coil Strainer Enable | Pre-Heating Coil Strainer XX Enable |  | preHeatingCoil(\d{0,4})StrainerEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | preheat,water,strainer,enable,cmd | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingEnable | preHeatingEnable | Pre-Heating Enable Command | Pre-Heating Enable Command |  | preHeatingEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | preheat,enable,common,cmd | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingEnableDb | preHeatingEnableDb | Pre-Heating Enable Deadband | Pre-Heating Enable Deadband |  | preHeatingEnableDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | preheat,enable,deadband,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingEnableSp | preHeatingEnableSp | Pre-Heating Enable Setpoint | Pre-Heating Enable Setpoint |  | preHeatingEnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | preheat,enable,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingStageAlarm | preHeatingStageXXXXAlarm | Pre-Heating Stage Alarm | Pre-Heating Stage XX Alarm |  | preHeatingStage(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal |  |  |  |  | XX |  | preheat,alarm | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingStage | preHeatingStageXXXX | Pre-Heating Stage Command | Pre-Heating Stage XX Command |  | preHeatingStage(\d{0,4}) | Yes | Yes | No | Bool | On/Off | On/Off |  |  |  |  | XX |  | preheat,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingStageMod | preHeatingStageXXXXMod | Pre-Heating Stage Modulation | Pre-Heating Stage XX Modulation |  | preHeatingStage(\d{0,4})Mod | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 | XX |  | preheat,modulation,cmd | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
preHeatingValve | preHeatingValve | Pre-Heating Valve Command | Pre-Heating Valve Command |  | preHeatingValve | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | preheat,valve,position,cmd | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released)
preHeatingValveFb | preHeatingValveFb | Pre-Heating Valve Feedback | Pre-Heating Valve Feedback |  | preHeatingValveFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | preheat,valve,position,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released)
preHeatingValveOvr | preHeatingValveOvr | Pre-Heating Valve Override | Pre-Heating Valve Override |  | preHeatingValveOvr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | preheat,valve,position,ovr | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released)
precipitationRate | precipitationRate | Precipitation Rate | Precipitation Rate |  | precipitationRate | Yes | Yes | No | Number |  |  | millimeters_per_minute | millimeters_per_minute | 2 | 1 |  |  | precipitation,rate,sensor | WTHR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
precipitationStatus | precipitationStatus | Precipitation Status | Precipitation Status |  | precipitationStatus | Yes | Yes | No | Bool | Precipitation/No Precipitation | Precipitation/No Precipitation | [6 empty] | precipitation,status,sensor | WTHR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
precipitationTotalizer | precipitationTotalizer | Precipitation Totalizer | Precipitation Totalizer |  | precipitationTotalizer | Yes | Yes | Yes | Number |  |  | inch | millimeter | 2 | 1 |  |  | precipitation,total,sensor | WTHR | 2.14,2.15 (Released),2.16 (Pre-Release)
priBypassFlow | priBypassFlowXXXX | Primary Bypass Flow | Primary Bypass Flow XX |  | priBypassFlow(\d{0,4}) | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | primary,water,bypass,flow,sensor | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassFlowDb | priBypassFlowXXXXDb | Primary Bypass Flow Deadband | Primary Bypass Flow XX Deadband |  | priBypassFlow(\d{0,4})Db | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | primary,water,bypass,flow,deadband,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassFlowHiSp | priBypassFlowXXXXHiSp | Primary Bypass Flow High Setpoint | Primary Bypass Flow XX High Setpoint |  | priBypassFlow(\d{0,4})HiSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | primary,water,bypass,flow,high,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassFlowLoSp | priBypassFlowXXXXLoSp | Primary Bypass Flow Low Setpoint | Primary Bypass Flow XX Low Setpoint |  | priBypassFlow(\d{0,4})LoSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | primary,water,bypass,flow,low,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassFlowMaxSp | priBypassFlowXXXXMaxSp | Primary Bypass Flow Max Reset Setpoint | Primary Bypass Flow XX Max Reset Setpoint |  | priBypassFlow(\d{0,4})MaxSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | primary,water,bypass,flow,max,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassFlowMinSp | priBypassFlowXXXXMinSp | Primary Bypass Flow Min Reset Setpoint | Primary Bypass Flow XX Min Reset Setpoint |  | priBypassFlow(\d{0,4})MinSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | primary,water,bypass,flow,min,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassFlowSp | priBypassFlowXXXXSp | Primary Bypass Flow Setpoint | Primary Bypass Flow XX Setpoint |  | priBypassFlow(\d{0,4})Sp | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | primary,water,bypass,flow,effective,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassPumpAlarm | priBypassPumpXXXXAlarm | Primary Bypass Pump Alarm | Primary Bypass Pump XX Alarm |  | priBypassPump(\w{0,4}(?=[A-Z]¦$))Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | priBypass,water,pump,common,alarm | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassPumpAlarmReset | priBypassPumpXXXXAlarmReset | Primary Bypass Pump Alarm Reset | Primary Bypass Pump XX Alarm Reset |  | priBypassPump(\w{0,4}(?=[A-Z]¦$))AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | priBypass,water,pump,reset,alarm | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassPump | priBypassPumpXXXX | Primary Bypass Pump Command | Primary Bypass Pump XX Command |  | priBypassPump((?:(?!Lead)(?!Ovr)\w){0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | priBypass,water,pump,status,cmd | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassPumpCurrent | priBypassPumpXXXXCurrent | Primary Bypass Pump Current | Primary Bypass Pump XX Current |  | priBypassPump(\w{0,4}(?=[A-Z]¦$))Current | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | priBypass,water,pump,current,sensor | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassPumpEnable | priBypassPumpXXXXEnable | Primary Bypass Pump Enable | Primary Bypass Pump XX Enable |  | priBypassPump(\w{0,4}(?=[A-Z]¦$))Enable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | priBypass,water,pump,enable,cmd | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassPumpEnableDb | priBypassPumpXXXXEnableDb | Primary Bypass Pump Enable Deadband | Primary Bypass Pump XX Enable Deadband |  | priBypassPump(\w{0,4}(?=[A-Z]¦$))EnableDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | priBypass,water,pump,enable,deadband,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.15 (Released),2.16 (Pre-Release)
priBypassPumpEnableSp | priBypassPumpXXXXEnableSp | Primary Bypass Pump Enable Setpoint | Primary Bypass Pump XX Enable Setpoint |  | priBypassPump((?:(?!Lag)\w){0,4}(?=[A-Z]¦$))EnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | priBypass,water,pump,enable,effective,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.15 (Released),2.16 (Pre-Release)
priBypassPumpEnteringPressure | priBypassPumpXXXXEnteringPressure | Primary Bypass Pump Entering Pressure | Primary Bypass Pump XX Entering Pressure |  | priBypassPump(\w{0,4}(?=[A-Z]¦$))EnteringPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | priBypass,water,pump,entering,pressure,sensor | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassPumpFault | priBypassPumpXXXXFault | Primary Bypass Pump Fault | Primary Bypass Pump XX Fault |  | priBypassPump(\w{0,4}(?=[A-Z]¦$))Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | priBypass,water,pump,fault,common | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassPumpLagDisableSp | priBypassPumpXXXXLagDisableSp | Primary Bypass Pump Lag Disable Setpoint | Primary Bypass Pump XX Lag Disable Setpoint |  | priBypassPump(\w{0,4}(?=[A-Z]¦$))LagDisableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | priBypass,water,pump,lag,disable,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.15 (Released),2.16 (Pre-Release)
priBypassPumpLagEnableSp | priBypassPumpXXXXLagEnableSp | Primary Bypass Pump Lag Enable Setpoint | Primary Bypass Pump XX Lag Enable Setpoint |  | priBypassPump(\w{0,4}(?=[A-Z]¦$))LagEnableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | priBypass,water,pump,lag,enable,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.15 (Released),2.16 (Pre-Release)
priBypassPumpLagReq | priBypassPumpXXXXLagReq | Primary Bypass Pump Lag Request | Primary Bypass Pump XX Lag Request |  | priBypassPump(\w{0,4}(?=[A-Z]¦$))LagReq | No | No | No | Bool | Request/No Request | Request/No Request | [6 empty] | priBypass,water,pump,lag,request,cmd | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.15 (Released),2.16 (Pre-Release)
priBypassPumpLead | priBypassPumpLead | Primary Bypass Pump Lead | Primary Bypass Pump Lead |  | priBypassPumpLead | Yes | Yes | No | Bool | Lead 1/Lead 2 | Lead 1/Lead 2 | [6 empty] | priBypass,water,pump,lead,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassPumpLeadXor | priBypassPumpLeadXor | Primary Bypass Pump Lead Change Over | Primary Bypass Pump Lead Xor |  | priBypassPumpLeadXor | No | No | No | Bool | On/Off | On/Off | [6 empty] | priBypass,water,pump,lead,changeOver,cmd | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassPumpLeadXorRuntimeSp | priBypassPumpLeadXorRuntimeSp | Primary Bypass Pump Lead Change Over Runtime Setpoint | Primary Bypass Pump Lead Xor Runtime Setpoint |  | priBypassPumpLeadXorRuntimeSp | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassPumpLeavingPressure | priBypassPumpXXXXLeavingPressure | Primary Bypass Pump Leaving Pressure | Primary Bypass Pump XX Leaving Pressure |  | priBypassPump(\w{0,4}(?=[A-Z]¦$))LeavingPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | priBypass,water,pump,leaving,pressure,sensor | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassPumpMaintSwitch | priBypassPumpXXXXMaintSwitch | Primary Bypass Pump Maintenance Switch | Primary Bypass Pump XX Maintenance Switch |  | priBypassPump(\w{0,4}(?=[A-Z]¦$))MaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | priBypass,water,pump,maintenance,switch,cmd | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.15 (Released),2.16 (Pre-Release)
priBypassPumpOvr | priBypassPumpXXXXOvr | Primary Bypass Pump Override | Primary Bypass Pump XX Override |  | priBypassPump(\w{0,4}(?=[A-Z]¦$))Ovr | No | No | No | Bool | On/Off | On/Off | [6 empty] | priBypass,water,pump,status,ovr | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassPumpPressureDelta | priBypassPumpXXXXPressureDelta | Primary Bypass Pump Pressure Delta | Primary Bypass Pump XX Pressure Delta |  | priBypassPump(\w{0,4}(?=[A-Z]¦$))PressureDelta | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | priBypass,water,pump,common,pressure,delta,sensor | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassPumpPressureHiAlarm | priBypassPumpXXXXPressureHiAlarm | Primary Bypass Pump Pressure High Alarm | Primary Bypass Pump XX Pressure High Alarm |  | priBypassPump(\w{0,4}(?=[A-Z]¦$))PressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | priBypass,water,pump,pressure,high,alarm | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassPumpPressureHiSp | priBypassPumpXXXXPressureHiSp | Primary Bypass Pump Pressure High Setpoint | Primary Bypass Pump XX Pressure High Setpoint |  | priBypassPump(\w{0,4}(?=[A-Z]¦$))PressureHiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | priBypass,water,pump,pressure,high,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassPumpPressureLoAlarm | priBypassPumpXXXXPressureLoAlarm | Primary Bypass Pump Pressure Low Alarm | Primary Bypass Pump XX Pressure Low Alarm |  | priBypassPump(\w{0,4}(?=[A-Z]¦$))PressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | priBypass,water,pump,pressure,low,alarm | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassPumpPressureLoSp | priBypassPumpXXXXPressureLoSp | Primary Bypass Pump Pressure Low Setpoint | Primary Bypass Pump XX Pressure Low Setpoint |  | priBypassPump(\w{0,4}(?=[A-Z]¦$))PressureLoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | priBypass,water,pump,pressure,low,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassPumpRuntime | priBypassPumpXXXXRuntime | Primary Bypass Pump Runtime | Primary Bypass Pump XX Runtime |  | priBypassPump(\w{0,4}(?=[A-Z]¦$))Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.15 (Released),2.16 (Pre-Release)
priBypassPumpSpeed | priBypassPumpXXXXSpeed | Primary Bypass Pump Speed | Primary Bypass Pump XX Speed |  | priBypassPump(\w{0,4}(?=[A-Z]¦$))Speed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | priBypass,water,pump,speed,cmd | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassPumpSpeedFb | priBypassPumpXXXXSpeedFb | Primary Bypass Pump Speed Feedback | Primary Bypass Pump XX Speed Feedback |  | priBypassPump(\w{0,4}(?=[A-Z]¦$))SpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | priBypass,water,pump,speed,sensor | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassPumpSpeedMaxSp | priBypassPumpXXXXSpeedMaxSp | Primary Bypass Pump Speed Max Setpoint | Primary Bypass Pump XX Speed Max Setpoint |  | priBypassPump(\w{0,4}(?=[A-Z]¦$))SpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | priBypass,water,pump,speed,max,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassPumpSpeedMinSp | priBypassPumpXXXXSpeedMinSp | Primary Bypass Pump Speed Min Setpoint | Primary Bypass Pump XX Speed Min Setpoint |  | priBypassPump(\w{0,4}(?=[A-Z]¦$))SpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | priBypass,water,pump,speed,min,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassPumpSpeedOvr | priBypassPumpXXXXSpeedOvr | Primary Bypass Pump Speed Override | Primary Bypass Pump XX Speed Override |  | priBypassPump(\w{0,4}(?=[A-Z]¦$))SpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | priBypass,water,pump,speed,ovr | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassPumpSpeedSp | priBypassPumpXXXXSpeedSp | Primary Bypass Pump Speed Setpoint | Primary Bypass Pump XX Speed Setpoint |  | priBypassPump(\w{0,4}(?=[A-Z]¦$))SpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | priBypass,water,pump,speed,effective,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassPumpStatus | priBypassPumpXXXXStatus | Primary Bypass Pump Status | Primary Bypass Pump XX Status |  | priBypassPump(\w{0,4}(?=[A-Z]¦$))Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | priBypass,water,pump,status,sensor | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassTemp | priBypassTempXXXX | Primary Bypass Temperature | Primary Bypass Temperature XX |  | priBypassTemp(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | primary,water,bypass,temp,sensor | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassValveAlarm | priBypassValveXXXXAlarm | Primary Bypass Valve Alarm | Primary Bypass Valve XX Alarm |  | priBypassValve(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | primary,water,bypass,valve,position,alarm | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassValve | priBypassValveXXXX | Primary Bypass Valve Command | Primary Bypass Valve XX Command |  | priBypassValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | primary,water,bypass,valve,position,cmd | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priBypassValveFb | priBypassValveXXXXFb | Primary Bypass Valve Feedback | Primary Bypass Valve XX Feedback |  | priBypassValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | primary,water,bypass,valve,position,sensor | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priEnergy | priEnergy | Primary Energy | Primary Energy |  | priEnergy | Yes | Yes | No | Number |  |  | kilobtu | kilobtu | 0 | 0 |  |  | primary,water,energy,common,sensor | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priEnteringFlow | priEnteringFlowXXXX | Primary Entering Flow | Primary Entering Flow XX |  | priEnteringFlow(\d{0,4}) | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | primary,water,entering,flow,sensor | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priEnteringFlowDb | priEnteringFlowXXXXDb | Primary Entering Flow Deadband | Primary Entering Flow XX Deadband |  | priEnteringFlow(\d{0,4})Db | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | primary,water,entering,flow,deadband,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priEnteringFlowHiSp | priEnteringFlowXXXXHiSp | Primary Entering Flow High Setpoint | Primary Entering Flow XX High Setpoint |  | priEnteringFlow(\d{0,4})HiSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | primary,water,entering,flow,high,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priEnteringFlowLoSp | priEnteringFlowXXXXLoSp | Primary Entering Flow Low Setpoint | Primary Entering Flow XX Low Setpoint |  | priEnteringFlow(\d{0,4})LoSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | primary,water,entering,flow,low,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priEnteringFlowMaxSp | priEnteringFlowXXXXMaxSp | Primary Entering Flow Max Setpoint | Primary Entering Flow XX Max Setpoint |  | priEnteringFlow(\d{0,4})MaxSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | primary,water,entering,flow,max,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priEnteringFlowMinSp | priEnteringFlowXXXXMinSp | Primary Entering Flow Min Setpoint | Primary Entering Flow XX Min Setpoint |  | priEnteringFlow(\d{0,4})MinSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | primary,water,entering,flow,min,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priEnteringFlowSp | priEnteringFlowXXXXSp | Primary Entering Flow Setpoint | Primary Entering Flow XX Setpoint |  | priEnteringFlow(\d{0,4})Sp | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | primary,water,entering,flow,effective,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priEnteringIsoValve | priEnteringIsoValveXXXX | Primary Entering Isolation Valve Command | Primary Entering Isolation Valve XX Command |  | priEnteringIsoValve(\d{0,4}) | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | primary,water,iso,entering,valve,position,cmd | GEO,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priEnteringIsoValveFb | priEnteringIsoValveXXXXFb | Primary Entering Isolation Valve Feedback | Primary Entering Isolation Valve XX Feedback |  | priEnteringIsoValve(\d{0,4})Fb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | primary,water,iso,entering,valve,position,sensor | GEO,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priEnteringPressure | priEnteringPressureXXXX | Primary Entering Pressure | Primary Entering Pressure XX |  | priEnteringPressure(\d{0,4}) | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | primary,water,entering,pressure,general,sensor | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priEnteringPressureDb | priEnteringPressureXXXXDb | Primary Entering Pressure Deadband | Primary Entering Pressure XX Deadband |  | priEnteringPressure(\d{0,4})Db | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | primary,water,entering,pressure,deadband,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priEnteringPressureHiAlarm | priEnteringPressureXXXXHiAlarm | Primary Entering Pressure High Alarm | Primary Entering Pressure XX High Alarm |  | priEnteringPressure(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | primary,water,entering,pressure,alarm,high | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.14,2.15 (Released),2.16 (Pre-Release)
priEnteringPressureHiSp | priEnteringPressureXXXXHiSp | Primary Entering Pressure High Setpoint | Primary Entering Pressure XX High Setpoint |  | priEnteringPressure(\d{0,4})HiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | primary,water,entering,pressure,high,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priEnteringPressureLoAlarm | priEnteringPressureXXXXLoAlarm | Primary Entering Pressure Low Alarm | Primary Entering Pressure XX Low Alarm |  | priEnteringPressure(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | primary,water,entering,pressure,low,alarm | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priEnteringPressureLoSp | priEnteringPressureXXXXLoSp | Primary Entering Pressure Low Setpoint | Primary Entering Pressure XX Low Setpoint |  | priEnteringPressure(\d{0,4})LoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | primary,water,entering,pressure,low,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priEnteringPressureMaxSp | priEnteringPressureXXXXMaxSp | Primary Entering Pressure Max Reset Setpoint | Primary Entering Pressure XX Max Reset Setpoint |  | priEnteringPressure(\d{0,4})MaxSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | primary,water,entering,pressure,max,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priEnteringPressureMinSp | priEnteringPressureXXXXMinSp | Primary Entering Pressure Min Reset Setpoint | Primary Entering Pressure XX Min Reset Setpoint |  | priEnteringPressure(\d{0,4})MinSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | primary,water,entering,pressure,min,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priEnteringPressureSp | priEnteringPressureXXXXSp | Primary Entering Pressure Setpoint | Primary Entering Pressure XX Setpoint |  | priEnteringPressure(\d{0,4})Sp | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | primary,water,entering,pressure,effective,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priEnteringTemp | priEnteringTempXXXX | Primary Entering Temperature | Primary Entering Temperature XX |  | priEnteringTemp(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | primary,water,entering,temp,sensor | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priEnteringTempDb | priEnteringTempXXXXDb | Primary Entering Temperature Deadband | Primary Entering Temperature XX Deadband |  | priEnteringTemp(\d{0,4})Db | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | primary,water,entering,temp,deadband,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priEnteringTempHiAlarm | priEnteringTempXXXXHiAlarm | Primary Entering Temperature High Alarm | Primary Entering Temperature XX High Alarm |  | priEnteringTemp(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | primary,water,entering,temp,high,alarm | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priEnteringTempHiSp | priEnteringTempXXXXHiSp | Primary Entering Temperature High Setpoint | Primary Entering Temperature XX High Setpoint |  | priEnteringTemp(\d{0,4})HiSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | primary,water,entering,temp,high,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priEnteringTempLoAlarm | priEnteringTempXXXXLoAlarm | Primary Entering Temperature Low Alarm | Primary Entering Temperature XX Low Alarm |  | priEnteringTemp(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | primary,water,entering,temp,low,alarm | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priEnteringTempLoSp | priEnteringTempXXXXLoSp | Primary Entering Temperature Low Setpoint | Primary Entering Temperature XX Low Setpoint |  | priEnteringTemp(\d{0,4})LoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | primary,water,entering,temp,low,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priEnteringTempMaxSp | priEnteringTempXXXXMaxSp | Primary Entering Temperature Max Reset Setpoint | Primary Entering Temperature XX Max Reset Setpoint |  | priEnteringTemp(\d{0,4})MaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | primary,water,entering,temp,max,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priEnteringTempMinSp | priEnteringTempXXXXMinSp | Primary Entering Temperature Min Reset Setpoint | Primary Entering Temperature XX Min Reset Setpoint |  | priEnteringTemp(\d{0,4})MinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | primary,water,entering,temp,min,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priEnteringTempSp | priEnteringTempXXXXSp | Primary Entering Temperature Setpoint | Primary Entering Temperature XX Setpoint |  | priEnteringTemp(\d{0,4})Sp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | primary,water,entering,temp,effective,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priEnteringValveAlarm | priEnteringValveXXXXAlarm | Primary Entering Valve Alarm | Primary Entering Valve XX Alarm |  | priEnteringValve(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | primary,water,entering,valve,common,position,alarm | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priEnteringValve | priEnteringValveXXXX | Primary Entering Valve Command | Primary Entering Valve XX Command |  | priEnteringValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | primary,water,entering,valve,common,position,sensor | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priEnteringValveFb | priEnteringValveXXXXFb | Primary Entering Valve Feedback | Primary Entering Valve XX Feedback |  | priEnteringValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | primary,water,entering,valve,common,position,cmd | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priFilterAlarm | priFilterXXXXAlarm | Primary Filter Alarm | Primary Filter XX Alarm |  | priFilter(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | primary,water,filter,common,alarm | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priFilterAlarmReset | priFilterXXXXAlarmReset | Primary Filter Alarm Reset | Primary Filter XX Alarm Reset |  | priFilter(\d{0,4})AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | primary,water,filter,reset,alarm | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priFilterEnable | priFilterXXXXEnable | Primary Filter Enable | Primary Filter XX Enable |  | priFilter(\d{0,4})Enable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | primary,water,filter,enable,cmd | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priFilterPressureDelta | priFilterXXXXPressureDelta | Primary Filter Pressure Delta | Primary Filter XX Pressure Delta |  | priFilter(\d{0,4})PressureDelta | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | primary,water,filter,pressure,delta,sensor | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priFilterPumpStatus | priFilterXXXXPumpStatus | Primary Filter Pump Status | Primary Filter XX Pump Status |  | priFilter(\d{0,4})PumpStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | primary,water,filter,pump,status,sensor | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priFlowStatus | priFlowXXXXStatus | Primary Flow Status | Primary Flow XX Status |  | priFlow(\d{0,4})Status | Yes | Yes | No | Bool | Flow/No Flow | Flow/No Flow | [6 empty] | primary,water,flow,status,sensor | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingFlow | priLeavingFlowXXXX | Primary Leaving Flow | Primary Leaving Flow XX |  | priLeavingFlow(\d{0,4}) | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | primary,water,leaving,flow,sensor | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingFlowDb | priLeavingFlowXXXXDb | Primary Leaving Flow Deadband | Primary Leaving Flow XX Deadband |  | priLeavingFlow(\d{0,4})Db | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | primary,water,leaving,flow,deadband,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingFlowHiSp | priLeavingFlowXXXXHiSp | Primary Leaving Flow High Setpoint | Primary Leaving Flow XX High Setpoint |  | priLeavingFlow(\d{0,4})HiSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | primary,water,leaving,flow,high,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingFlowLoSp | priLeavingFlowXXXXLoSp | Primary Leaving Flow Low Setpoint | Primary Leaving Flow XX Low Setpoint |  | priLeavingFlow(\d{0,4})LoSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | primary,water,leaving,flow,low,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingFlowMaxSp | priLeavingFlowXXXXMaxSp | Primary Leaving Flow Max Setpoint | Primary Leaving Flow XX Max Setpoint |  | priLeavingFlow(\d{0,4})MaxSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | primary,water,leaving,flow,max,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingFlowMinSp | priLeavingFlowXXXXMinSp | Primary Leaving Flow Min Setpoint | Primary Leaving Flow XX Min Setpoint |  | priLeavingFlow(\d{0,4})MinSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | primary,water,leaving,flow,min,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingFlowSp | priLeavingFlowXXXXSp | Primary Leaving Flow Setpoint | Primary Leaving Flow XX Setpoint |  | priLeavingFlow(\d{0,4})Sp | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | primary,water,leaving,flow,effective,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingIsoValve | priLeavingIsoValveXXXX | Primary Leaving Isolation Valve Command | Primary Leaving Isolation Valve XX Command |  | priLeavingIsoValve(\d{0,4}) | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | primary,water,iso,leaving,valve,position,cmd | GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingIsoValveFb | priLeavingIsoValveXXXXFb | Primary Leaving Isolation Valve Feedback | Primary Leaving Isolation Valve XX Feedback |  | priLeavingIsoValve(\d{0,4})Fb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | primary,water,iso,leaving,valve,position,sensor | GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingPressure | priLeavingPressureXXXX | Primary Leaving Pressure | Primary Leaving Pressure XX |  | priLeavingPressure(\d{0,4}) | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | primary,water,leaving,pressure,general,sensor | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingPressureDb | priLeavingPressureXXXXDb | Primary Leaving Pressure Deadband | Primary Leaving Pressure XX Deadband |  | priLeavingPressure(\d{0,4})Db | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | primary,water,leaving,pressure,deadband,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingPressureHiAlarm | priLeavingPressureXXXXHiAlarm | Primary Leaving Pressure High Alarm | Primary Leaving Pressure XX High Alarm |  | priLeavingPressure(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | primary,water,leaving,pressure,high,alarm | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingPressureHiSp | priLeavingPressureXXXXHiSp | Primary Leaving Pressure High Setpoint | Primary Leaving Pressure XX High Setpoint |  | priLeavingPressure(\d{0,4})HiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | primary,water,leaving,pressure,high,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingPressureLoAlarm | priLeavingPressureXXXXLoAlarm | Primary Leaving Pressure Low Alarm | Primary Leaving Pressure XX Low Alarm |  | priLeavingPressure(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | primary,water,leaving,pressure,low,alarm | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingPressureLoSp | priLeavingPressureXXXXLoSp | Primary Leaving Pressure Low Setpoint | Primary Leaving Pressure XX Low Setpoint |  | priLeavingPressure(\d{0,4})LoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | primary,water,leaving,pressure,low,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingPressureMaxSp | priLeavingPressureXXXXMaxSp | Primary Leaving Pressure Max Reset Setpoint | Primary Leaving Pressure XX Max Reset Setpoint |  | priLeavingPressure(\d{0,4})MaxSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | primary,water,leaving,pressure,max,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingPressureMinSp | priLeavingPressureXXXXMinSp | Primary Leaving Pressure Min Reset Setpoint | Primary Leaving Pressure XX Min Reset Setpoint |  | priLeavingPressure(\d{0,4})MinSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | primary,water,leaving,pressure,min,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingPressureSp | priLeavingPressureXXXXSp | Primary Leaving Pressure Setpoint | Primary Leaving Pressure XX Setpoint |  | priLeavingPressure(\d{0,4})Sp | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | primary,water,leaving,pressure,effective,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingTemp | priLeavingTempXXXX | Primary Leaving Temperature | Primary Leaving Temperature XX |  | priLeavingTemp(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | primary,water,leaving,temp,sensor | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingTempDb | priLeavingTempXXXXDb | Primary Leaving Temperature Deadband | Primary Leaving Temperature XX Deadband |  | priLeavingTemp(\d{0,4})Db | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | primary,water,leaving,temp,deadband,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingTempFault | priLeavingTempXXXXFault | Primary Leaving Temperature Fault | Primary Leaving Temperature XX Fault |  | priLeavingTemp(\d{0,4})Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | primary,water,leaving,temp,fault | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingTempHiAlarm | priLeavingTempXXXXHiAlarm | Primary Leaving Temperature High Alarm | Primary Leaving Temperature XX High Alarm |  | priLeavingTemp(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | primary,water,leaving,temp,high,alarm | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingTempHiSp | priLeavingTempXXXXHiSp | Primary Leaving Temperature High Setpoint | Primary Leaving Temperature XX High Setpoint |  | priLeavingTemp(\d{0,4})HiSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | primary,water,leaving,temp,high,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingTempLoAlarm | priLeavingTempXXXXLoAlarm | Primary Leaving Temperature Low Alarm | Primary Leaving Temperature XX Low Alarm |  | priLeavingTemp(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | primary,water,leaving,temp,low,alarm | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingTempLoSp | priLeavingTempXXXXLoSp | Primary Leaving Temperature Low Setpoint | Primary Leaving Temperature XX Low Setpoint |  | priLeavingTemp(\d{0,4})LoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | primary,water,leaving,temp,low,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingTempMaxSp | priLeavingTempXXXXMaxSp | Primary Leaving Temperature Max Reset Setpoint | Primary Leaving Temperature XX Max Reset Setpoint |  | priLeavingTemp(\d{0,4})MaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | primary,water,leaving,temp,max,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingTempMinSp | priLeavingTempXXXXMinSp | Primary Leaving Temperature Min Reset Setpoint | Primary Leaving Temperature XX Min Reset Setpoint |  | priLeavingTemp(\d{0,4})MinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | primary,water,leaving,temp,min,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingTempOccSp | priLeavingTempXXXXOccSp | Primary Leaving Temperature Occupied Setpoint | Primary Leaving Temperature XX Occupied Setpoint |  | priLeavingTemp(\d{0,4})OccSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | primary,water,leaving,temp,occupied,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingTempSp | priLeavingTempXXXXSp | Primary Leaving Temperature Setpoint | Primary Leaving Temperature XX Setpoint |  | priLeavingTemp(\d{0,4})Sp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | primary,water,leaving,temp,effective,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingTempSpMode | priLeavingTempXXXXSpMode | Primary Leaving Temperature Setpoint Mode | Primary Leaving Temperature XX Setpoint Mode |  | priLeavingTemp(\d{0,4})SpMode | No | No | No | Bool | Reset/Fixed | Reset/Fixed | [6 empty] | primary,water,leaving,temp,mode,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingTempUnoccSp | priLeavingTempXXXXUnoccSp | Primary Leaving Temperature Unoccupied Setpoint | Primary Leaving Temperature XX Unoccupied Setpoint |  | priLeavingTemp(\d{0,4})UnoccSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | primary,water,leaving,temp,unoccupied,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingValveAlarm | priLeavingValveXXXXAlarm | Primary Leaving Valve Alarm | Primary Leaving Valve XX Alarm |  | priLeavingValve(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | primary,water,leaving,valve,common,position,alarm | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingValve | priLeavingValveXXXX | Primary Leaving Valve Command | Primary Leaving Valve XX Command |  | priLeavingValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | primary,water,leaving,valve,common,position,cmd | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priLeavingValveFb | priLeavingValveXXXXFb | Primary Leaving Valve Feedback | Primary Leaving Valve XX Feedback |  | priLeavingValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | primary,water,leaving,valve,common,position,sensor | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priMixingValve | priMixingValveXXXX | Primary Mixing Valve Command | Primary Mixing Valve XX Command |  | priMixingValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | primary,water,mixing,valve,position,cmd | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priMixingValveFb | priMixingValveXXXXFb | Primary Mixing Valve Feedback | Primary Mixing Valve XX Feedback |  | priMixingValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | primary,water,mixing,valve,position,sensor | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPower | priPower | Primary Power | Primary Power |  | priPower | Yes | Yes | No | Number |  |  | kilobtus_per_hour | kilobtus_per_hour | 1 | 1 |  |  | primary,water,power,common,sensor | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPressureDelta | priPressureDeltaXXXX | Primary Pressure Differential | Primary Pressure Differential XX |  | priPressureDelta(\d{0,4}) | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | primary,water,common,delta,pressure,general,sensor | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPressureDeltaDb | priPressureDeltaXXXXDb | Primary Pressure Differential Deadband | Primary Pressure Differential XX Deadband |  | priPressureDelta(\d{0,4})Db | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | primary,water,common,delta,pressure,deadband,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPressureDeltaHiAlarm | priPressureDeltaXXXXHiAlarm | Primary Pressure Differential High Alarm | Primary Pressure Differential XX High Alarm |  | priPressureDelta(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | primary,water,common,delta,pressure,high,alarm | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPressureDeltaHiSp | priPressureDeltaXXXXHiSp | Primary Pressure Differential High Setpoint | Primary Pressure Differential XX High Setpoint |  | priPressureDelta(\d{0,4})HiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | primary,water,common,delta,pressure,high,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPressureDeltaLoAlarm | priPressureDeltaXXXXLoAlarm | Primary Pressure Differential Low Alarm | Primary Pressure Differential XX Low Alarm |  | priPressureDelta(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | primary,water,common,delta,pressure,low,alarm | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPressureDeltaLoSp | priPressureDeltaXXXXLoSp | Primary Pressure Differential Low Setpoint | Primary Pressure Differential XX Low Setpoint |  | priPressureDelta(\d{0,4})LoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | primary,water,common,delta,pressure,low,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPressureDeltaMaxSp | priPressureDeltaXXXXMaxSp | Primary Pressure Differential Max Reset Setpoint | Primary Pressure Differential XX Max Reset Setpoint |  | priPressureDelta(\d{0,4})MaxSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | primary,water,common,delta,pressure,max,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPressureDeltaMinSp | priPressureDeltaXXXXMinSp | Primary Pressure Differential Min Reset Setpoint | Primary Pressure Differential XX Min Reset Setpoint |  | priPressureDelta(\d{0,4})MinSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | primary,water,common,delta,pressure,min,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPressureDeltaSp | priPressureDeltaXXXXSp | Primary Pressure Differential Setpoint | Primary Pressure Differential XX Setpoint |  | priPressureDelta(\d{0,4})Sp | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | primary,water,common,delta,pressure,effective,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPumpAlarm | priPumpXXXXAlarm | Primary Pump Alarm | Primary Pump XX Alarm |  | priPump(\w{0,4}(?=[A-Z]¦$))Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | primary,water,pump,common,alarm | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPumpAlarmReset | priPumpXXXXAlarmReset | Primary Pump Alarm Reset | Primary Pump XX Alarm Reset |  | priPump(\w{0,4}(?=[A-Z]¦$))AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | primary,water,pump,reset,alarm | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPump | priPumpXXXX | Primary Pump Command | Primary Pump XX Command |  | priPump((?:(?!Lead)(?!Ovr)\w){0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | primary,water,pump,status,cmd | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPumpCurrent | priPumpXXXXCurrent | Primary Pump Current | Primary Pump XX Current |  | priPump(\w{0,4}(?=[A-Z]¦$))Current | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | primary,water,pump,current,sensor | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPumpEnable | priPumpXXXXEnable | Primary Pump Enable | Primary Pump XX Enable |  | priPump(\w{0,4}(?=[A-Z]¦$))Enable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | primary,water,pump,enable,cmd | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPumpEnableDb | priPumpXXXXEnableDb | Primary Pump Enable Deadband | Primary Pump XX Enable Deadband |  | priPump(\w{0,4}(?=[A-Z]¦$))EnableDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | primary,water,pump,enable,deadband,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.15 (Released),2.16 (Pre-Release)
priPumpEnableSp | priPumpXXXXEnableSp | Primary Pump Enable Setpoint | Primary Pump XX Enable Setpoint |  | priPump((?:(?!Lag)\w){0,4}(?=[A-Z]¦$))EnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | primary,water,pump,enable,effective,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.15 (Released),2.16 (Pre-Release)
priPumpEnteringPressure | priPumpXXXXEnteringPressure | Primary Pump Entering Pressure | Primary Pump XX Entering Pressure |  | priPump(\w{0,4}(?=[A-Z]¦$))EnteringPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | primary,water,pump,entering,pressure,sensor | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPumpFault | priPumpXXXXFault | Primary Pump Fault | Primary Pump XX Fault |  | priPump(\w{0,4}(?=[A-Z]¦$))Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | primary,water,pump,fault,common | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPumpLagDisableSp | priPumpXXXXLagDisableSp | Primary Pump Lag Disable Setpoint | Primary Pump XX Lag Disable Setpoint |  | priPump(\w{0,4}(?=[A-Z]¦$))LagDisableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | primary,water,pump,lag,disable,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPumpLagEnableSp | priPumpXXXXLagEnableSp | Primary Pump Lag Enable Setpoint | Primary Pump XX Lag Enable Setpoint |  | priPump(\w{0,4}(?=[A-Z]¦$))LagEnableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | primary,water,pump,lag,enable,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPumpLagReq | priPumpXXXXLagReq | Primary Pump Lag Request | Primary Pump XX Lag Request |  | priPump(\w{0,4}(?=[A-Z]¦$))LagReq | No | No | No | Bool | Request/No Request | Request/No Request | [6 empty] | primary,water,pump,lag,request,cmd | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPumpLead | priPumpLead | Primary Pump Lead | Primary Pump Lead |  | priPumpLead | Yes | Yes | No | Bool | Lead 1/Lead 2 | Lead 1/Lead 2 | [6 empty] | primary,water,pump,lead,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPumpLeadXor | priPumpLeadXor | Primary Pump Lead Change Over | Primary Pump Lead Change Over |  | priPumpLeadXor | No | No | No | Bool | On/Off | On/Off | [6 empty] | primary,water,pump,lead,changeOver,common,cmd | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.15 (Released),2.16 (Pre-Release)
priPumpLeadXorDay | priPumpLeadXorDay | Primary Pump Lead Change Over Day | Primary Pump Lead Change Over Day |  | priPumpLeadXorDay | No | No | No | Number |  | Sun,Mon,Tue,Wed,Thur,Fri,Sat | day | day | 0 | 0 |  |  | primary,water,pump,lead,changeOver,day,cmd | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.15 (Released),2.16 (Pre-Release)
priPumpLeadXorHour | priPumpLeadXorHour | Primary Pump Lead Change Over Hour | Primary Pump Lead Change Over Hour |  | priPumpLeadXorHour | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | primary,water,pump,lead,changeOver,hour,cmd | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.15 (Released),2.16 (Pre-Release)
priPumpLeadXorMode | priPumpLeadXorMode | Primary Pump Lead Change Over Mode | Primary Pump Lead Change Over Mode |  | priPumpLeadXorMode | No | No | No | Str |  | 1Week/2Week/3Week/4Week | [6 empty] | primary,water,pump,lead,changeOver,mode,cmd | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.15 (Released),2.16 (Pre-Release)
priPumpLeadXorRuntimeSp | priPumpLeadXorRuntimeSp | Primary Pump Lead Change Over Runtime Setpoint | Primary Pump Lead Change Over Runtime Setpoint |  | priPumpLeadXorRuntimeSp | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPumpLeavingPressure | priPumpXXXXLeavingPressure | Primary Pump Leaving Pressure | Primary Pump XX Leaving Pressure |  | priPump(\w{0,4}(?=[A-Z]¦$))LeavingPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | primary,water,pump,leaving,pressure,sensor | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPumpMaint | priPumpXXXXMaint | Primary Pump Maintenance | Primary Pump XX Maintenance |  | priPump(\w{0,4}(?=[A-Z]¦$))Maint | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | primary,water,pump,maintenance,common,cmd | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.15 (Released),2.16 (Pre-Release)
priPumpMaintSwitch | priPumpXXXXMaintSwitch | Primary Pump Maintenance Switch | Primary Pump XX Maintenance Switch |  | priPump(\w{0,4}(?=[A-Z]¦$))MaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | primary,water,pump,maintenance,switch,cmd | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.15 (Released),2.16 (Pre-Release)
priPumpOvr | priPumpXXXXOvr | Primary Pump Override | Primary Pump XX Override |  | priPump(\w{0,4}(?=[A-Z]¦$))Ovr | No | No | No | Bool | On/Off | On/Off | [6 empty] | primary,water,pump,status,ovr | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPumpPressureDelta | priPumpXXXXPressureDelta | Primary Pump Pressure Delta | Primary Pump XX Pressure Delta |  | priPump(\w{0,4}(?=[A-Z]¦$))PressureDelta | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | primary,water,pump,common,pressure,delta,sensor | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPumpPressureHiAlarm | priPumpXXXXPressureHiAlarm | Primary Pump Pressure High Alarm | Primary Pump XX Pressure High Alarm |  | priPump(\w{0,4}(?=[A-Z]¦$))PressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | primary,water,pump,pressure,high,alarm | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPumpPressureHiSp | priPumpXXXXPressureHiSp | Primary Pump Pressure High Setpoint | Primary Pump XX Pressure High Setpoint |  | priPump(\w{0,4}(?=[A-Z]¦$))PressureHiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | primary,water,pump,pressure,high,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPumpPressureLoAlarm | priPumpXXXXPressureLoAlarm | Primary Pump Pressure Low Alarm | Primary Pump XX Pressure Low Alarm |  | priPump(\w{0,4}(?=[A-Z]¦$))PressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | primary,water,pump,pressure,low,alarm | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPumpPressureLoSp | priPumpXXXXPressureLoSp | Primary Pump Pressure Low Setpoint | Primary Pump XX Pressure Low Setpoint |  | priPump(\w{0,4}(?=[A-Z]¦$))PressureLoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | primary,water,pump,pressure,low,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPumpRuntime | priPumpXXXXRuntime | Primary Pump Runtime | Primary Pump XX Runtime |  | priPump(\w{0,4}(?=[A-Z]¦$))Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.15 (Released),2.16 (Pre-Release)
priPumpSpeed | priPumpXXXXSpeed | Primary Pump Speed | Primary Pump XX Speed |  | priPump(\w{0,4}(?=[A-Z]¦$))Speed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | primary,water,pump,speed,cmd | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPumpSpeedFb | priPumpXXXXSpeedFb | Primary Pump Speed Feedback | Primary Pump XX Speed Feedback |  | priPump(\w{0,4}(?=[A-Z]¦$))SpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | primary,water,pump,speed,sensor | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPumpSpeedMaxSp | priPumpXXXXSpeedMaxSp | Primary Pump Speed Max Setpoint | Primary Pump XX Speed Max Setpoint |  | priPump(\w{0,4}(?=[A-Z]¦$))SpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | primary,water,pump,speed,max,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPumpSpeedMinSp | priPumpXXXXSpeedMinSp | Primary Pump Speed Min Setpoint | Primary Pump XX Speed Min Setpoint |  | priPump(\w{0,4}(?=[A-Z]¦$))SpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | primary,water,pump,speed,min,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPumpSpeedOvr | priPumpXXXXSpeedOvr | Primary Pump Speed Override | Primary Pump XX Speed Override |  | priPump(\w{0,4}(?=[A-Z]¦$))SpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | primary,water,pump,speed,ovr | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPumpSpeedSp | priPumpXXXXSpeedSp | Primary Pump Speed Setpoint | Primary Pump XX Speed Setpoint |  | priPump(\w{0,4}(?=[A-Z]¦$))SpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | primary,water,pump,speed,effective,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPumpStage | priPumpStage | Primary Pump Stage Command | Primary Pump Stage Command |  | priPumpStage | No | No | No | Number |  |  |  |  | 0 | 0 |  |  | primary,water,pump,staging,cmd | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.14,2.15 (Released),2.16 (Pre-Release)
priPumpStageDownDelayOnSp | priPumpStageDownDelayOnSp | Primary Pump Stage Down Delay On Septoint | Primary Pump Stage Down Delay On Septoint |  | priPumpStageDownDelayOnSp | No | No | No | Number |  |  | minute | minute | 0 | 0 |  |  | primary,water,pump,stageDown,delay,on,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPumpStageDownSp | priPumpStageDownSp | Primary Pump Stage Down Septoint | Primary Pump Stage Down Septoint |  | priPumpStageDownSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | primary,water,pump,stageDown,effective,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPumpStageUpDelayOnSp | priPumpStageUpDelayOnSp | Primary Pump Stage Up Delay On Septoint | Primary Pump Stage Up Delay On Septoint |  | priPumpStageUpDelayOnSp | No | No | No | Number |  |  | minute | minute | 0 | 0 |  |  | primary,water,pump,stageUp,delay,on,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPumpStageUpSp | priPumpStageUpSp | Primary Pump Stage Up Septoint | Primary Pump Stage Up Septoint |  | priPumpStageUpSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | primary,water,pump,stageUp,effective,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priPumpStatus | priPumpXXXXStatus | Primary Pump Status | Primary Pump XX Status |  | priPump(\w{0,4}(?=[A-Z]¦$))Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | primary,water,pump,status,sensor,common | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priStrainerAlarm | priStrainerAlarm | Primary Strainer Alarm | Primary Strainer Alarm |  | priStrainerAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | primary,water,strainer,alarm | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priStrainerEnable | priStrainerEnable | Primary Strainer Enable | Primary Strainer Enable |  | priStrainerEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | primary,water,strainer,enable,cmd | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priTempDelta | priTempDeltaXXXX | Primary Temperature Delta | Primary Temperature Delta XX |  | priTempDelta(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | primary,water,delta,temp,sensor | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priTempDeltaSp | priTempDeltaXXXXSp | Primary Temperature Delta Setpoint | Primary Temperature Delta XX Setpoint |  | priTempDelta(\d{0,4})Sp | Yes | Yes | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | primary,water,delta,temp,effective,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priTempDeltaDb | priTempDeltaXXXXDb | Primary Temperature Differential Deadband | Primary Temperature Differential XX Deadband |  | priTempDelta(\d{0,4})Db | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | primary,water,delta,temp,deadband,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priTempDeltaHiSp | priTempDeltaXXXXHiSp | Primary Temperature Differential High Setpoint | Primary Temperature Differential XX High Setpoint |  | priTempDelta(\d{0,4})HiSp | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | primary,water,delta,temp,high,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priTempDeltaLoSp | priTempDeltaXXXXLoSp | Primary Temperature Differential Low Setpoint | Primary Temperature Differential XX Low Setpoint |  | priTempDelta(\d{0,4})LoSp | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | primary,water,delta,temp,low,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priTempDeltaMaxSp | priTempDeltaXXXXMaxSp | Primary Temperature Differential Max Reset Setpoint | Primary Temperature Differential XX Max Reset Setpoint |  | priTempDelta(\d{0,4})MaxSp | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | primary,water,delta,temp,max,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priTempDeltaMinSp | priTempDeltaXXXXMinSp | Primary Temperature Differential Min Reset Setpoint | Primary Temperature Differential XX Min Reset Setpoint |  | priTempDelta(\d{0,4})MinSp | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | primary,water,delta,temp,min,sp | CWS,GEO,HWS,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priValveOneThird | priValveOneThird | Primary Valve 1/3 Command | Primary Valve 1/3 Command |  | priValveOneThird | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | primary,water,oneThird,valve,position,cmd | GEO,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priValveOneThirdFb | priValveOneThirdFb | Primary Valve 1/3 Feedback | Primary Valve 1/3 Feedback |  | priValveOneThirdFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | primary,water,oneThird,valve,position,sensor | GEO,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priValveTwoThird | priValveTwoThird | Primary Valve 2/3 Command | Primary Valve 2/3 Command |  | priValveTwoThird | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | primary,water,twoThird,valve,position,cmd | GEO,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priValveTwoThirdFb | priValveTwoThirdFb | Primary Valve 2/3 Feedback | Primary Valve 2/3 Feedback |  | priValveTwoThirdFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | primary,water,twoThird,valve,position,sensor | GEO,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priValve | priValveXXXX | Primary Valve Command | Primary Valve XX Command |  | priValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | primary,water,general,valve,position,cmd | GEO,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
priValveFb | priValveXXXXFb | Primary Valve Feedback | Primary Valve XX Feedback |  | priValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | primary,water,general,valve,position,sensor | GEO,PWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
pullStation | pullStation | Pull Station | Pull Station |  | pullStation | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | pullStation,sensor | DOOR,SEC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
pulse | pulse | Pulse Input | Pulse Input |  | pulse | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | pulse,sensor | CM,DCWS,DHWS,GM,PM,PRLY,PV,VGM,VPM,WH | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
pumpAlarm | pumpXXXXAlarm | Pump Alarm | Pump XX Alarm |  | pump(\w{0,4}(?=[A-Z]¦$))Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | general,water,pump,common,alarm | DCWS,DHWS,PMP,ROS,WSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
pumpAlarmReset | pumpXXXXAlarmReset | Pump Alarm Reset | Pump XX Alarm Reset |  | pump(\w{0,4}(?=[A-Z]¦$))AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | general,water,pump,reset,alarm | DCWS,DHWS,PMP,ROS,WSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
pump | pumpXXXX | Pump Command | Pump XX Command |  | pump((?:(?!Lead)(?!Ovr)\w){0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | general,water,pump,status,cmd | DCWS,DHWS,PMP,ROS,WSS | 2.15 (Released),2.16 (Pre-Release)
pumpCurrent | pumpXXXXCurrent | Pump Current | Pump XX Current |  | pump(\w{0,4}(?=[A-Z]¦$))Current | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | general,water,pump,current,sensor | DCWS,DHWS,PMP,ROS,WSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
pumpEnable | pumpXXXXEnable | Pump Enable | Pump XX Enable |  | pump(\w{0,4}(?=[A-Z]¦$))Enable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | general,water,pump,enable,cmd | DCWS,DHWS,PMP,ROS,WSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
pumpEnableDb | pumpXXXXEnableDb | Pump Enable Deadband | Pump XX Enable Deadband |  | pump(\w{0,4}(?=[A-Z]¦$))EnableDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | general,water,pump,enable,deadband,sp | DCWS,DHWS,PMP,ROS,WSS | 2.15 (Released),2.16 (Pre-Release)
pumpEnableSp | pumpXXXXEnableSp | Pump Enable Setpoint | Pump XX Enable Setpoint |  | pump((?:(?!Lag)\w){0,4}(?=[A-Z]¦$))EnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | general,water,pump,enable,effective,sp | DCWS,DHWS,PMP,ROS,WSS | 2.15 (Released),2.16 (Pre-Release)
pumpEnteringPressure | pumpXXXXEnteringPressure | Pump Entering Pressure | Pump XX Entering Pressure |  | pump(\w{0,4}(?=[A-Z]¦$))EnteringPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | general,water,pump,entering,pressure,sensor | DCWS,DHWS,PMP,ROS,WSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
pumpFault | pumpXXXXFault | Pump Fault | Pump XX Fault |  | pump(\w{0,4}(?=[A-Z]¦$))Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | general,water,pump,fault,common | DCWS,DHWS,PMP,ROS,WSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
pumpLagDisableSp | pumpXXXXLagDisableSp | Pump Lag Disable Setpoint | Pump XX Lag Disable Setpoint |  | pump(\w{0,4}(?=[A-Z]¦$))LagDisableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | general,water,pump,lag,disable,sp | DCWS,DHWS,PMP,ROS,WSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
pumpLagEnableSp | pumpXXXXLagEnableSp | Pump Lag Enable Setpoint | Pump XX Lag Enable Setpoint |  | pump(\w{0,4}(?=[A-Z]¦$))LagEnableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | general,water,pump,lag,enable,sp | DCWS,DHWS,PMP,ROS,WSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
pumpLagReq | pumpXXXXLagReq | Pump Lag Request | Pump XX Lag Request |  | pump(\w{0,4}(?=[A-Z]¦$))LagReq | No | No | No | Bool | Request/No Request | Request/No Request | [6 empty] | general,water,pump,lag,request,cmd | DCWS,DHWS,PMP,ROS,WSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
pumpLead | pumpLead | Pump Lead | Pump Lead |  | pumpLead | Yes | Yes | No | Bool | Lead 1/Lead 2 | Lead 1/Lead 2 | [6 empty] | general,water,pump,lead,sp | DCWS,DHWS,PMP,ROS,WSS | 2.15 (Released),2.16 (Pre-Release)
pumpLeadXor | pumpLeadXor | Pump Lead Change Over | Pump Lead Change Over |  | pumpLeadXor | No | No | No | Bool | On/Off | On/Off | [6 empty] | general,water,pump,lead,changeOver,cmd | DCWS,DHWS,PMP,ROS,WSS | 2.15 (Released),2.16 (Pre-Release)
pumpLeadXorRuntimeSp | pumpLeadXorRuntimeSp | Pump Lead Change Over Runtime Setpoint | Pump Lead Change Over Runtime Setpoint |  | pumpLeadXorRuntimeSp | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | DCWS,DHWS,PMP,ROS,WSS | 2.15 (Released),2.16 (Pre-Release)
pumpLeavingPressure | pumpXXXXLeavingPressure | Pump Leaving Pressure | Pump XX Leaving Pressure |  | pump(\w{0,4}(?=[A-Z]¦$))LeavingPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | general,water,pump,leaving,pressure,sensor | DCWS,DHWS,PMP,ROS,WSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
pumpMaintSwitch | pumpXXXXMaintSwitch | Pump Maintenance Switch | Pump XX Maintenance Switch |  | pump(\w{0,4}(?=[A-Z]¦$))MaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | general,water,pump,maintenance,switch,cmd | DCWS,DHWS,PMP,ROS,WSS | 2.15 (Released),2.16 (Pre-Release)
pumpOvr | pumpXXXXOvr | Pump Override | Pump XX Override |  | pump(\w{0,4}(?=[A-Z]¦$))Ovr | No | No | No | Bool | On/Off | On/Off | [6 empty] | general,water,pump,status,ovr | DCWS,DHWS,PMP,ROS,WSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
pumpPressureDelta | pumpXXXXPressureDelta | Pump Pressure Delta | Pump XX Pressure Delta |  | pump(\w{0,4}(?=[A-Z]¦$))PressureDelta | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | general,water,pump,common,pressure,delta,sensor | DCWS,DHWS,PMP,ROS,WSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
pumpPressureHiAlarm | pumpXXXXPressureHiAlarm | Pump Pressure High Alarm | Pump XX Pressure High Alarm |  | pump(\w{0,4}(?=[A-Z]¦$))PressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | general,water,pump,pressure,high,alarm | DCWS,DHWS,PMP,ROS,WSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
pumpPressureHiSp | pumpXXXXPressureHiSp | Pump Pressure High Setpoint | Pump XX Pressure High Setpoint |  | pump(\w{0,4}(?=[A-Z]¦$))PressureHiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | general,water,pump,pressure,high,sp | DCWS,DHWS,PMP,ROS,WSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
pumpPressureLoAlarm | pumpXXXXPressureLoAlarm | Pump Pressure Low Alarm | Pump XX Pressure Low Alarm |  | pump(\w{0,4}(?=[A-Z]¦$))PressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | general,water,pump,pressure,low,alarm | DCWS,DHWS,PMP,ROS,WSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
pumpPressureLoSp | pumpXXXXPressureLoSp | Pump Pressure Low Setpoint | Pump XX Pressure Low Setpoint |  | pump(\w{0,4}(?=[A-Z]¦$))PressureLoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | general,water,pump,pressure,low,sp | DCWS,DHWS,PMP,ROS,WSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
pumpRuntime | pumpXXXXRuntime | Pump Runtime | Pump XX Runtime |  | pump(\w{0,4}(?=[A-Z]¦$))Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | DCWS,DHWS,PMP,ROS,WSS | 2.15 (Released),2.16 (Pre-Release)
pumpSpeed | pumpXXXXSpeed | Pump Speed | Pump XX Speed |  | pump(\w{0,4}(?=[A-Z]¦$))Speed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | general,water,pump,speed,cmd | DCWS,DHWS,PMP,ROS,WSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
pumpSpeedFb | pumpXXXXSpeedFb | Pump Speed Feedback | Pump XX Speed Feedback |  | pump(\w{0,4}(?=[A-Z]¦$))SpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | general,water,pump,speed,sensor | DCWS,DHWS,PMP,ROS,WSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
pumpSpeedMaxSp | pumpXXXXSpeedMaxSp | Pump Speed Max Setpoint | Pump XX Speed Max Setpoint |  | pump(\w{0,4}(?=[A-Z]¦$))SpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | general,water,pump,speed,max,sp | DCWS,DHWS,PMP,ROS,WSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
pumpSpeedMinSp | pumpXXXXSpeedMinSp | Pump Speed Min Setpoint | Pump XX Speed Min Setpoint |  | pump(\w{0,4}(?=[A-Z]¦$))SpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | general,water,pump,speed,min,sp | DCWS,DHWS,PMP,ROS,WSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
pumpSpeedOvr | pumpXXXXSpeedOvr | Pump Speed Override | Pump XX Speed Override |  | pump(\w{0,4}(?=[A-Z]¦$))SpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | general,water,pump,speed,ovr | DCWS,DHWS,PMP,ROS,WSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
pumpSpeedSp | pumpXXXXSpeedSp | Pump Speed Setpoint | Pump XX Speed Setpoint |  | pump(\w{0,4}(?=[A-Z]¦$))SpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | general,water,pump,speed,effective,sp | DCWS,DHWS,PMP,ROS,WSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
pumpStatus | pumpXXXXStatus | Pump Status | Pump XX Status |  | pump(\w{0,4}(?=[A-Z]¦$))Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | general,water,pump,status,sensor | DCWS,DHWS,PMP,ROS,WSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
purgeModeEnable | purgeModeEnable | Purge Mode Enable | Purge Mode Enable |  | purgeModeEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | purge,mode,enable,cmd | AHU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
pushButton | pushButton | Push Button | Push Button |  | pushButton | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | pushButton,sensor | DOOR,SEC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
rackHumidity | rackHumidity | Rack Humidity | Rack Humidity |  | rackHumidity | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | rack,humidity,sensor | CRAC,CRAH | 2.15 (Released),2.16 (Pre-Release)
rackTemp | rackTemp | Rack Temperature | Rack Temperature |  | rackTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | rack,temp,sensor | CRAC,CRAH | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
rackTempHiAlarm | rackTempHiAlarm | Rack Temperature High Alarm | Rack Temperature High Alarm |  | rackTempHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | rack,temp,high,alarm | CRAC,CRAH | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
radiantCoolingValve | radiantCoolingValveXXXX | Radiant Cooling Valve Command | Radiant Cooling Valve XX Command |  | radiantCoolingValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 | XX |  | radiant,valve,cool,position,cmd | RP,RPC,RPF | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
radiantCoolingValveFb | radiantCoolingValveXXXXFb | Radiant Cooling Valve Feedback | Radiant Cooling Valve XX Feedback |  | radiantCoolingValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 | XX |  | radiant,valve,cool,position,sensor | RP,RPC,RPF | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
radiantHeatingValve | radiantHeatingValveXXXX | Radiant Heating Valve Command | Radiant Heating Valve XX Command |  | radiantHeatingValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 | XX |  | radiant,valve,heat,position,cmd | RP,RPC,RPF | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
radiantHeatingValveFb | radiantHeatingValveXXXXFb | Radiant Heating Valve Feedback | Radiant Heating Valve XX Feedback |  | radiantHeatingValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 | XX |  | radiant,valve,heat,position,sensor | RP,RPC,RPF | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
radiatorFan | radiatorFan | Radiator Fan Command | Radiator Fan Command |  | radiatorFan | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | radiator,air,fan,status,cmd | CMP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
radiatorFanStatus | radiatorFanStatus | Radiator Fan Status | Radiator Fan Status |  | radiatorFanStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | radiator,air,fan,status,sensor | CMP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilDischargeTemp | reCoolingCoilXXXXDischargeTemp | Re-Cooling Coil Discharge Temperature | Re-Cooling Coil XX Discharge Temperature |  | reCoolingCoil(\d{0,4})DischargeTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | recool,coil,air,discharge,temp,sensor | AFMS,AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilDischargeTempDb | reCoolingCoilXXXXDischargeTempDb | Re-Cooling Coil Discharge Temperature Deadband | Re-Cooling Coil XX Discharge Temperature Deadband |  | reCoolingCoil(\d{0,4})DischargeTempDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | recool,coil,air,discharge,temp,deadband,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilDischargeTempHiSp | reCoolingCoilXXXXDischargeTempHiSp | Re-Cooling Coil Discharge Temperature High Setpoint | Re-Cooling Coil XX Discharge Temperature High Setpoint |  | reCoolingCoil(\d{0,4})DischargeTempHiSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | recool,coil,air,discharge,temp,high,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilDischargeTempLoSp | reCoolingCoilXXXXDischargeTempLoSp | Re-Cooling Coil Discharge Temperature Low Setpoint | Re-Cooling Coil XX Discharge Temperature Low Setpoint |  | reCoolingCoil(\d{0,4})DischargeTempLoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | recool,coil,air,discharge,temp,low,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilDischargeTempMaxSp | reCoolingCoilXXXXDischargeTempMaxSp | Re-Cooling Coil Discharge Temperature Max Reset Setpoint | Re-Cooling Coil XX Discharge Temperature Max Reset Setpoint |  | reCoolingCoil(\d{0,4})DischargeTempMaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | recool,coil,air,discharge,temp,max,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilDischargeTempMinSp | reCoolingCoilXXXXDischargeTempMinSp | Re-Cooling Coil Discharge Temperature Min Reset Setpoint | Re-Cooling Coil XX Discharge Temperature Min Reset Setpoint |  | reCoolingCoil(\d{0,4})DischargeTempMinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | recool,coil,air,discharge,temp,min,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilDischargeTempSp | reCoolingCoilXXXXDischargeTempSp | Re-Cooling Coil Discharge Temperature Setpoint | Re-Cooling Coil XX Discharge Temperature Setpoint |  | reCoolingCoil(\d{0,4})DischargeTempSp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | recool,coil,air,discharge,temp,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilEnergy | reCoolingCoilXXXXEnergy | Re-Cooling Coil Energy (Tons Refrig) | Re-Cooling Coil XX Energy (Tons Refrig) |  | reCoolingCoil(\d{0,4})Energy | Yes | Yes | No | Number |  |  | tons_refrigeration_hour | tons_refrigeration_hour | 0 | 0 |  |  | recool,coil,water,energy,common,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilEnteringPressure | reCoolingCoilXXXXEnteringPressure | Re-Cooling Coil Entering Pressure | Re-Cooling Coil XX Entering Pressure |  | reCoolingCoil(\d{0,4})EnteringPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | recool,coil,water,entering,pressure,general,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilEnteringTemp | reCoolingCoilXXXXEnteringTemp | Re-Cooling Coil Entering Temperature | Re-Cooling Coil XX Entering Temperature |  | reCoolingCoil(\d{0,4})EnteringTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | recool,coil,water,entering,temp,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilFilterAlarm | reCoolingCoilXXXXFilterAlarm | Re-Cooling Coil Filter Alarm | Re-Cooling Coil XX Filter Alarm |  | reCoolingCoil(\d{0,4})FilterAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | recool,coil,air,filter,general,alarm | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilFilterAlarmReset | reCoolingCoilXXXXFilterAlarmReset | Re-Cooling Coil Filter Alarm Reset | Re-Cooling Coil XX Filter Alarm Reset |  | reCoolingCoil(\d{0,4})FilterAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | recool,coil,air,filter,reset,alarm | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilFilterPressureDelta | reCoolingCoilXXXXFilterPressureDelta | Re-Cooling Coil Filter Pressure Delta | Re-Cooling Coil XX Filter Pressure Delta |  | reCoolingCoil(\d{0,4})FilterPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | recool,coil,air,filter,pressure,delta,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released)
reCoolingCoilFilterRuntime | reCoolingCoilXXXXFilterRuntime | Re-Cooling Coil Filter Runtime | Re-Cooling Coil XX Filter Runtime |  | reCoolingCoil(\d{0,4})FilterRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.15 (Released),2.16 (Pre-Release)
reCoolingCoilFlow | reCoolingCoilXXXXFlow | Re-Cooling Coil Flow | Re-Cooling Coil XX Flow |  | reCoolingCoil(\d{0,4})Flow | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | recool,coil,water,flow,status,cmd | AFMS,AHU,CRAC,CRAH,CU,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilFlowStatus | reCoolingCoilXXXXFlowStatus | Re-Cooling Coil Flow Status | Re-Cooling Coil XX Flow Status |  | reCoolingCoil(\d{0,4})FlowStatus | Yes | Yes | No | Bool | Flow/No Flow | Flow/No Flow | [6 empty] | recool,coil,water,flow,status,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilLeavingPressure | reCoolingCoilXXXXLeavingPressure | Re-Cooling Coil Leaving Pressure | Re-Cooling Coil XX Leaving Pressure |  | reCoolingCoil(\d{0,4})LeavingPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | recool,coil,water,leaving,pressure,general,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilLeavingTemp | reCoolingCoilXXXXLeavingTemp | Re-Cooling Coil Leaving Temperature | Re-Cooling Coil XX Leaving Temperature |  | reCoolingCoil(\d{0,4})LeavingTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | recool,coil,water,leaving,temp,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPower | reCoolingCoilXXXXPower | Re-Cooling Coil Power | Re-Cooling Coil XX Power |  | reCoolingCoil(\d{0,4})Power | Yes | Yes | No | Number |  |  | tons_refrigeration | tons_refrigeration | 1 | 1 |  |  | recool,coil,water,power,common,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPumpAlarm | reCoolingCoilXXXXPumpAlarm | Re-Cooling Coil Pump Alarm | Re-Cooling Coil XX Pump Alarm |  | reCoolingCoil(\d{0,4})PumpAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | recool,coil,water,pump,common,alarm | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPumpAlarmReset | reCoolingCoilXXXXPumpAlarmReset | Re-Cooling Coil Pump Alarm Reset | Re-Cooling Coil XX Pump Alarm Reset |  | reCoolingCoil(\d{0,4})PumpAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | recool,coil,water,pump,reset,alarm | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPump | reCoolingCoilXXXXPump | Re-Cooling Coil Pump Command | Re-Cooling Coil XX Pump Command |  | reCoolingCoil(\d{0,4})Pump | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | recool,coil,water,pump,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPumpCurrent | reCoolingCoilXXXXPumpCurrent | Re-Cooling Coil Pump Current | Re-Cooling Coil XX Pump Current |  | reCoolingCoil(\d{0,4})PumpCurrent | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | recool,coil,water,pump,current,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPumpEnable | reCoolingCoilXXXXPumpEnable | Re-Cooling Coil Pump Enable | Re-Cooling Coil XX Pump Enable |  | reCoolingCoil(\d{0,4})PumpEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | recool,coil,water,pump,enable,cmd | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPumpEnableDb | reCoolingCoilXXXXPumpEnableDb | Re-Cooling Coil Pump Enable Deadband | Re-Cooling Coil XX Pump Enable Deadband |  | reCoolingCoil(\d{0,4})PumpEnableDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | recool,coil,water,pump,enable,deadband,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPumpEnableSp | reCoolingCoilXXXXPumpEnableSp | Re-Cooling Coil Pump Enable Setpoint | Re-Cooling Coil XX Pump Enable Setpoint |  | reCoolingCoil(\d{0,4})PumpEnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | recool,coil,water,pump,enable,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPumpEnteringPressure | reCoolingCoilXXXXPumpEnteringPressure | Re-Cooling Coil Pump Entering Pressure | Re-Cooling Coil XX Pump Entering Pressure |  | reCoolingCoil(\d{0,4})PumpEnteringPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | recool,coil,water,pump,entering,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPumpFault | reCoolingCoilXXXXPumpFault | Re-Cooling Coil Pump Fault | Re-Cooling Coil XX Pump Fault |  | reCoolingCoil(\d{0,4})PumpFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | recool,coil,water,pump,fault,common | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPumpLagDisableSp | reCoolingCoilXXXXPumpLagDisableSp | Re-Cooling Coil Pump Lag Disable Setpoint | Re-Cooling Coil XX Pump Lag Disable Setpoint |  | reCoolingCoil(\d{0,4})PumpLagDisableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | recool,coil,water,pump,lag,disable,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPumpLagEnableSp | reCoolingCoilXXXXPumpLagEnableSp | Re-Cooling Coil Pump Lag Enable Setpoint | Re-Cooling Coil XX Pump Lag Enable Setpoint |  | reCoolingCoil(\d{0,4})PumpLagEnableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | recool,coil,water,pump,lag,enable,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPumpLagReq | reCoolingCoilXXXXPumpLagReq | Re-Cooling Coil Pump Lag Request | Re-Cooling Coil XX Pump Lag Request |  | reCoolingCoil(\d{0,4})PumpLagReq | No | No | No | Bool | Request/No Request | Request/No Request | [6 empty] | recool,coil,water,pump,lag,request,cmd | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPumpLead | reCoolingCoilPumpLead | Re-Cooling Coil Pump Lead | Re-Cooling Coil Pump Lead |  | reCoolingCoilPumpLead | Yes | Yes | No | Bool | Lead 1/Lead 2 | Lead 1/Lead 2 | [6 empty] | recool,coil,water,pump,lead,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPumpLeadXor | reCoolingCoilPumpLeadXor | Re-Cooling Coil Pump Lead Change Over | Re-Cooling Coil Pump Lead Change Over |  | reCoolingCoilPumpLeadXor | No | No | No | Bool | On/Off | On/Off | [6 empty] | recool,coil,water,pump,lead,changeOver,cmd | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPumpLeadXorRuntimeSp | reCoolingCoilPumpLeadXorRuntimeSp | Re-Cooling Coil Pump Lead Change Over Runtime Setpoint | Re-Cooling Coil Pump Lead Change Over Runtime Setpoint |  | reCoolingCoilPumpLeadXorRuntimeSp | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPumpLeavingPressure | reCoolingCoilXXXXPumpLeavingPressure | Re-Cooling Coil Pump Leaving Pressure | Re-Cooling Coil XX Pump Leaving Pressure |  | reCoolingCoil(\d{0,4})PumpLeavingPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | recool,coil,water,pump,leaving,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPumpMaintSwitch | reCoolingCoilXXXXPumpMaintSwitch | Re-Cooling Coil Pump Maintenance Switch | Re-Cooling Coil XX Pump Maintenance Switch |  | reCoolingCoil(\d{0,4})PumpMaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | recool,coil,water,pump,maintenance,switch,cmd | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPumpOvr | reCoolingCoilXXXXPumpOvr | Re-Cooling Coil Pump Override | Re-Cooling Coil XX Pump Override |  | reCoolingCoil(\d{0,4})PumpOvr | No | No | No | Bool | On/Off | On/Off | [6 empty] | recool,coil,water,pump,status,ovr | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPumpPressureDelta | reCoolingCoilXXXXPumpPressureDelta | Re-Cooling Coil Pump Pressure Delta | Re-Cooling Coil XX Pump Pressure Delta |  | reCoolingCoil(\d{0,4})PumpPressureDelta | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | recool,coil,water,pump,common,pressure,delta,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPumpPressureHiAlarm | reCoolingCoilXXXXPumpPressureHiAlarm | Re-Cooling Coil Pump Pressure High Alarm | Re-Cooling Coil XX Pump Pressure High Alarm |  | reCoolingCoil(\d{0,4})PumpPressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | recool,coil,water,pump,pressure,high,alarm | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPumpPressureHiSp | reCoolingCoilXXXXPumpPressureHiSp | Re-Cooling Coil Pump Pressure High Setpoint | Re-Cooling Coil XX Pump Pressure High Setpoint |  | reCoolingCoil(\d{0,4})PumpPressureHiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | recool,coil,water,pump,pressure,high,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPumpPressureLoAlarm | reCoolingCoilXXXXPumpPressureLoAlarm | Re-Cooling Coil Pump Pressure Low Alarm | Re-Cooling Coil XX Pump Pressure Low Alarm |  | reCoolingCoil(\d{0,4})PumpPressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | recool,coil,water,pump,pressure,low,alarm | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPumpPressureLoSp | reCoolingCoilXXXXPumpPressureLoSp | Re-Cooling Coil Pump Pressure Low Setpoint | Re-Cooling Coil XX Pump Pressure Low Setpoint |  | reCoolingCoil(\d{0,4})PumpPressureLoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | recool,coil,water,pump,pressure,low,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPumpRuntime | reCoolingCoilXXXXPumpRuntime | Re-Cooling Coil Pump Runtime | Re-Cooling Coil XX Pump Runtime |  | reCoolingCoil(\d{0,4})PumpRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPumpSpeed | reCoolingCoilXXXXPumpSpeed | Re-Cooling Coil Pump Speed | Re-Cooling Coil XX Pump Speed |  | reCoolingCoil(\d{0,4})PumpSpeed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | recool,coil,water,pump,speed,cmd | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPumpSpeedFb | reCoolingCoilXXXXPumpSpeedFb | Re-Cooling Coil Pump Speed Feedback | Re-Cooling Coil XX Pump Speed Feedback |  | reCoolingCoil(\d{0,4})PumpSpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | recool,coil,water,pump,speed,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPumpSpeedMaxSp | reCoolingCoilXXXXPumpSpeedMaxSp | Re-Cooling Coil Pump Speed Max Setpoint | Re-Cooling Coil XX Pump Speed Max Setpoint |  | reCoolingCoil(\d{0,4})PumpSpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | recool,coil,water,pump,speed,max,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPumpSpeedMinSp | reCoolingCoilXXXXPumpSpeedMinSp | Re-Cooling Coil Pump Speed Min Setpoint | Re-Cooling Coil XX Pump Speed Min Setpoint |  | reCoolingCoil(\d{0,4})PumpSpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | recool,coil,water,pump,speed,min,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPumpSpeedOvr | reCoolingCoilXXXXPumpSpeedOvr | Re-Cooling Coil Pump Speed Override | Re-Cooling Coil XX Pump Speed Override |  | reCoolingCoil(\d{0,4})PumpSpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | recool,coil,water,pump,speed,ovr | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPumpSpeedSp | reCoolingCoilXXXXPumpSpeedSp | Re-Cooling Coil Pump Speed Setpoint | Re-Cooling Coil XX Pump Speed Setpoint |  | reCoolingCoil(\d{0,4})PumpSpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | recool,coil,water,pump,speed,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilPumpStatus | reCoolingCoilXXXXPumpStatus | Re-Cooling Coil Pump Status | Re-Cooling Coil XX Pump Status |  | reCoolingCoil(\d{0,4})PumpStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | recool,coil,water,pump,status,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilStrainerAlarm | reCoolingCoilXXXXStrainerAlarm | Re-Cooling Coil Strainer Alarm | Re-Cooling Coil XX Strainer Alarm |  | reCoolingCoil(\d{0,4})StrainerAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | recool,coil,water,strainer,alarm | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingCoilStrainerEnable | reCoolingCoilXXXXStrainerEnable | Re-Cooling Coil Strainer Enable | Re-Cooling Coil XX Strainer Enable |  | reCoolingCoil(\d{0,4})StrainerEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | recool,coil,water,strainer,enable,cmd | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingValve | reCoolingValve | Re-Cooling Valve Command | Re-Cooling Valve Command |  | reCoolingValve | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | recool,valve,position,cmd | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingValveFb | reCoolingValveFb | Re-Cooling Valve Feedback | Re-Cooling Valve Feedback |  | reCoolingValveFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | recool,valve,position,sensor | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reCoolingValveOvr | reCoolingValveOvr | Re-Cooling Valve Override Commmand | Re-Cooling Valve Override Commmand |  | reCoolingValveOvr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | recool,valve,position,ovr | AHU,CRAC,CRAH,DHU,DOAS,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilDischargeTemp | reHeatingCoilXXXXDischargeTemp | Re-Heating Coil Discharge Temperature | Re-Heating Coil XX Discharge Temperature |  | reHeatingCoil(\d{0,4})DischargeTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | reheat,coil,air,discharge,temp,sensor | AFMS,AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilDischargeTempDb | reHeatingCoilXXXXDischargeTempDb | Re-Heating Coil Discharge Temperature Deadband | Re-Heating Coil XX Discharge Temperature Deadband |  | reHeatingCoil(\d{0,4})DischargeTempDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | reheat,coil,air,discharge,temp,deadband,sp | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilDischargeTempHiSp | reHeatingCoilXXXXDischargeTempHiSp | Re-Heating Coil Discharge Temperature High Setpoint | Re-Heating Coil XX Discharge Temperature High Setpoint |  | reHeatingCoil(\d{0,4})DischargeTempHiSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | reheat,coil,air,discharge,temp,high,sp | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilDischargeTempLoSp | reHeatingCoilXXXXDischargeTempLoSp | Re-Heating Coil Discharge Temperature Low Setpoint | Re-Heating Coil XX Discharge Temperature Low Setpoint |  | reHeatingCoil(\d{0,4})DischargeTempLoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | reheat,coil,air,discharge,temp,low,sp | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilDischargeTempMaxSp | reHeatingCoilXXXXDischargeTempMaxSp | Re-Heating Coil Discharge Temperature Max Reset Setpoint | Re-Heating Coil XX Discharge Temperature Max Reset Setpoint |  | reHeatingCoil(\d{0,4})DischargeTempMaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | reheat,coil,air,discharge,temp,max,sp | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilDischargeTempMinSp | reHeatingCoilXXXXDischargeTempMinSp | Re-Heating Coil Discharge Temperature Min Reset Setpoint | Re-Heating Coil XX Discharge Temperature Min Reset Setpoint |  | reHeatingCoil(\d{0,4})DischargeTempMinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | reheat,coil,air,discharge,temp,min,sp | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilDischargeTempSp | reHeatingCoilXXXXDischargeTempSp | Re-Heating Coil Discharge Temperature Setpoint | Re-Heating Coil XX Discharge Temperature Setpoint |  | reHeatingCoil(\d{0,4})DischargeTempSp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | reheat,coil,air,discharge,temp,effective,sp | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilEnergy | reHeatingCoilXXXXEnergy | Re-Heating Coil Energy | Re-Heating Coil XX Energy |  | reHeatingCoil(\d{0,4})Energy | Yes | Yes | No | Number |  |  | kilobtu | kilobtu | 0 | 0 |  |  | reheat,coil,water,energy,common,sensor | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilEnteringPressure | reHeatingCoilXXXXEnteringPressure | Re-Heating Coil Entering Pressure | Re-Heating Coil XX Entering Pressure |  | reHeatingCoil(\d{0,4})EnteringPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | reheat,coil,water,entering,pressure,general,sensor | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilEnteringTemp | reHeatingCoilXXXXEnteringTemp | Re-Heating Coil Entering Temperature | Re-Heating Coil XX Entering Temperature |  | reHeatingCoil(\d{0,4})EnteringTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | reheat,coil,water,entering,temp,sensor | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilFilterAlarm | reHeatingCoilXXXXFilterAlarm | Re-Heating Coil Filter Alarm | Re-Heating Coil XX Filter Alarm |  | reHeatingCoil(\d{0,4})FilterAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | reheat,coil,air,filter,general,alarm | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilFilterAlarmReset | reHeatingCoilXXXXFilterAlarmReset | Re-Heating Coil Filter Alarm Reset | Re-Heating Coil XX Filter Alarm Reset |  | reHeatingCoil(\d{0,4})FilterAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | reheat,coil,air,filter,reset,alarm | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilFilterPressureDelta | reHeatingCoilXXXXFilterPressureDelta | Re-Heating Coil Filter Pressure Delta | Re-Heating Coil XX Filter Pressure Delta |  | reHeatingCoil(\d{0,4})FilterPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reheat,coil,air,filter,pressure,delta,sensor | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released)
reHeatingCoilFilterRuntime | reHeatingCoilXXXXFilterRuntime | Re-Heating Coil Filter Runtime | Re-Heating Coil XX Filter Runtime |  | reHeatingCoil(\d{0,4})FilterRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.15 (Released),2.16 (Pre-Release)
reHeatingCoilFlow | reHeatingCoilXXXXFlow | Re-Heating Coil Flow | Re-Heating Coil XX Flow |  | reHeatingCoil(\d{0,4})Flow | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | reheat,coil,water,flow,cmd | AFMS,AHU,CRAC,CRAH,CU,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilFlowStatus | reHeatingCoilXXXXFlowStatus | Re-Heating Coil Flow Status | Re-Heating Coil XX Flow Status |  | reHeatingCoil(\d{0,4})FlowStatus | Yes | Yes | No | Bool | Flow/No Flow | Flow/No Flow | [6 empty] | reheat,coil,water,flow,status | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilLeavingPressure | reHeatingCoilXXXXLeavingPressure | Re-Heating Coil Leaving Pressure | Re-Heating Coil XX Leaving Pressure |  | reHeatingCoil(\d{0,4})LeavingPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | reheat,coil,water,leaving,pressure,general,sensor | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilLeavingTemp | reHeatingCoilXXXXLeavingTemp | Re-Heating Coil Leaving Temperature | Re-Heating Coil XX Leaving Temperature |  | reHeatingCoil(\d{0,4})LeavingTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | reheat,coil,water,leaving,temp,sensor | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilLowLimitAlarm | reHeatingCoilXXXXLowLimitAlarm | Re-Heating Coil Low Limit Alarm | Re-Heating Coil XX Low Limit Alarm |  | reHeatingCoil(\d{0,4})LowLimitAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | reheat,coil,water,low,limit,alarm | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPower | reHeatingCoilXXXXPower | Re-Heating Coil Power | Re-Heating Coil XX Power |  | reHeatingCoil(\d{0,4})Power | Yes | Yes | No | Number |  |  | kilobtus_per_hour | kilobtus_per_hour | 1 | 1 |  |  | reheat,coil,water,power,common,sensor | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPumpAlarm | reHeatingCoilXXXXPumpAlarm | Re-Heating Coil Pump Alarm | Re-Heating Coil XX Pump Alarm |  | reHeatingCoil(\d{0,4})PumpAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | reheat,coil,water,pump,common,alarm | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPumpAlarmReset | reHeatingCoilXXXXPumpAlarmReset | Re-Heating Coil Pump Alarm Reset | Re-Heating Coil XX Pump Alarm Reset |  | reHeatingCoil(\d{0,4})PumpAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | reheat,coil,water,pump,reset,alarm | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPump | reHeatingCoilXXXXPump | Re-Heating Coil Pump Command | Re-Heating Coil XX Pump Command |  | reHeatingCoil(\d{0,4})Pump | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | reheat,coil,water,pump,status,cmd | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPumpCurrent | reHeatingCoilXXXXPumpCurrent | Re-Heating Coil Pump Current | Re-Heating Coil XX Pump Current |  | reHeatingCoil(\d{0,4})PumpCurrent | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | reheat,coil,water,pump,current,sensor | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPumpEnable | reHeatingCoilXXXXPumpEnable | Re-Heating Coil Pump Enable | Re-Heating Coil XX Pump Enable |  | reHeatingCoil(\d{0,4})PumpEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | reheat,coil,water,pump,enable,cmd | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPumpEnableDb | reHeatingCoilXXXXPumpEnableDb | Re-Heating Coil Pump Enable Deadband | Re-Heating Coil XX Pump Enable Deadband |  | reHeatingCoil(\d{0,4})PumpEnableDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | reheat,coil,water,pump,enable,deadband,sp | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPumpEnableSp | reHeatingCoilXXXXPumpEnableSp | Re-Heating Coil Pump Enable Setpoint | Re-Heating Coil XX Pump Enable Setpoint |  | reHeatingCoil(\d{0,4})PumpEnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | reheat,coil,water,pump,enable,effective,sp | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPumpEnteringPressure | reHeatingCoilXXXXPumpEnteringPressure | Re-Heating Coil Pump Entering Pressure | Re-Heating Coil XX Pump Entering Pressure |  | reHeatingCoil(\d{0,4})PumpEnteringPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | reheat,coil,water,pump,entering,pressure,sensor | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPumpFault | reHeatingCoilXXXXPumpFault | Re-Heating Coil Pump Fault | Re-Heating Coil XX Pump Fault |  | reHeatingCoil(\d{0,4})PumpFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | reheat,coil,water,pump,fault,common | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPumpLagDisableSp | reHeatingCoilXXXXPumpLagDisableSp | Re-Heating Coil Pump Lag Disable Setpoint | Re-Heating Coil XX Pump Lag Disable Setpoint |  | reHeatingCoil(\d{0,4})PumpLagDisableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | reheat,coil,water,pump,lag,disable,sp | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPumpLagEnableSp | reHeatingCoilXXXXPumpLagEnableSp | Re-Heating Coil Pump Lag Enable Setpoint | Re-Heating Coil XX Pump Lag Enable Setpoint |  | reHeatingCoil(\d{0,4})PumpLagEnableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | reheat,coil,water,pump,lag,enable,sp | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPumpLagReq | reHeatingCoilXXXXPumpLagReq | Re-Heating Coil Pump Lag Request | Re-Heating Coil XX Pump Lag Request |  | reHeatingCoil(\d{0,4})PumpLagReq | No | No | No | Bool | Request/No Request | Request/No Request | [6 empty] | reheat,coil,water,pump,lag,request,cmd | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPumpLead | reHeatingCoilPumpLead | Re-Heating Coil Pump Lead | Re-Heating Coil Pump Lead |  | reHeatingCoilPumpLead | Yes | Yes | No | Bool | Lead 1/Lead 2 | Lead 1/Lead 2 | [6 empty] | reheat,coil,water,pump,lead,sp | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPumpLeadXor | reHeatingCoilPumpLeadXor | Re-Heating Coil Pump Lead Change Over | Re-Heating Coil Pump Lead Change Over |  | reHeatingCoilPumpLeadXor | No | No | No | Bool | On/Off | On/Off | [6 empty] | reheat,coil,water,pump,lead,changeOver,cmd | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPumpLeadXorRuntimeSp | reHeatingCoilPumpLeadXorRuntimeSp | Re-Heating Coil Pump Lead Change Over Runtime Setpoint | Re-Heating Coil Pump Lead Change Over Runtime Setpoint |  | reHeatingCoilPumpLeadXorRuntimeSp | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPumpLeavingPressure | reHeatingCoilXXXXPumpLeavingPressure | Re-Heating Coil Pump Leaving Pressure | Re-Heating Coil XX Pump Leaving Pressure |  | reHeatingCoil(\d{0,4})PumpLeavingPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | reheat,coil,water,pump,leaving,pressure,sensor | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPumpMaintSwitch | reHeatingCoilXXXXPumpMaintSwitch | Re-Heating Coil Pump Maintenance Switch | Re-Heating Coil XX Pump Maintenance Switch |  | reHeatingCoil(\d{0,4})PumpMaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | reheat,coil,water,pump,maintenance,switch,cmd | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPumpOvr | reHeatingCoilXXXXPumpOvr | Re-Heating Coil Pump Override | Re-Heating Coil XX Pump Override |  | reHeatingCoil(\d{0,4})PumpOvr | No | No | No | Bool | On/Off | On/Off | [6 empty] | reheat,coil,water,pump,status,ovr | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPumpPressureDelta | reHeatingCoilXXXXPumpPressureDelta | Re-Heating Coil Pump Pressure Delta | Re-Heating Coil XX Pump Pressure Delta |  | reHeatingCoil(\d{0,4})PumpPressureDelta | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | reheat,coil,water,pump,common,pressure,delta,sensor | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPumpPressureHiAlarm | reHeatingCoilXXXXPumpPressureHiAlarm | Re-Heating Coil Pump Pressure High Alarm | Re-Heating Coil XX Pump Pressure High Alarm |  | reHeatingCoil(\d{0,4})PumpPressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | reheat,coil,water,pump,pressure,high,alarm | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPumpPressureHiSp | reHeatingCoilXXXXPumpPressureHiSp | Re-Heating Coil Pump Pressure High Setpoint | Re-Heating Coil XX Pump Pressure High Setpoint |  | reHeatingCoil(\d{0,4})PumpPressureHiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | reheat,coil,water,pump,pressure,high,sp | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPumpPressureLoAlarm | reHeatingCoilXXXXPumpPressureLoAlarm | Re-Heating Coil Pump Pressure Low Alarm | Re-Heating Coil XX Pump Pressure Low Alarm |  | reHeatingCoil(\d{0,4})PumpPressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | reheat,coil,water,pump,pressure,low,alarm | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPumpPressureLoSp | reHeatingCoilXXXXPumpPressureLoSp | Re-Heating Coil Pump Pressure Low Setpoint | Re-Heating Coil XX Pump Pressure Low Setpoint |  | reHeatingCoil(\d{0,4})PumpPressureLoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | reheat,coil,water,pump,pressure,low,sp | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPumpRuntime | reHeatingCoilXXXXPumpRuntime | Re-Heating Coil Pump Runtime | Re-Heating Coil XX Pump Runtime |  | reHeatingCoil(\d{0,4})PumpRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPumpSpeed | reHeatingCoilXXXXPumpSpeed | Re-Heating Coil Pump Speed | Re-Heating Coil XX Pump Speed |  | reHeatingCoil(\d{0,4})PumpSpeed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | reheat,coil,water,pump,speed,cmd | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPumpSpeedFb | reHeatingCoilXXXXPumpSpeedFb | Re-Heating Coil Pump Speed Feedback | Re-Heating Coil XX Pump Speed Feedback |  | reHeatingCoil(\d{0,4})PumpSpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | reheat,coil,water,pump,speed,sensor | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPumpSpeedMaxSp | reHeatingCoilXXXXPumpSpeedMaxSp | Re-Heating Coil Pump Speed Max Setpoint | Re-Heating Coil XX Pump Speed Max Setpoint |  | reHeatingCoil(\d{0,4})PumpSpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | reheat,coil,water,pump,speed,max,sp | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPumpSpeedMinSp | reHeatingCoilXXXXPumpSpeedMinSp | Re-Heating Coil Pump Speed Min Setpoint | Re-Heating Coil XX Pump Speed Min Setpoint |  | reHeatingCoil(\d{0,4})PumpSpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | reheat,coil,water,pump,speed,min,sp | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPumpSpeedOvr | reHeatingCoilXXXXPumpSpeedOvr | Re-Heating Coil Pump Speed Override | Re-Heating Coil XX Pump Speed Override |  | reHeatingCoil(\d{0,4})PumpSpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | reheat,coil,water,pump,speed,ovr | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPumpSpeedSp | reHeatingCoilXXXXPumpSpeedSp | Re-Heating Coil Pump Speed Setpoint | Re-Heating Coil XX Pump Speed Setpoint |  | reHeatingCoil(\d{0,4})PumpSpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | reheat,coil,water,pump,speed,effective,sp | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilPumpStatus | reHeatingCoilXXXXPumpStatus | Re-Heating Coil Pump Status | Re-Heating Coil XX Pump Status |  | reHeatingCoil(\d{0,4})PumpStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | reheat,coil,water,pump,status,sensor | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilStrainerAlarm | reHeatingCoilXXXXStrainerAlarm | Re-Heating Coil Strainer Alarm | Re-Heating Coil XX Strainer Alarm |  | reHeatingCoil(\d{0,4})StrainerAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | reheat,coil,water,strainer,alarm | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingCoilStrainerEnable | reHeatingCoilXXXXStrainerEnable | Re-Heating Coil Strainer Enable | Re-Heating Coil XX Strainer Enable |  | reHeatingCoil(\d{0,4})StrainerEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | reheat,coil,water,strainer,enable,cmd | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingEnable | reHeatingEnable | Re-Heating Enable Command | Re-Heating Enable Command |  | reHeatingEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | reheat,enable,common,cmd | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingEnableDb | reHeatingEnableDb | Re-Heating Enable Deadband | Re-Heating Enable Deadband |  | reHeatingEnableDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | reheat,enable,deadband,sp | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingEnableSp | reHeatingEnableSp | Re-Heating Enable Setpoint | Re-Heating Enable Setpoint |  | reHeatingEnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | reheat,enable,effective,sp | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingStage | reHeatingStageXXXX | Re-Heating Stage Command | Re-Heating Stage XX Command |  | reHeatingStage(\d{0,4}) | Yes | Yes | No | Bool | On/Off | On/Off |  |  |  |  | XX |  | reheat,status,cmd | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingStageMod | reHeatingStageXXXXMod | Re-Heating Stage Modulation | Re-Heating Stage XX Modulation |  | reHeatingStage(\d{0,4})Mod | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 | XX |  | reheat,modulation,cmd | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingStageOvr | reHeatingStageXXXXOvr | Re-Heating Stage Override | Re-Heating Stage XX Override |  | reHeatingStage(\d{0,4})Ovr | No | No | No | Bool | On/Off | On/Off |  |  |  |  | XX |  | reheat,status,sensor | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingStageRuntime | reHeatingStageXXXXRuntime | Re-Heating Stage Runtime | Re-Heating Stage XX Runtime |  | reHeatingStage(\d{0,4})Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 | XX |  | blacklist | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.15 (Released),2.16 (Pre-Release)
reHeatingStageStatus | reHeatingStageXXXXStatus | Re-Heating Stage Status | Re-Heating Stage XX Status |  | reHeatingStage(\d{0,4})Status | Yes | Yes | No | Bool | On/Off | On/Off |  |  |  |  | XX |  | reheat,status,ovr | AHU,CRAC,CRAH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingValve | reHeatingValveXXXX | Re-Heating Valve Command | Re-Heating Valve XX Command |  | reHeatingValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 | XX |  | reheat,valve,position,cmd | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingValveFb | reHeatingValveXXXXFb | Re-Heating Valve Feedback | Re-Heating Valve XX Feedback |  | reHeatingValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 | XX |  | reheat,valve,position,sensor | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reHeatingValveOvr | reHeatingValveXXXXOvr | Re-Heating Valve Override | Re-Heating Valve XX Override |  | reHeatingValve(\d{0,4})Ovr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 | XX |  | reheat,valve,position,ovr | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,FCU,MAU,RTU,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reactCoil | reactCoil | Reactivation Coil Command | Reactivation Coil Command |  | reactCoil | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | reactivation,coil,cmd | AHU,DHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reactCoilDischargeTemp | reactCoilDischargeTemp | Reactivation Coil Discharge Temperature | Reactivation Coil Discharge Temperature |  | reactCoilDischargeTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | reactivation,coil,discharge,temp,sensor | AFMS,AHU,DHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reactFanAlarm | reactFanXXXXAlarm | Reactivation Fan Alarm | Reactivation Fan XX Alarm |  | reactFan(\w{0,4}(?=[A-Z]¦$))Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | reactivation,air,fan,common,alarm | AHU,DHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reactFanAlarmReset | reactFanXXXXAlarmReset | Reactivation Fan Alarm Reset | Reactivation Fan XX Alarm Reset |  | reactFan(\w{0,4}(?=[A-Z]¦$))AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | reactivation,air,fan,alarm,reset | AHU,DHU | 2.15 (Released),2.16 (Pre-Release)
reactFan | reactFanXXXX | Reactivation Fan Command | Reactivation Fan XX Command |  | reactFan((?:(?!Ovr)\w){0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | reactivation,air,fan,status,cmd | AHU,DHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reactFanCurrent | reactFanXXXXCurrent | Reactivation Fan Current | Reactivation Fan XX Current |  | reactFan(\w{0,4}(?=[A-Z]¦$))Current | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | reactivation,air,fan,current,sensor | AHU,DHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reactFanDischargeTemp | reactFanXXXXDischargeTemp | Reactivation Fan Discharge Temperature | Reactivation Fan XX Discharge Temperature |  | reactFan(\w{0,4}(?=[A-Z]¦$))DischargeTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | reactivation,air,fan,dischargeTemp,sensor | AFMS,AHU,DHU | 2.15 (Released),2.16 (Pre-Release)
reactFanEnteringPressure | reactFanXXXXEnteringPressure | Reactivation Fan Entering Pressure | Reactivation Fan XX Entering Pressure |  | reactFan(\w{0,4}(?=[A-Z]¦$))EnteringPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | reactivation,air,fan,entering,pressure,sensor | AHU,DHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reactFanFault | reactFanXXXXFault | Reactivation Fan Fault | Reactivation Fan XX Fault |  | reactFan(\w{0,4}(?=[A-Z]¦$))Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | reactivation,air,fan,fault | AHU,DHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reactFanLeavingPressure | reactFanXXXXLeavingPressure | Reactivation Fan Leaving Pressure | Reactivation Fan XX Leaving Pressure |  | reactFan(\w{0,4}(?=[A-Z]¦$))LeavingPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | reactivation,air,fan,leaving,pressure,sensor | AHU,DHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reactFanMaintSwitch | reactFanXXXXMaintSwitch | Reactivation Fan Maintenance Switch | Reactivation Fan XX Maintenance Switch |  | reactFan(\w{0,4}(?=[A-Z]¦$))MaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | reactivation,air,fan,maintenance,switch,cmd | AHU,DHU | 2.15 (Released),2.16 (Pre-Release)
reactFanOvr | reactFanXXXXOvr | Reactivation Fan Override | Reactivation Fan XX Override |  | reactFan(\w{0,4}(?=[A-Z]¦$))Ovr | No | No | No | Bool | On/Off | On/Off | [6 empty] | reactivation,air,fan,status,ovr | AHU,DHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reactFanPressureDelta | reactFanXXXXPressureDelta | Reactivation Fan Pressure Delta | Reactivation Fan XX Pressure Delta |  | reactFan(\w{0,4}(?=[A-Z]¦$))PressureDelta | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | reactivation,air,fan,common,pressure,delta,sensor | AHU,DHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reactFanPressureHiAlarm | reactFanXXXXPressureHiAlarm | Reactivation Fan Pressure High Alarm | Reactivation Fan XX Pressure High Alarm |  | reactFan(\w{0,4}(?=[A-Z]¦$))PressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | reactivation,air,fan,pressure,high,alarm | AHU,DHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reactFanPressureHiSp | reactFanXXXXPressureHiSp | Reactivation Fan Pressure High Setpoint | Reactivation Fan XX Pressure High Setpoint |  | reactFan(\w{0,4}(?=[A-Z]¦$))PressureHiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | reactivation,air,fan,pressure,high,sp | AHU,DHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reactFanPressureLoAlarm | reactFanXXXXPressureLoAlarm | Reactivation Fan Pressure Low Alarm | Reactivation Fan XX Pressure Low Alarm |  | reactFan(\w{0,4}(?=[A-Z]¦$))PressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | reactivation,air,fan,pressure,low,alarm | AHU,DHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reactFanPressureLoSp | reactFanXXXXPressureLoSp | Reactivation Fan Pressure Low Setpoint | Reactivation Fan XX Pressure Low Setpoint |  | reactFan(\w{0,4}(?=[A-Z]¦$))PressureLoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | reactivation,air,fan,pressure,low,sp | AHU,DHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reactFanRuntime | reactFanXXXXRuntime | Reactivation Fan Runtime | Reactivation Fan XX Runtime |  | reactFan(\w{0,4}(?=[A-Z]¦$))Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,DHU | 2.15 (Released),2.16 (Pre-Release)
reactFanSpeed | reactFanXXXXSpeed | Reactivation Fan Speed | Reactivation Fan XX Speed |  | reactFan(\w{0,4}(?=[A-Z]¦$))Speed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | reactivation,air,fan,speed,cmd | AHU,DHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reactFanSpeedFb | reactFanXXXXSpeedFb | Reactivation Fan Speed Feedback | Reactivation Fan XX Speed Feedback |  | reactFan(\w{0,4}(?=[A-Z]¦$))SpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | reactivation,air,fan,speed,sensor | AHU,DHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reactFanSpeedMaxSp | reactFanXXXXSpeedMaxSp | Reactivation Fan Speed Max Setpoint | Reactivation Fan XX Speed Max Setpoint |  | reactFan(\w{0,4}(?=[A-Z]¦$))SpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | reactivation,air,fan,speed,max,sp | AHU,DHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reactFanSpeedMinSp | reactFanXXXXSpeedMinSp | Reactivation Fan Speed Min Setpoint | Reactivation Fan XX Speed Min Setpoint |  | reactFan(\w{0,4}(?=[A-Z]¦$))SpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | reactivation,air,fan,speed,min,sp | AHU,DHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reactFanSpeedOvr | reactFanXXXXSpeedOvr | Reactivation Fan Speed Override | Reactivation Fan XX Speed Override |  | reactFan(\w{0,4}(?=[A-Z]¦$))SpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | reactivation,air,fan,speed,ovr | AHU,DHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reactFanSpeedSp | reactFanXXXXSpeedSp | Reactivation Fan Speed Setpoint | Reactivation Fan XX Speed Setpoint |  | reactFan(\w{0,4}(?=[A-Z]¦$))SpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | reactivation,air,fan,speed,effective,sp | AHU,DHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reactFanStatus | reactFanXXXXStatus | Reactivation Fan Status | Reactivation Fan XX Status |  | reactFan(\w{0,4}(?=[A-Z]¦$))Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | reactivation,air,fan,status,sensor | AHU,DHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reactValve | reactValve | Reactivation Valve Command | Reactivation Valve Command |  | reactValve | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | reactivation,valve,status,cmd | AHU,DHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reactValveFb | reactValveFb | Reactivation Valve Feedback | Reactivation Valve Feedback |  | reactValveFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | reactivation,valve,status,sensor | AHU,DHU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
energyReactive | energyReactive | Reactive Energy | Reactive Energy |  | energyReactive | Yes | Yes | Yes | Number |  |  | kilovolt_ampere_reactive_hour | kilovolt_ampere_reactive_hour | 0 | 0 |  |  | common,energy,reactive,sensor | AHU,ATS,ATU,BLR,BRK,CLR,CRAC,CRAH,CU,CUH,CWS,DH,DHU,DOAS,EC,EF,FCU,FPB,GEO,HP,HWS,MAU,PDU,PM,PRLY,PV,RPP,RTU,SMS,STS,TVS,TWR,UPS,UV,VAV,VPM,FCU,HP,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
powerReactive | powerReactive | Reactive Power | Reactive Power |  | powerReactive | Yes | Yes | No | Number |  |  | kilovolt_ampere_reactive | kilovolt_ampere_reactive | 1 | 1 |  | N | common,power,reactive,sensor | ATS,BRK,CU,INV,PDU,PFC,PM,PRLY,PV,RECT,RPP,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
powerReactivePhaseA | powerReactivePhaseA | Reactive Power (Phase A) | Reactive Power (Phase A) |  | powerReactivePhaseA | Yes | Yes | No | Number |  |  | kilovolt_ampere_reactive | kilovolt_ampere_reactive | 1 | 1 |  | A | common,power,reactive,sensor | ATS,BRK,CU,INV,PDU,PFC,PM,PRLY,PV,RECT,RPP,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
powerReactivePhaseB | powerReactivePhaseB | Reactive Power (Phase B) | Reactive Power (Phase B) |  | powerReactivePhaseB | Yes | Yes | No | Number |  |  | kilovolt_ampere_reactive | kilovolt_ampere_reactive | 1 | 1 |  | B | common,power,reactive,sensor | ATS,BRK,CU,INV,PDU,PFC,PM,PRLY,PV,RECT,RPP,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
powerReactivePhaseC | powerReactivePhaseC | Reactive Power (Phase C) | Reactive Power (Phase C) |  | powerReactivePhaseC | Yes | Yes | No | Number |  |  | kilovolt_ampere_reactive | kilovolt_ampere_reactive | 1 | 1 |  | C | common,power,reactive,sensor | ATS,BRK,CU,INV,PDU,PFC,PM,PRLY,PV,RECT,RPP,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
readyToLoad | readyToLoad | Ready To Load | Ready To Load |  | readyToLoad | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | ready,load,cmd | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
readyToRun | readyToRun | Ready To Run | Ready To Run |  | readyToRun | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | ready,run,cmd | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
powerReal | powerReal | Real Power | Real Power |  | powerReal | Yes | Yes | No | Number |  |  | kilowatt | kilowatt | 1 | 1 |  | N | common,power,real,sensor | AC,AHU,ATS,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CU,CUH,CWS,DAC,DH,DHU,DOAS,EC,EF,FCU,FPB,GEO,HP,HUM,HWS,INV,MAU,PDU,PFC,PM,PRLY,PV,RECT,RPP,RTU,SMS,STS,TVS,TWR,UPS,UV,VAV,VPM,WS,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
powerRealPhaseA | powerRealPhaseA | Real Power (Phase A) | Real Power (Phase A) |  | powerRealPhaseA | Yes | Yes | No | Number |  |  | kilowatt | kilowatt | 1 | 1 |  | A | common,power,real,sensor | AC,AHU,ATS,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CU,CUH,CWS,DAC,DH,DHU,DOAS,EC,EF,FCU,FPB,GEO,HP,HUM,HWS,INV,MAU,PDU,PFC,PM,PRLY,PV,RECT,RPP,RTU,SMS,STS,TVS,TWR,UPS,UV,VAV,VPM,WS,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
powerRealPhaseB | powerRealPhaseB | Real Power (Phase B) | Real Power (Phase B) |  | powerRealPhaseB | Yes | Yes | No | Number |  |  | kilowatt | kilowatt | 1 | 1 |  | B | common,power,real,sensor | AC,AHU,ATS,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CU,CUH,CWS,DAC,DH,DHU,DOAS,EC,EF,FCU,FPB,GEO,HP,HUM,HWS,INV,MAU,PDU,PFC,PM,PRLY,PV,RECT,RPP,RTU,SMS,STS,TVS,TWR,UPS,UV,VAV,VPM,WS,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
powerRealPhaseC | powerRealPhaseC | Real Power (Phase C) | Real Power (Phase C) |  | powerRealPhaseC | Yes | Yes | No | Number |  |  | kilowatt | kilowatt | 1 | 1 |  | C | common,power,real,sensor | AC,AHU,ATS,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CU,CUH,CWS,DAC,DH,DHU,DOAS,EC,EF,FCU,FPB,GEO,HP,HUM,HWS,INV,MAU,PDU,PFC,PM,PRLY,PV,RECT,RPP,RTU,SMS,STS,TVS,TWR,UPS,UV,VAV,VPM,WS,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
powerRealMax | powerRealMax | Real Power Maximum | Real Power Maximum |  | powerRealMax | Yes | Yes | No | Number |  |  | kilowatt | kilowatt | 1 | 1 |  | N | common,power,real,max,calc | PRLY | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
powerRealMaxDateTime | powerRealMaxDateTime | Real Power Maximum Date & Time | Real Power Maximum Date & Time |  | powerRealMaxDateTime | Yes | No | No | Str | [7 empty] | N | common,power,real,dateTime,calc | PRLY | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recBypassDamper | recBypassDamper | Reclaim Coil Bypass Damper Command | Reclaim Coil Bypass Damper Command |  | recBypassDamper | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | reclaim,coil,bypass,damper,position,cmd | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recBypassDamperFb | recBypassDamperFb | Reclaim Coil Bypass Damper Feedback | Reclaim Coil Bypass Damper Feedback |  | recBypassDamperFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | reclaim,coil,bypass,damper,position,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recDischargeFanAlarm | recDischargeFanAlarm | Reclaim Coil Discharge Fan Alarm | Reclaim Coil Discharge Fan Alarm |  | recDischargeFanAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | reclaim,coil,discharge,air,fan,common,alarm | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recDischargeFanAlarmReset | recDischargeFanAlarmReset | Reclaim Coil Discharge Fan Alarm Reset | Reclaim Coil Discharge Fan Alarm Reset |  | recDischargeFanAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | reclaim,coil,discharge,air,fan,reset,alarm | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.15 (Released),2.16 (Pre-Release)
recDischargeFan | recDischargeFan | Reclaim Coil Discharge Fan Command | Reclaim Coil Discharge Fan Command |  | recDischargeFan | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | reclaim,coil,discharge,air,fan,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recDischargeFanCurrent | recDischargeFanCurrent | Reclaim Coil Discharge Fan Current | Reclaim Coil Discharge Fan Current |  | recDischargeFanCurrent | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | reclaim,coil,discharge,air,fan,current,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recDischargeFanEnteringPressure | recDischargeFanEnteringPressure | Reclaim Coil Discharge Fan Entering Pressure | Reclaim Coil Discharge Fan Entering Pressure |  | recDischargeFanEnteringPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,discharge,air,fan,entering,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recDischargeFanFault | recDischargeFanFault | Reclaim Coil Discharge Fan Fault | Reclaim Coil Discharge Fan Fault |  | recDischargeFanFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | reclaim,coil,discharge,air,fan,fault | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recDischargeFanLeavingPressure | recDischargeFanLeavingPressure | Reclaim Coil Discharge Fan Leaving Pressure | Reclaim Coil Discharge Fan Leaving Pressure |  | recDischargeFanLeavingPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,discharge,air,fan,leaving,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recDischargeFanMaintSwitch | recDischargeFanMaintSwitch | Reclaim Coil Discharge Fan Maintenance Switch | Reclaim Coil Discharge Fan Maintenance Switch |  | recDischargeFanMaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | reclaim,coil,discharge,air,fan,maintenance,switch,cmd | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.15 (Released),2.16 (Pre-Release)
recDischargeFanOvr | recDischargeFanOvr | Reclaim Coil Discharge Fan Override | Reclaim Coil Discharge Fan Override |  | recDischargeFanOvr | No | No | No | Bool | On/Off | On/Off | [6 empty] | reclaim,coil,discharge,air,fan,status,ovr | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recDischargeFanPressureDelta | recDischargeFanPressureDelta | Reclaim Coil Discharge Fan Pressure Delta | Reclaim Coil Discharge Fan Pressure Delta |  | recDischargeFanPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,discharge,air,fan,common,pressure,delta,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recDischargeFanPressureHiAlarm | recDischargeFanPressureHiAlarm | Reclaim Coil Discharge Fan Pressure High Alarm | Reclaim Coil Discharge Fan Pressure High Alarm |  | recDischargeFanPressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | reclaim,coil,discharge,air,fan,pressure,high,alarm | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recDischargeFanPressureHiSp | recDischargeFanPressureHiSp | Reclaim Coil Discharge Fan Pressure High Setpoint | Reclaim Coil Discharge Fan Pressure High Setpoint |  | recDischargeFanPressureHiSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,discharge,air,fan,pressure,high,sp | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recDischargeFanPressureLoAlarm | recDischargeFanPressureLoAlarm | Reclaim Coil Discharge Fan Pressure Low Alarm | Reclaim Coil Discharge Fan Pressure Low Alarm |  | recDischargeFanPressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | reclaim,coil,discharge,air,fan,pressure,low,alarm | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recDischargeFanPressureLoSp | recDischargeFanPressureLoSp | Reclaim Coil Discharge Fan Pressure Low Setpoint | Reclaim Coil Discharge Fan Pressure Low Setpoint |  | recDischargeFanPressureLoSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,discharge,air,fan,pressure,low,sp | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recDischargeFanRuntime | recDischargeFanRuntime | Reclaim Coil Discharge Fan Runtime | Reclaim Coil Discharge Fan Runtime |  | recDischargeFanRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.15 (Released),2.16 (Pre-Release)
recDischargeFanSpeed | recDischargeFanSpeed | Reclaim Coil Discharge Fan Speed | Reclaim Coil Discharge Fan Speed |  | recDischargeFanSpeed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,coil,discharge,air,fan,speed,cmd | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recDischargeFanSpeedFb | recDischargeFanSpeedFb | Reclaim Coil Discharge Fan Speed Feedback | Reclaim Coil Discharge Fan Speed Feedback |  | recDischargeFanSpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,coil,discharge,air,fan,speed,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recDischargeFanSpeedMaxSp | recDischargeFanSpeedMaxSp | Reclaim Coil Discharge Fan Speed Max Setpoint | Reclaim Coil Discharge Fan Speed Max Setpoint |  | recDischargeFanSpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,coil,discharge,air,fan,speed,max,sp | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recDischargeFanSpeedMinSp | recDischargeFanSpeedMinSp | Reclaim Coil Discharge Fan Speed Min Setpoint | Reclaim Coil Discharge Fan Speed Min Setpoint |  | recDischargeFanSpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,coil,discharge,air,fan,speed,min,sp | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recDischargeFanSpeedOvr | recDischargeFanSpeedOvr | Reclaim Coil Discharge Fan Speed Override | Reclaim Coil Discharge Fan Speed Override |  | recDischargeFanSpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,coil,discharge,air,fan,speed,ovr | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recDischargeFanSpeedSp | recDischargeFanSpeedSp | Reclaim Coil Discharge Fan Speed Setpoint | Reclaim Coil Discharge Fan Speed Setpoint |  | recDischargeFanSpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,coil,discharge,air,fan,speed,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recDischargeFanStatus | recDischargeFanStatus | Reclaim Coil Discharge Fan Status | Reclaim Coil Discharge Fan Status |  | recDischargeFanStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | reclaim,coil,discharge,air,fan,status,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recDischargeIsoDamper | recDischargeIsoDamper | Reclaim Coil Discharge Isolation Damper Command | Reclaim Coil Discharge Isolation Damper Command |  | recDischargeIsoDamper | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | reclaim,coil,discharge,iso,air,damper,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recDischargeIsoDamperFb | recDischargeIsoDamperFb | Reclaim Coil Discharge Isolation Damper Feedback | Reclaim Coil Discharge Isolation Damper Feedback |  | recDischargeIsoDamperFb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | reclaim,coil,discharge,iso,air,damper,status,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recExhaustFanAlarm | recExhaustFanAlarm | Reclaim Coil Exhaust Fan Alarm | Reclaim Coil Exhaust Fan Alarm |  | recExhaustFanAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | reclaim,coil,exhaust,air,fan,common,alarm | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recExhaustFanAlarmReset | recExhaustFanAlarmReset | Reclaim Coil Exhaust Fan Alarm Reset | Reclaim Coil Exhaust Fan Alarm Reset |  | recExhaustFanAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | reclaim,coil,exhaust,air,fan,alarm,reset | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.15 (Released),2.16 (Pre-Release)
recExhaustFan | recExhaustFan | Reclaim Coil Exhaust Fan Command | Reclaim Coil Exhaust Fan Command |  | recExhaustFan | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | reclaim,coil,exhaust,air,fan,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recExhaustFanCurrent | recExhaustFanCurrent | Reclaim Coil Exhaust Fan Current | Reclaim Coil Exhaust Fan Current |  | recExhaustFanCurrent | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | reclaim,coil,exhaust,air,fan,current,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recExhaustFanEnteringPressure | recExhaustFanEnteringPressure | Reclaim Coil Exhaust Fan Entering Pressure | Reclaim Coil Exhaust Fan Entering Pressure |  | recExhaustFanEnteringPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,exhaust,air,fan,entering,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recExhaustFanFault | recExhaustFanFault | Reclaim Coil Exhaust Fan Fault | Reclaim Coil Exhaust Fan Fault |  | recExhaustFanFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | reclaim,coil,exhaust,air,fan,fault | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recExhaustFanLeavingPressure | recExhaustFanLeavingPressure | Reclaim Coil Exhaust Fan Leaving Pressure | Reclaim Coil Exhaust Fan Leaving Pressure |  | recExhaustFanLeavingPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,exhaust,air,fan,leaving,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recExhaustFanMaintSwitch | recExhaustFanMaintSwitch | Reclaim Coil Exhaust Fan Maintenance Switch | Reclaim Coil Exhaust Fan Maintenance Switch |  | recExhaustFanMaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | reclaim,coil,exhaust,air,fan,maintenance,switch,cmd | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.15 (Released),2.16 (Pre-Release)
recExhaustFanOvr | recExhaustFanOvr | Reclaim Coil Exhaust Fan Override | Reclaim Coil Exhaust Fan Override |  | recExhaustFanOvr | No | No | No | Bool | On/Off | On/Off | [6 empty] | reclaim,coil,exhaust,air,fan,status,ovr | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recExhaustFanPressureDelta | recExhaustFanPressureDelta | Reclaim Coil Exhaust Fan Pressure Delta | Reclaim Coil Exhaust Fan Pressure Delta |  | recExhaustFanPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,exhaust,air,fan,common,pressure,delta,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recExhaustFanPressureHiAlarm | recExhaustFanPressureHiAlarm | Reclaim Coil Exhaust Fan Pressure High Alarm | Reclaim Coil Exhaust Fan Pressure High Alarm |  | recExhaustFanPressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | reclaim,coil,exhaust,air,fan,pressure,high,alarm | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recExhaustFanPressureHiSp | recExhaustFanPressureHiSp | Reclaim Coil Exhaust Fan Pressure High Setpoint | Reclaim Coil Exhaust Fan Pressure High Setpoint |  | recExhaustFanPressureHiSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,exhaust,air,fan,pressure,high,sp | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recExhaustFanPressureLoAlarm | recExhaustFanPressureLoAlarm | Reclaim Coil Exhaust Fan Pressure Low Alarm | Reclaim Coil Exhaust Fan Pressure Low Alarm |  | recExhaustFanPressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | reclaim,coil,exhaust,air,fan,pressure,low,alarm | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recExhaustFanPressureLoSp | recExhaustFanPressureLoSp | Reclaim Coil Exhaust Fan Pressure Low Setpoint | Reclaim Coil Exhaust Fan Pressure Low Setpoint |  | recExhaustFanPressureLoSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,exhaust,air,fan,pressure,low,sp | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recExhaustFanRuntime | recExhaustFanRuntime | Reclaim Coil Exhaust Fan Runtime | Reclaim Coil Exhaust Fan Runtime |  | recExhaustFanRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.15 (Released),2.16 (Pre-Release)
recExhaustFanSpeed | recExhaustFanSpeed | Reclaim Coil Exhaust Fan Speed | Reclaim Coil Exhaust Fan Speed |  | recExhaustFanSpeed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,coil,exhaust,air,fan,speed,cmd | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recExhaustFanSpeedFb | recExhaustFanSpeedFb | Reclaim Coil Exhaust Fan Speed Feedback | Reclaim Coil Exhaust Fan Speed Feedback |  | recExhaustFanSpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,coil,exhaust,air,fan,speed,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recExhaustFanSpeedMaxSp | recExhaustFanSpeedMaxSp | Reclaim Coil Exhaust Fan Speed Max Setpoint | Reclaim Coil Exhaust Fan Speed Max Setpoint |  | recExhaustFanSpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,coil,exhaust,air,fan,speed,max,sp | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recExhaustFanSpeedMinSp | recExhaustFanSpeedMinSp | Reclaim Coil Exhaust Fan Speed Min Setpoint | Reclaim Coil Exhaust Fan Speed Min Setpoint |  | recExhaustFanSpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,coil,exhaust,air,fan,speed,min,sp | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recExhaustFanSpeedOvr | recExhaustFanSpeedOvr | Reclaim Coil Exhaust Fan Speed Override | Reclaim Coil Exhaust Fan Speed Override |  | recExhaustFanSpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,coil,exhaust,air,fan,speed,ovr | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recExhaustFanSpeedSp | recExhaustFanSpeedSp | Reclaim Coil Exhaust Fan Speed Setpoint | Reclaim Coil Exhaust Fan Speed Setpoint |  | recExhaustFanSpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,coil,exhaust,air,fan,speed,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recExhaustFanStatus | recExhaustFanStatus | Reclaim Coil Exhaust Fan Status | Reclaim Coil Exhaust Fan Status |  | recExhaustFanStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | reclaim,coil,exhaust,air,fan,status,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recExhaustIsoDamper | recExhaustIsoDamper | Reclaim Coil Exhaust Isolation Damper Command | Reclaim Coil Exhaust Isolation Damper Command |  | recExhaustIsoDamper | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | reclaim,coil,exhaust,iso,air,damper,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recExhaustIsoDamperFb | recExhaustIsoDamperFb | Reclaim Coil Exhaust Isolation Damper Feedback | Reclaim Coil Exhaust Isolation Damper Feedback |  | recExhaustIsoDamperFb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | reclaim,coil,exhaust,iso,air,damper,status,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recFaceBypassDamper | recFaceBypassDamper | Reclaim Coil Face Bypass Damper Command | Reclaim Coil Face Bypass Damper Command |  | recFaceBypassDamper | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | reclaim,coil,faceBypass,damper,position,cmd | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recFaceBypassDamperFb | recFaceBypassDamperFb | Reclaim Coil Face Bypass Damper Feedback | Reclaim Coil Face Bypass Damper Feedback |  | recFaceBypassDamperFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | reclaim,coil,faceBypass,damper,position,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recFaceDamper | recFaceDamper | Reclaim Coil Face Damper Command | Reclaim Coil Face Damper Command |  | recFaceDamper | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | reclaim,coil,face,damper,position,cmd | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recFaceDamperFb | recFaceDamperFb | Reclaim Coil Face Damper Feedback | Reclaim Coil Face Damper Feedback |  | recFaceDamperFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | reclaim,coil,face,damper,position,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recMixingValve | recMixingValve | Reclaim Coil Mixing Valve Command | Reclaim Coil Mixing Valve Command |  | recMixingValve | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | reclaim,coil,water,mixing,valve,position,cmd | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recMixingValveFb | recMixingValveFb | Reclaim Coil Mixing Valve Feedback | Reclaim Coil Mixing Valve Feedback |  | recMixingValveFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | reclaim,coil,water,mixing,valve,position,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOutsideFanAlarm | recOutsideFanAlarm | Reclaim Coil Outside Fan Alarm | Reclaim Coil Outside Fan Alarm |  | recOutsideFanAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | reclaim,coil,outside,air,fan,common,alarm | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOutsideFanAlarmReset | recOutsideFanAlarmReset | Reclaim Coil Outside Fan Alarm Reset | Reclaim Coil Outside Fan Alarm Reset |  | recOutsideFanAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | reclaim,coil,outside,air,fan,alarm,reset | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.15 (Released),2.16 (Pre-Release)
recOutsideFan | recOutsideFan | Reclaim Coil Outside Fan Command | Reclaim Coil Outside Fan Command |  | recOutsideFan | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | reclaim,coil,outside,air,fan,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOutsideFanCurrent | recOutsideFanCurrent | Reclaim Coil Outside Fan Current | Reclaim Coil Outside Fan Current |  | recOutsideFanCurrent | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | reclaim,coil,outside,air,fan,current,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOutsideFanEnteringPressure | recOutsideFanEnteringPressure | Reclaim Coil Outside Fan Entering Pressure | Reclaim Coil Outside Fan Entering Pressure |  | recOutsideFanEnteringPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,outside,air,fan,entering,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOutsideFanFault | recOutsideFanFault | Reclaim Coil Outside Fan Fault | Reclaim Coil Outside Fan Fault |  | recOutsideFanFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | reclaim,coil,outside,air,fan,fault | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOutsideFanLeavingPressure | recOutsideFanLeavingPressure | Reclaim Coil Outside Fan Leaving Pressure | Reclaim Coil Outside Fan Leaving Pressure |  | recOutsideFanLeavingPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,outside,air,fan,leaving,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOutsideFanMaintSwitch | recOutsideFanMaintSwitch | Reclaim Coil Outside Fan Maintenance Switch | Reclaim Coil Outside Fan Maintenance Switch |  | recOutsideFanMaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | reclaim,coil,outside,air,fan,maintenance,switch,cmd | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.15 (Released),2.16 (Pre-Release)
recOutsideFanOvr | recOutsideFanOvr | Reclaim Coil Outside Fan Override | Reclaim Coil Outside Fan Override |  | recOutsideFanOvr | No | No | No | Bool | On/Off | On/Off | [6 empty] | reclaim,coil,outside,air,fan,status,ovr | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOutsideFanPressureDelta | recOutsideFanPressureDelta | Reclaim Coil Outside Fan Pressure Delta | Reclaim Coil Outside Fan Pressure Delta |  | recOutsideFanPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,outside,air,fan,common,pressure,delta,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOutsideFanPressureHiAlarm | recOutsideFanPressureHiAlarm | Reclaim Coil Outside Fan Pressure High Alarm | Reclaim Coil Outside Fan Pressure High Alarm |  | recOutsideFanPressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | reclaim,coil,outside,air,fan,pressure,high,alarm | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOutsideFanPressureHiSp | recOutsideFanPressureHiSp | Reclaim Coil Outside Fan Pressure High Setpoint | Reclaim Coil Outside Fan Pressure High Setpoint |  | recOutsideFanPressureHiSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,outside,air,fan,pressure,high,sp | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOutsideFanPressureLoAlarm | recOutsideFanPressureLoAlarm | Reclaim Coil Outside Fan Pressure Low Alarm | Reclaim Coil Outside Fan Pressure Low Alarm |  | recOutsideFanPressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | reclaim,coil,outside,air,fan,pressure,low,alarm | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOutsideFanPressureLoSp | recOutsideFanPressureLoSp | Reclaim Coil Outside Fan Pressure Low Setpoint | Reclaim Coil Outside Fan Pressure Low Setpoint |  | recOutsideFanPressureLoSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,outside,air,fan,pressure,low,sp | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOutsideFanRuntime | recOutsideFanRuntime | Reclaim Coil Outside Fan Runtime | Reclaim Coil Outside Fan Runtime |  | recOutsideFanRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.15 (Released),2.16 (Pre-Release)
recOutsideFanSpeed | recOutsideFanSpeed | Reclaim Coil Outside Fan Speed | Reclaim Coil Outside Fan Speed |  | recOutsideFanSpeed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,coil,outside,air,fan,speed,cmd | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOutsideFanSpeedFb | recOutsideFanSpeedFb | Reclaim Coil Outside Fan Speed Feedback | Reclaim Coil Outside Fan Speed Feedback |  | recOutsideFanSpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,coil,outside,air,fan,speed,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOutsideFanSpeedMaxSp | recOutsideFanSpeedMaxSp | Reclaim Coil Outside Fan Speed Max Setpoint | Reclaim Coil Outside Fan Speed Max Setpoint |  | recOutsideFanSpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,coil,outside,air,fan,speed,max,sp | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOutsideFanSpeedMinSp | recOutsideFanSpeedMinSp | Reclaim Coil Outside Fan Speed Min Setpoint | Reclaim Coil Outside Fan Speed Min Setpoint |  | recOutsideFanSpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,coil,outside,air,fan,speed,min,sp | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOutsideFanSpeedOvr | recOutsideFanSpeedOvr | Reclaim Coil Outside Fan Speed Override | Reclaim Coil Outside Fan Speed Override |  | recOutsideFanSpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,coil,outside,air,fan,speed,ovr | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOutsideFanSpeedSp | recOutsideFanSpeedSp | Reclaim Coil Outside Fan Speed Setpoint | Reclaim Coil Outside Fan Speed Setpoint |  | recOutsideFanSpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,coil,outside,air,fan,speed,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOutsideFanStatus | recOutsideFanStatus | Reclaim Coil Outside Fan Status | Reclaim Coil Outside Fan Status |  | recOutsideFanStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | reclaim,coil,outside,air,fan,status,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOutsideFilterAlarm | recOutsideFilterAlarm | Reclaim Coil Outside Filter Alarm | Reclaim Coil Outside Filter Alarm |  | recOutsideFilterAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | reclaim,coil,outside,air,filter,general,alarm | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOutsideFilterAlarmReset | recOutsideFilterAlarmReset | Reclaim Coil Outside Filter Alarm Reset | Reclaim Coil Outside Filter Alarm Reset |  | recOutsideFilterAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | reclaim,coil,outside,air,filter,reset,alarm | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOutsideFilterPressureDelta | recOutsideFilterPressureDelta | Reclaim Coil Outside Filter Pressure Delta | Reclaim Coil Outside Filter Pressure Delta |  | recOutsideFilterPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,outside,air,filter,pressure,delta,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released)
recOutsideFilterRuntime | recOutsideFilterRuntime | Reclaim Coil Outside Filter Runtime | Reclaim Coil Outside Filter Runtime |  | recOutsideFilterRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.15 (Released),2.16 (Pre-Release)
recOutsideIsoDamper | recOutsideIsoDamper | Reclaim Coil Outside Isolation Damper Command | Reclaim Coil Outside Isolation Damper Command |  | recOutsideIsoDamper | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | reclaim,coil,outside,iso,air,damper,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOutsideIsoDamperFb | recOutsideIsoDamperFb | Reclaim Coil Outside Isolation Damper Feedback | Reclaim Coil Outside Isolation Damper Feedback |  | recOutsideIsoDamperFb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | reclaim,coil,outside,iso,air,damper,status,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recReturnFanAlarm | recReturnFanAlarm | Reclaim Coil Return Fan Alarm | Reclaim Coil Return Fan Alarm |  | recReturnFanAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | reclaim,coil,return,air,fan,common,alarm | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recReturnFanAlarmReset | recReturnFanAlarmReset | Reclaim Coil Return Fan Alarm Reset | Reclaim Coil Return Fan Alarm Reset |  | recReturnFanAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | reclaim,coil,return,air,fan,alarm,reset | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.15 (Released),2.16 (Pre-Release)
recReturnFan | recReturnFan | Reclaim Coil Return Fan Command | Reclaim Coil Return Fan Command |  | recReturnFan | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | reclaim,coil,return,air,fan,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recReturnFanCurrent | recReturnFanCurrent | Reclaim Coil Return Fan Current | Reclaim Coil Return Fan Current |  | recReturnFanCurrent | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | reclaim,coil,return,air,fan,current,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recReturnFanEnteringPressure | recReturnFanEnteringPressure | Reclaim Coil Return Fan Entering Pressure | Reclaim Coil Return Fan Entering Pressure |  | recReturnFanEnteringPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,return,air,fan,entering,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recReturnFanFault | recReturnFanFault | Reclaim Coil Return Fan Fault | Reclaim Coil Return Fan Fault |  | recReturnFanFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | reclaim,coil,return,air,fan,fault | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recReturnFanLeavingPressure | recReturnFanLeavingPressure | Reclaim Coil Return Fan Leaving Pressure | Reclaim Coil Return Fan Leaving Pressure |  | recReturnFanLeavingPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,return,air,fan,leaving,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recReturnFanMaintSwitch | recReturnFanMaintSwitch | Reclaim Coil Return Fan Maintenance Switch | Reclaim Coil Return Fan Maintenance Switch |  | recReturnFanMaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | reclaim,coil,return,air,fan,maintenance,switch,cmd | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.15 (Released),2.16 (Pre-Release)
recReturnFanOvr | recReturnFanOvr | Reclaim Coil Return Fan Override | Reclaim Coil Return Fan Override |  | recReturnFanOvr | No | No | No | Bool | On/Off | On/Off | [6 empty] | reclaim,coil,return,air,fan,status,ovr | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recReturnFanPressureDelta | recReturnFanPressureDelta | Reclaim Coil Return Fan Pressure Delta | Reclaim Coil Return Fan Pressure Delta |  | recReturnFanPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,return,air,fan,common,pressure,delta,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recReturnFanPressureHiAlarm | recReturnFanPressureHiAlarm | Reclaim Coil Return Fan Pressure High Alarm | Reclaim Coil Return Fan Pressure High Alarm |  | recReturnFanPressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | reclaim,coil,return,air,fan,pressure,high,alarm | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recReturnFanPressureHiSp | recReturnFanPressureHiSp | Reclaim Coil Return Fan Pressure High Setpoint | Reclaim Coil Return Fan Pressure High Setpoint |  | recReturnFanPressureHiSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,return,air,fan,pressure,high,sp | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recReturnFanPressureLoAlarm | recReturnFanPressureLoAlarm | Reclaim Coil Return Fan Pressure Low Alarm | Reclaim Coil Return Fan Pressure Low Alarm |  | recReturnFanPressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | reclaim,coil,return,air,fan,pressure,low,alarm | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recReturnFanPressureLoSp | recReturnFanPressureLoSp | Reclaim Coil Return Fan Pressure Low Setpoint | Reclaim Coil Return Fan Pressure Low Setpoint |  | recReturnFanPressureLoSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,return,air,fan,pressure,low,sp | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recReturnFanRuntime | recReturnFanRuntime | Reclaim Coil Return Fan Runtime | Reclaim Coil Return Fan Runtime |  | recReturnFanRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.15 (Released),2.16 (Pre-Release)
recReturnFanSpeed | recReturnFanSpeed | Reclaim Coil Return Fan Speed | Reclaim Coil Return Fan Speed |  | recReturnFanSpeed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,coil,return,air,fan,speed,cmd | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recReturnFanSpeedFb | recReturnFanSpeedFb | Reclaim Coil Return Fan Speed Feedback | Reclaim Coil Return Fan Speed Feedback |  | recReturnFanSpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,coil,return,air,fan,speed,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recReturnFanSpeedMaxSp | recReturnFanSpeedMaxSp | Reclaim Coil Return Fan Speed Max Setpoint | Reclaim Coil Return Fan Speed Max Setpoint |  | recReturnFanSpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,coil,return,air,fan,speed,max,sp | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recReturnFanSpeedMinSp | recReturnFanSpeedMinSp | Reclaim Coil Return Fan Speed Min Setpoint | Reclaim Coil Return Fan Speed Min Setpoint |  | recReturnFanSpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,coil,return,air,fan,speed,min,sp | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recReturnFanSpeedOvr | recReturnFanSpeedOvr | Reclaim Coil Return Fan Speed Override | Reclaim Coil Return Fan Speed Override |  | recReturnFanSpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,coil,return,air,fan,speed,ovr | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recReturnFanSpeedSp | recReturnFanSpeedSp | Reclaim Coil Return Fan Speed Setpoint | Reclaim Coil Return Fan Speed Setpoint |  | recReturnFanSpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,coil,return,air,fan,speed,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recReturnFanStatus | recReturnFanStatus | Reclaim Coil Return Fan Status | Reclaim Coil Return Fan Status |  | recReturnFanStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | reclaim,coil,return,air,fan,status,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recReturnFilterAlarm | recReturnFilterAlarm | Reclaim Coil Return Filter Alarm | Reclaim Coil Return Filter Alarm |  | recReturnFilterAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | reclaim,coil,return,air,filter,general,alarm | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recReturnFilterAlarmReset | recReturnFilterAlarmReset | Reclaim Coil Return Filter Alarm Reset | Reclaim Coil Return Filter Alarm Reset |  | recReturnFilterAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | reclaim,coil,return,air,filter,reset,alarm | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recReturnFilterPressureDelta | recReturnFilterPressureDelta | Reclaim Coil Return Filter Pressure Delta | Reclaim Coil Return Filter Pressure Delta |  | recReturnFilterPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,return,air,filter,pressure,delta,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released)
recReturnFilterRuntime | recReturnFilterRuntime | Reclaim Coil Return Filter Runtime | Reclaim Coil Return Filter Runtime |  | recReturnFilterRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.15 (Released),2.16 (Pre-Release)
recReturnIsoDamper | recReturnIsoDamper | Reclaim Coil Return Isolation Damper Command | Reclaim Coil Return Isolation Damper Command |  | recReturnIsoDamper | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | reclaim,coil,return,iso,air,damper,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recReturnIsoDamperFb | recReturnIsoDamperFb | Reclaim Coil Return Isolation Damper Feedback | Reclaim Coil Return Isolation Damper Feedback |  | recReturnIsoDamperFb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | reclaim,coil,return,iso,air,damper,status,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recEaCoilEnteringPressure | recEaCoilEnteringPressure | Reclaim Exhaust Coil Entering Pressure | Reclaim Exhaust Coil Entering Pressure |  | recEaCoilEnteringPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,exhaustCoil,entering,air,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recEaCoilExhaustEnthalpy | recEaCoilExhaustEnthalpy | Reclaim Exhaust Coil Exhaust Enthalpy | Reclaim Exhaust Coil Exhaust Enthalpy |  | recEaCoilExhaustEnthalpy | Yes | Yes | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | reclaim,coil,exhaustCoil,exhaust,air,enthalpy,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recEaCoilExhaustFlow | recEaCoilExhaustFlow | Reclaim Exhaust Coil Exhaust Flow | Reclaim Exhaust Coil Exhaust Flow |  | recEaCoilExhaustFlow | Yes | Yes | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | reclaim,coil,exhaustCoil,exhaust,air,flow,sensor | AFMS,AHU,CRAC,CRAH,CU,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recEaCoilExhaustHumidity | recEaCoilExhaustHumidity | Reclaim Exhaust Coil Exhaust Humidity | Reclaim Exhaust Coil Exhaust Humidity |  | recEaCoilExhaustHumidity | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | reclaim,coil,exhaustCoil,exhaust,air,humidity,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recEaCoilExhaustPressure | recEaCoilExhaustPressure | Reclaim Exhaust Coil Exhaust Pressure | Reclaim Exhaust Coil Exhaust Pressure |  | recEaCoilExhaustPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,exhaustCoil,exhaust,air,static,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recEaCoilExhaustTemp | recEaCoilExhaustTemp | Reclaim Exhaust Coil Exhaust Temperature | Reclaim Exhaust Coil Exhaust Temperature |  | recEaCoilExhaustTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | reclaim,coil,exhaustCoil,exhaust,air,temp,sensor | AFMS,AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recEaCoilExhaustVelPressure | recEaCoilExhaustVelPressure | Reclaim Exhaust Coil Exhaust Velocity Pressure | Reclaim Exhaust Coil Exhaust Velocity Pressure |  | recEaCoilExhaustVelPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,exhaustCoil,exhaust,air,dynamic,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recEaCoilLeavingPressure | recEaCoilLeavingPressure | Reclaim Exhaust Coil Leaving Pressure | Reclaim Exhaust Coil Leaving Pressure |  | recEaCoilLeavingPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,exhaustCoil,leaving,air,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recEaCoilLeavingTemp | recEaCoilLeavingTemp | Reclaim Exhaust Coil Leaving Temperature | Reclaim Exhaust Coil Leaving Temperature |  | recEaCoilLeavingTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | reclaim,coil,exhaustCoil,leaving,air,temp,sensor | AFMS,AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recEaCoilReturnVelPressure | recEaCoilReturnVelPressure | Reclaim Exhaust Coil Leaving Velocity Pressure | Reclaim Exhaust Coil Leaving Velocity Pressure |  | recEaCoilReturnVelPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,exhaustCoil,return,air,dynamic,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recEaCoilReturnEnthalpy | recEaCoilReturnEnthalpy | Reclaim Exhaust Coil Return Enthalpy | Reclaim Exhaust Coil Return Enthalpy |  | recEaCoilReturnEnthalpy | Yes | Yes | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | reclaim,coil,exhaustCoil,return,air,enthalpy,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recEaCoilReturnFlow | recEaCoilReturnFlow | Reclaim Exhaust Coil Return Flow | Reclaim Exhaust Coil Return Flow |  | recEaCoilReturnFlow | Yes | Yes | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | reclaim,coil,exhaustCoil,return,air,flow,sensor | AFMS,AHU,CRAC,CRAH,CU,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recEaCoilReturnHumidity | recEaCoilReturnHumidity | Reclaim Exhaust Coil Return Humidity | Reclaim Exhaust Coil Return Humidity |  | recEaCoilReturnHumidity | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | reclaim,coil,exhaustCoil,return,air,humidity,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recEaCoilReturnPressure | recEaCoilReturnPressure | Reclaim Exhaust Coil Return Pressure | Reclaim Exhaust Coil Return Pressure |  | recEaCoilReturnPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,exhaustCoil,return,air,static,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recEaCoilReturnTemp | recEaCoilReturnTemp | Reclaim Exhaust Coil Return Temperature | Reclaim Exhaust Coil Return Temperature |  | recEaCoilReturnTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | reclaim,coil,exhaustCoil,return,air,temp,sensor | AFMS,AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recEaCoilStrainerAlarm | recEaCoilStrainerAlarm | Reclaim Exhaust Coil Strainer Alarm | Reclaim Exhaust Coil Strainer Alarm |  | recEaCoilStrainerAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | reclaim,coil,exhaustCoil,water,strainer,alarm | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recEaCoilStrainerEnable | recEaCoilStrainerEnable | Reclaim Exhaust Coil Strainer Enable | Reclaim Exhaust Coil Strainer Enable |  | recEaCoilStrainerEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | reclaim,coil,exhaustCoil,water,strainer,enable,cmd | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recEaCoilTempDelta | recEaCoilTempDelta | Reclaim Exhaust Coil Temperature Delta | Reclaim Exhaust Coil Temperature Delta |  | recEaCoilTempDelta | Yes | Yes | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | reclaim,coil,exhaustCoil,delta,temp,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recEaCoilFlow | recEaCoilFlow | Reclaim Exhaust Coil Water Flow | Reclaim Exhaust Coil Water Flow |  | recEaCoilFlow | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | reclaim,coil,exhaustCoil,water,flow,sensor | AFMS,AHU,CRAC,CRAH,CU,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recEaCoilEnteringTemp | recEaCoilEnteringTemp | Reclaim Exhuast Coil Entering Temperature | Reclaim Exhuast Coil Entering Temperature |  | recEaCoilEnteringTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | reclaim,coil,exhaustCoil,entering,air,temp,sensor | AFMS,AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recEaCoilPressureDelta | recEaCoilPressureDelta | Reclaim Exhuast Coil Pressure Delta | Reclaim Exhuast Coil Pressure Delta |  | recEaCoilPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,exhaustCoil,delta,air,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOaCoilDischargeEnthalpy | recOaCoilDischargeEnthalpy | Reclaim Outside Coil Discharge Enthalpy | Reclaim Outside Coil Discharge Enthalpy |  | recOaCoilDischargeEnthalpy | Yes | Yes | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | reclaim,coil,outsideCoil,discharge,air,enthalpy,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOaCoilDischargeFlow | recOaCoilDischargeFlow | Reclaim Outside Coil Discharge Flow | Reclaim Outside Coil Discharge Flow |  | recOaCoilDischargeFlow | Yes | Yes | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | reclaim,coil,outsideCoil,discharge,air,flow,sensor | AFMS,AHU,CRAC,CRAH,CU,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOaCoilDischargeHumidity | recOaCoilDischargeHumidity | Reclaim Outside Coil Discharge Humidity | Reclaim Outside Coil Discharge Humidity |  | recOaCoilDischargeHumidity | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | reclaim,coil,outsideCoil,discharge,air,humidity,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOaCoilDischargePressure | recOaCoilDischargePressure | Reclaim Outside Coil Discharge Pressure | Reclaim Outside Coil Discharge Pressure |  | recOaCoilDischargePressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,outsideCoil,discharge,air,static,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOaCoilDischargeTemp | recOaCoilDischargeTemp | Reclaim Outside Coil Discharge Temperature | Reclaim Outside Coil Discharge Temperature |  | recOaCoilDischargeTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | reclaim,coil,outsideCoil,discharge,air,temp,sensor | AFMS,AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOaCoilDischargeVelPressure | recOaCoilDischargeVelPressure | Reclaim Outside Coil Discharge Velocity Pressure | Reclaim Outside Coil Discharge Velocity Pressure |  | recOaCoilDischargeVelPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,outsideCoil,discharge,air,dynamic,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOaCoilEnteringPressure | recOaCoilEnteringPressure | Reclaim Outside Coil Entering Pressure | Reclaim Outside Coil Entering Pressure |  | recOaCoilEnteringPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,outsideCoil,entering,air,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOaCoilEnteringTemp | recOaCoilEnteringTemp | Reclaim Outside Coil Entering Temperature | Reclaim Outside Coil Entering Temperature |  | recOaCoilEnteringTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | reclaim,coil,outsideCoil,entering,air,temp,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOaCoilLeavingPressure | recOaCoilLeavingPressure | Reclaim Outside Coil Leaving Pressure | Reclaim Outside Coil Leaving Pressure |  | recOaCoilLeavingPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,outsideCoil,leaving,air,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOaCoilLeavingTemp | recOaCoilLeavingTemp | Reclaim Outside Coil Leaving Temperature | Reclaim Outside Coil Leaving Temperature |  | recOaCoilLeavingTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | reclaim,coil,outsideCoil,leaving,air,temp,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOaCoilOutsideEnthalpy | recOaCoilOutsideEnthalpy | Reclaim Outside Coil Outside Enthalpy | Reclaim Outside Coil Outside Enthalpy |  | recOaCoilOutsideEnthalpy | Yes | Yes | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | reclaim,coil,outsideCoil,outside,air,enthalpy,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOaCoilOutsideFlow | recOaCoilOutsideFlow | Reclaim Outside Coil Outside Flow | Reclaim Outside Coil Outside Flow |  | recOaCoilOutsideFlow | Yes | Yes | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | reclaim,coil,outsideCoil,outside,air,flow,sensor | AFMS,AHU,CRAC,CRAH,CU,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOaCoilOutsideHumidity | recOaCoilOutsideHumidity | Reclaim Outside Coil Outside Humidity | Reclaim Outside Coil Outside Humidity |  | recOaCoilOutsideHumidity | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | reclaim,coil,outsideCoil,outside,air,humidity,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOaCoilOutsidePressure | recOaCoilOutsidePressure | Reclaim Outside Coil Outside Pressure | Reclaim Outside Coil Outside Pressure |  | recOaCoilOutsidePressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,outsideCoil,outside,air,static,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOaCoilOutsideTemp | recOaCoilOutsideTemp | Reclaim Outside Coil Outside Temperature | Reclaim Outside Coil Outside Temperature |  | recOaCoilOutsideTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | reclaim,coil,outsideCoil,outside,air,temp,sensor | AFMS,AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOaCoilOutsideVelPressure | recOaCoilOutsideVelPressure | Reclaim Outside Coil Outside Velocity Pressure | Reclaim Outside Coil Outside Velocity Pressure |  | recOaCoilOutsideVelPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,outsideCoil,outside,air,dynamic,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOaCoilPressureDelta | recOaCoilPressureDelta | Reclaim Outside Coil Pressure Delta | Reclaim Outside Coil Pressure Delta |  | recOaCoilPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | reclaim,coil,outsideCoil,air,pressure,delta,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOaCoilStrainerAlarm | recOaCoilStrainerAlarm | Reclaim Outside Coil Strainer Alarm | Reclaim Outside Coil Strainer Alarm |  | recOaCoilStrainerAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | reclaim,coil,outsideCoil,water,strainer,alarm | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOaCoilStrainerEnable | recOaCoilStrainerEnable | Reclaim Outside Coil Strainer Enable | Reclaim Outside Coil Strainer Enable |  | recOaCoilStrainerEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | reclaim,coil,outsideCoil,water,strainer,enable,cmd | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOaCoilTempDelta | recOaCoilTempDelta | Reclaim Outside Coil Temperature Delta | Reclaim Outside Coil Temperature Delta |  | recOaCoilTempDelta | Yes | Yes | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | reclaim,coil,outsideCoil,delta,temp,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recOaCoilFlow | recOaCoilFlow | Reclaim Outside Coil Water Flow | Reclaim Outside Coil Water Flow |  | recOaCoilFlow | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | reclaim,coil,outsideCoil,water,flow,sensor | AFMS,AHU,CRAC,CRAH,CU,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recPumpAlarm | recPumpXXXXAlarm | Reclaim Pump Alarm | Reclaim Pump XX Alarm |  | recPump(\w{0,4}(?=[A-Z]¦$))Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | reclaim,water,pump,common,alarm | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recPumpAlarmReset | recPumpXXXXAlarmReset | Reclaim Pump Alarm Reset | Reclaim Pump XX Alarm Reset |  | recPump(\w{0,4}(?=[A-Z]¦$))AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | reclaim,water,pump,reset,alarm | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recPump | recPumpXXXX | Reclaim Pump Command | Reclaim Pump XX Command |  | recPump((?:(?!Lead)(?!Ovr)\w){0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | reclaim,water,pump,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.15 (Released),2.16 (Pre-Release)
recPumpCurrent | recPumpXXXXCurrent | Reclaim Pump Current | Reclaim Pump XX Current |  | recPump(\w{0,4}(?=[A-Z]¦$))Current | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | reclaim,water,pump,current,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recPumpEnable | recPumpXXXXEnable | Reclaim Pump Enable | Reclaim Pump XX Enable |  | recPump(\w{0,4}(?=[A-Z]¦$))Enable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | reclaim,water,pump,enable,cmd | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recPumpEnableDb | recPumpXXXXEnableDb | Reclaim Pump Enable Deadband | Reclaim Pump XX Enable Deadband |  | recPump(\w{0,4}(?=[A-Z]¦$))EnableDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | reclaim,water,pump,enable,deadband,sp | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.15 (Released),2.16 (Pre-Release)
recPumpEnableSp | recPumpXXXXEnableSp | Reclaim Pump Enable Setpoint | Reclaim Pump XX Enable Setpoint |  | recPump((?:(?!Lag)\w){0,4}(?=[A-Z]¦$))EnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | reclaim,water,pump,enable,sp,common | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.14,2.15 (Released),2.16 (Pre-Release)
recPumpEnteringPressure | recPumpXXXXEnteringPressure | Reclaim Pump Entering Pressure | Reclaim Pump XX Entering Pressure |  | recPump(\w{0,4}(?=[A-Z]¦$))EnteringPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | reclaim,water,pump,entering,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recPumpFault | recPumpXXXXFault | Reclaim Pump Fault | Reclaim Pump XX Fault |  | recPump(\w{0,4}(?=[A-Z]¦$))Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | reclaim,water,pump,fault,common | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recPumpLagDisableSp | recPumpXXXXLagDisableSp | Reclaim Pump Lag Disable Setpoint | Reclaim Pump XX Lag Disable Setpoint |  | recPump(\w{0,4}(?=[A-Z]¦$))LagDisableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,water,pump,lag,disable,sp | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recPumpLagEnableSp | recPumpXXXXLagEnableSp | Reclaim Pump Lag Enable Setpoint | Reclaim Pump XX Lag Enable Setpoint |  | recPump(\w{0,4}(?=[A-Z]¦$))LagEnableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,water,pump,lag,enable,sp | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recPumpLagReq | recPumpXXXXLagReq | Reclaim Pump Lag Request | Reclaim Pump XX Lag Request |  | recPump(\w{0,4}(?=[A-Z]¦$))LagReq | No | No | No | Bool | Request/No Request | Request/No Request | [6 empty] | reclaim,water,pump,lag,request,cmd | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recPumpLead | recPumpLead | Reclaim Pump Lead | Reclaim Pump Lead |  | recPumpLead | Yes | Yes | No | Bool | Lead 1/Lead 2 | Lead 1/Lead 2 | [6 empty] | reclaim,water,pump,lead,sp | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.15 (Released),2.16 (Pre-Release)
recPumpLeadXor | recPumpLeadXor | Reclaim Pump Lead Change Over | Reclaim Pump Lead Change Over |  | recPumpLeadXor | No | No | No | Bool | On/Off | On/Off | [6 empty] | reclaim,water,pump,lead,changeOver,cmd | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.15 (Released),2.16 (Pre-Release)
recPumpLeadXorRuntimeSp | recPumpLeadXorRuntimeSp | Reclaim Pump Lead Change Over Runtime Setpoint | Reclaim Pump Lead Change Over Runtime Setpoint |  | recPumpLeadXorRuntimeSp | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.15 (Released),2.16 (Pre-Release)
recPumpLeavingPressure | recPumpXXXXLeavingPressure | Reclaim Pump Leaving Pressure | Reclaim Pump XX Leaving Pressure |  | recPump(\w{0,4}(?=[A-Z]¦$))LeavingPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | reclaim,water,pump,leaving,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recPumpMaintSwitch | recPumpXXXXMaintSwitch | Reclaim Pump Maintenance Switch | Reclaim Pump XX Maintenance Switch |  | recPump(\w{0,4}(?=[A-Z]¦$))MaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | reclaim,water,pump,maintenance,switch,cmd | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.15 (Released),2.16 (Pre-Release)
recPumpOvr | recPumpXXXXOvr | Reclaim Pump Override | Reclaim Pump XX Override |  | recPump(\w{0,4}(?=[A-Z]¦$))Ovr | No | No | No | Bool | On/Off | On/Off | [6 empty] | reclaim,water,pump,status,ovr | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recPumpPressureDelta | recPumpXXXXPressureDelta | Reclaim Pump Pressure Delta | Reclaim Pump XX Pressure Delta |  | recPump(\w{0,4}(?=[A-Z]¦$))PressureDelta | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | reclaim,water,pump,common,pressure,delta,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recPumpPressureHiAlarm | recPumpXXXXPressureHiAlarm | Reclaim Pump Pressure High Alarm | Reclaim Pump XX Pressure High Alarm |  | recPump(\w{0,4}(?=[A-Z]¦$))PressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | reclaim,water,pump,pressure,high,alarm | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recPumpPressureHiSp | recPumpXXXXPressureHiSp | Reclaim Pump Pressure High Setpoint | Reclaim Pump XX Pressure High Setpoint |  | recPump(\w{0,4}(?=[A-Z]¦$))PressureHiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | reclaim,water,pump,pressure,high,sp | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recPumpPressureLoAlarm | recPumpXXXXPressureLoAlarm | Reclaim Pump Pressure Low Alarm | Reclaim Pump XX Pressure Low Alarm |  | recPump(\w{0,4}(?=[A-Z]¦$))PressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | reclaim,water,pump,pressure,low,alarm | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recPumpPressureLoSp | recPumpXXXXPressureLoSp | Reclaim Pump Pressure Low Setpoint | Reclaim Pump XX Pressure Low Setpoint |  | recPump(\w{0,4}(?=[A-Z]¦$))PressureLoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | reclaim,water,pump,pressure,low,sp | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recPumpRuntime | recPumpXXXXRuntime | Reclaim Pump Runtime | Reclaim Pump XX Runtime |  | recPump(\w{0,4}(?=[A-Z]¦$))Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.15 (Released),2.16 (Pre-Release)
recPumpSpeed | recPumpXXXXSpeed | Reclaim Pump Speed | Reclaim Pump XX Speed |  | recPump(\w{0,4}(?=[A-Z]¦$))Speed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,water,pump,speed,cmd | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recPumpSpeedFb | recPumpXXXXSpeedFb | Reclaim Pump Speed Feedback | Reclaim Pump XX Speed Feedback |  | recPump(\w{0,4}(?=[A-Z]¦$))SpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,water,pump,speed,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recPumpSpeedMaxSp | recPumpXXXXSpeedMaxSp | Reclaim Pump Speed Max Setpoint | Reclaim Pump XX Speed Max Setpoint |  | recPump(\w{0,4}(?=[A-Z]¦$))SpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,water,pump,speed,max,sp | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recPumpSpeedMinSp | recPumpXXXXSpeedMinSp | Reclaim Pump Speed Min Setpoint | Reclaim Pump XX Speed Min Setpoint |  | recPump(\w{0,4}(?=[A-Z]¦$))SpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,water,pump,speed,min,sp | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recPumpSpeedOvr | recPumpXXXXSpeedOvr | Reclaim Pump Speed Override | Reclaim Pump XX Speed Override |  | recPump(\w{0,4}(?=[A-Z]¦$))SpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,water,pump,speed,ovr | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recPumpSpeedSp | recPumpXXXXSpeedSp | Reclaim Pump Speed Setpoint | Reclaim Pump XX Speed Setpoint |  | recPump(\w{0,4}(?=[A-Z]¦$))SpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | reclaim,water,pump,speed,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
recPumpStatus | recPumpXXXXStatus | Reclaim Pump Status | Reclaim Pump XX Status |  | recPump(\w{0,4}(?=[A-Z]¦$))Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | reclaim,water,pump,status,sensor | AHU,CRAC,CRAH,DHU,DOAS,REC,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
rectifierAlarm | rectifierAlarm | Rectifier Alarm | Rectifier Alarm |  | rectifierAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | rectifier,alarm | RECT,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
rectifierStatus | rectifierStatus | Rectifier Status | Rectifier Status |  | rectifierStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | rectifier,status,sensor | RECT,UPS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
refrigAlarm | refrigAlarm | Refrigerant Alarm | Refrigerant Alarm |  | refrigAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | refrig,general,common,alarm | AC,AHU,CRAC,CRAH,CU,DHU,DOAS,FCU,HP,RTU,VRF,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
refrigCoil | refrigCoilXXXX | Refrigerant Coil Command | Refrigerant Coil XX Comamnd |  | refrigCoil(\d{0,4}) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | refrig,coil,cmd | AC,AHU,CRAC,CRAH,DHU,DOAS,FCU,HP,RTU,VRF,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
refrigCoilDemand | refrigCoilXXXXDemand | Refrigerant Coil Demand | Refrigerant Coil XX Demand |  | refrigCoil(\d{0,4})Demand | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | refrig,coil,demand,sensor | AC,AHU,CRAC,CRAH,DHU,DOAS,FCU,HP,RTU,VRF,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
refrigCoilDischargeHumidity | refrigCoilXXXXDischargeHumidity | Refrigerant Coil Discharge Humidity | Refrigerant Coil XX Discharge Humidity |  | refrigCoil(\d{0,4})DischargeHumidity | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | refrig,coil,discharge,humidity,sensor | AC,AHU,CRAC,CRAH,DHU,DOAS,FCU,HP,RTU,VRF,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
refrigCoilDischargeTemp | refrigCoilXXXXDischargeTemp | Refrigerant Coil Discharge Temperature | Refrigerant Coil XX Discharge Temperature |  | refrigCoil(\d{0,4})DischargeTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | refrig,coil,discharge,temp,sensor | AC,AFMS,AHU,CRAC,CRAH,DHU,DOAS,FCU,HP,RTU,VRF,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
refrigCoilFilterAlarm | refrigCoilFilterXXXXAlarm | Refrigerant Coil Filter Alarm | Refrigerant Coil Filter XX Alarm |  | refrigCoilFilter(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | refrig,filter,common,alarm | AC,AHU,CRAC,CRAH,DHU,DOAS,FCU,HP,RTU,VRF,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
refrigCoilFilterAlarmReset | refrigCoilFilterXXXXAlarmReset | Refrigerant Coil Filter Alarm Reset | Refrigerant Coil Filter XX Alarm Reset |  | refrigCoilFilter(\d{0,4})AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | refrig,filter,reset,alarm | AC,AHU,CRAC,CRAH,DHU,DOAS,FCU,HP,RTU,VRF,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
refrigCoilGasTemp | refrigCoilXXXXGasTemp | Refrigerant Coil Gas Temperature | Refrigerant Coil XX Gas Temperature |  | refrigCoil(\d{0,4})GasTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | refrig,coil,gas,temp,sensor | AC,AHU,CRAC,CRAH,DHU,DOAS,FCU,HP,RTU,VRF,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
refrigCoilLiquidTemp | refrigCoilXXXXLiquidTemp | Refrigerant Coil Liquid Temperature | Refrigerant Coil XX Liquid Temperature |  | refrigCoil(\d{0,4})LiquidTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | refrig,coil,liquid,temp,sensor | AC,AHU,CRAC,CRAH,DHU,DOAS,FCU,HP,RTU,VRF,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
refrigCoilTempDelta | refrigCoilXXXXTempDelta | Refrigerant Coil Temperature Differential | Refrigerant Coil XX Temperature Differential |  | refrigCoil(\d{0,4})TempDelta | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | refrig,coil,delta,temp,sensor | AC,AHU,CRAC,CRAH,DHU,DOAS,FCU,HP,RTU,VRF,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
refrigLeakAlarm | refrigLeakXXXXAlarm | Refrigerant Leak Alarm | Refrigerant Leak XX Alarm |  | refrigLeak(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | refrig,leak,effective,alarm | CU,CWS,MSC,RFG,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
refrigLeakHiAlarm | refrigLeakXXXXHiAlarm | Refrigerant Leak High Alarm | Refrigerant Leak XX High Alarm |  | refrigLeak(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | refrig,leak,high,alarm,sp | CU,CWS,MSC,RFG,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
refrigLeakLoAlarm | refrigLeakXXXXLoAlarm | Refrigerant Leak Low Alarm | Refrigerant Leak XX Low Alarm |  | refrigLeak(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | refrig,leak,low,alarm,sp | CU,CWS,MSC,RFG,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
refrigStatus | refrigStatus | Refrigerant Status | Refrigerant Status |  | refrigStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | refrig,coil,status,sensor | AC,AHU,CRAC,CRAH,DHU,DOAS,FCU,HP,RTU,VRF,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reliefDamper | reliefDamperXXXX | Relief Damper Command | Relief Damper XX Command |  | reliefDamper(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | relief,air,damper,position,cmd | MSC,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reliefDamperFb | reliefDamperXXXXFb | Relief Damper Feedback | Relief Damper XX Feedback |  | reliefDamper(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | relief,air,damper,position,sensor | MSC,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reliefDamperOvr | reliefDamperXXXXOvr | Relief Damper Override | Relief Damper XX Override |  | reliefDamper(\d{0,4})Ovr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | relief,air,damper,position,ovr | MSC,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
remoteStart | remoteStart | Remote Start | Remote Start |  | remoteStart | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | remote,start,cmd | GEN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFlow | returnFlowXXXX | Return Airflow | Return Airflow XX |  | returnFlow(\d{0,4}) | Yes | Yes | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | return,air,flow,general,sensor | AFMS,AHU,ATU,CRAC,CRAH,CU,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFlowAlarm | returnFlowXXXXAlarm | Return Airflow Alarm | Return Airflow XX Alarm |  | returnFlow(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | return,air,flow,alarm | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFlowDb | returnFlowXXXXDb | Return Airflow Deadband | Return Airflow XX Deadband |  | returnFlow(\d{0,4})Db | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | return,air,flow,deadband,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFlowFault | returnFlowXXXXFault | Return Airflow Fault | Return Airflow XX Fault |  | returnFlow(\d{0,4})Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | return,air,flow,fault | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFlowHiSp | returnFlowXXXXHiSp | Return Airflow High Setpoint | Return Airflow XX High Setpoint |  | returnFlow(\d{0,4})HiSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | return,air,flow,high,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFlowLoSp | returnFlowXXXXLoSp | Return Airflow Low Setpoint | Return Airflow XX Low Setpoint |  | returnFlow(\d{0,4})LoSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | return,air,flow,low,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFlowMaxSp | returnFlowXXXXMaxSp | Return Airflow Max Reset Setpoint | Return Airflow XX Max Reset Setpoint |  | returnFlow(\d{0,4})MaxSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | return,air,flow,max,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFlowMinSp | returnFlowXXXXMinSp | Return Airflow Min Reset Setpoint | Return Airflow XX Min Reset Setpoint |  | returnFlow(\d{0,4})MinSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | return,air,flow,min,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFlowOccSp | returnFlowXXXXOccSp | Return Airflow Occupied Setpoint | Return Airflow XX Occupied Setpoint |  | returnFlow(\d{0,4})OccSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | return,air,flow,occupied,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFlowOffsetSp | returnFlowXXXXOffsetSp | Return Airflow Offset Setpoint | Return Airflow XX Offset Setpoint |  | returnFlow(\d{0,4})OffsetSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | return,air,flow,offset,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFlowSp | returnFlowXXXXSp | Return Airflow Setpoint | Return Airflow XX Setpoint |  | returnFlow(\d{0,4})Sp | Yes | Yes | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | return,air,flow,effective,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFlowStatus | returnFlowXXXXStatus | Return Airflow Status | Return Airflow XX Status |  | returnFlow(\d{0,4})Status | Yes | Yes | No | Bool | Flow/No Flow | Flow/No Flow | [6 empty] | return,air,flow,status,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFlowUnoccSp | returnFlowXXXXUnoccSp | Return Airflow Unoccupied Setpoint | Return Airflow XX Unoccupied Setpoint |  | returnFlow(\d{0,4})UnoccSp | No | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | return,air,flow,unoccupied,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnCO | returnCOXXXX | Return CO | Return CO XX |  | returnCO(?:(?!2)(\d{0,4})?) | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | return,air,co,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnCO2 | returnCO2XXXX | Return CO2 | Return CO2 XX |  | returnCO2(\d{0,4}) | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | return,air,co2,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnCO2Db | returnCO2XXXXDb | Return CO2 Deadband | Return CO2 XX Deadband |  | returnCO2(\d{0,4})Db | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | return,air,co2,deadband,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnCO2Fault | returnCO2XXXXFault | Return CO2 Fault | Return CO2 XX Fault |  | returnCO2(\d{0,4})Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | return,air,co2,fault | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnCO2HiSp | returnCO2XXXXHiSp | Return CO2 High Reset Setpoint | Return CO2 XX High Reset Setpoint |  | returnCO2(\d{0,4})HiSp | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | return,air,co2,high,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnCO2LoSp | returnCO2XXXXLoSp | Return CO2 Low Reset Setpoint | Return CO2 XX Low Reset Setpoint |  | returnCO2(\d{0,4})LoSp | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | return,air,co2,low,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnCO2MaxSp | returnCO2XXXXMaxSp | Return CO2 Max Reset Setpoint | Return CO2 XX Max Reset Setpoint |  | returnCO2(\d{0,4})MaxSp | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | return,air,co2,max,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnCO2MinSp | returnCO2XXXXMinSp | Return CO2 Min Reset Setpoint | Return CO2 XX Min Reset Setpoint |  | returnCO2(\d{0,4})MinSp | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | return,air,co2,min,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnCO2Sp | returnCO2XXXXSp | Return CO2 Setpoint | Return CO2 XX Setpoint |  | returnCO2(\d{0,4})Sp | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | return,air,co2,effective,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnDamper | returnDamperXXXX | Return Damper | Return Damper XX |  | returnDamper(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | common,return,air,damper,position,cmd | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnDamperAlarm | returnDamperXXXXAlarm | Return Damper Alarm | Return Damper XX Alarm |  | returnDamper(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | common,return,air,damper,alarm | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnDamperFb | returnDamperXXXXFb | Return Damper Feedback | Return Damper XX Feedback |  | returnDamper(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | common,return,air,damper,position,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnDamperMaxSp | returnDamperXXXXMaxSp | Return Damper Maximum Setpoint | Return Damper XX Maximum Setpoint |  | returnDamper(\d{0,4})MaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | common,return,air,damper,position,max,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnDamperMinSp | returnDamperXXXXMinSp | Return Damper Minimum Setpoint | Return Damper XX Minimum Setpoint |  | returnDamper(\d{0,4})MinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | common,return,air,damper,position,min,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnDamperOvr | returnDamperXXXXOvr | Return Damper Override | Return Damper XX Override |  | returnDamper(\d{0,4})Ovr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | common,return,air,damper,position,ovr | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnDehumidDb | returnDehumidXXXXDb | Return Dehumidification Deadband | Return Dehumidification XX Deadband |  | returnDehumid(\d{0,4})Db | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | return,air,dehumid,deadband,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnDehumidMaxSp | returnDehumidXXXXMaxSp | Return Dehumidification Max Reset Setpoint | Return Dehumidification XX Max Reset Setpoint |  | returnDehumid(\d{0,4})MaxSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | return,air,dehumid,max,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnDehumidMinSp | returnDehumidXXXXMinSp | Return Dehumidification Min Reset Setpoint | Return Dehumidification XX Min Reset Setpoint |  | returnDehumid(\d{0,4})MinSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | return,air,dehumid,min,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnDehumidSp | returnDehumidXXXXSp | Return Dehumidification Setpoint | Return Dehumidification XX Setpoint |  | returnDehumid(\d{0,4})Sp | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | return,air,dehumid,effective,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnDewpoint | returnDewpointXXXX | Return Dewpoint | Return Dewpoint XX |  | returnDewpoint(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | return,air,dewpoint,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnDewpointDb | returnDewpointXXXXDb | Return Dewpoint Deadband | Return Dewpoint XX Deadband |  | returnDewpoint(\d{0,4})Db | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | return,air,dewpoint,deadband,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnDewpointHiSp | returnDewpointXXXXHiSp | Return Dewpoint High Setpoint | Return Dewpoint XX High Setpoint |  | returnDewpoint(\d{0,4})HiSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | return,air,dewpoint,high,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnDewpointLoSp | returnDewpointXXXXLoSp | Return Dewpoint Low Setpoint | Return Dewpoint XX Low Setpoint |  | returnDewpoint(\d{0,4})LoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | return,air,dewpoint,low,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnDewpointMaxSp | returnDewpointXXXXMaxSp | Return Dewpoint Max Reset Setpoint | Return Dewpoint XX Max Reset Setpoint |  | returnDewpoint(\d{0,4})MaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | return,air,dewpoint,max,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnDewpointMinSp | returnDewpointXXXXMinSp | Return Dewpoint Min Reset Setpoint | Return Dewpoint XX Min Reset Setpoint |  | returnDewpoint(\d{0,4})MinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | return,air,dewpoint,min,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnDewpointSp | returnDewpointXXXXSp | Return Dewpoint Setpoint | Return Dewpoint XX Setpoint |  | returnDewpoint(\d{0,4})Sp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | return,air,dewpoint,effective,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnEnthalpy | returnEnthalpyXXXX | Return Enthalpy | Return Enthalpy XX |  | returnEnthalpy(\d{0,4}) | Yes | Yes | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | return,air,enthalpy,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnEnthalpyDb | returnEnthalpyXXXXDb | Return Enthalpy Deadband | Return Enthalpy XX Deadband |  | returnEnthalpy(\d{0,4})Db | No | No | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | return,air,enthalpy,deadband,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnEnthalpyHiSp | returnEnthalpyXXXXHiSp | Return Enthalpy High Setpoint | Return Enthalpy XX High Setpoint |  | returnEnthalpy(\d{0,4})HiSp | No | No | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | return,air,enthalpy,high,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnEnthalpyLoSp | returnEnthalpyXXXXLoSp | Return Enthalpy Low Setpoint | Return Enthalpy XX Low Setpoint |  | returnEnthalpy(\d{0,4})LoSp | No | No | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | return,air,enthalpy,low,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnEnthalpyMaxSp | returnEnthalpyXXXXMaxSp | Return Enthalpy Max Setpoint | Return Enthalpy XX Max Setpoint |  | returnEnthalpy(\d{0,4})MaxSp | No | No | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | return,air,enthalpy,max,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnEnthalpyMinSp | returnEnthalpyXXXXMinSp | Return Enthalpy Min Setpoint | Return Enthalpy XX Min Setpoint |  | returnEnthalpy(\d{0,4})MinSp | No | No | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | return,air,enthalpy,min,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnEnthalpySp | returnEnthalpyXXXXSp | Return Enthalpy Setpoint | Return Enthalpy XX Setpoint |  | returnEnthalpy(\d{0,4})Sp | Yes | Yes | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | return,air,enthalpy,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanAlarm | returnFanXXXXAlarm | Return Fan Alarm | Return Fan XX Alarm |  | returnFan(\w{0,4}(?=[A-Z]¦$))Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | return,air,fan,general,common,alarm | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanAlarmReset | returnFanXXXXAlarmReset | Return Fan Alarm Reset | Return Fan XX Alarm Reset |  | returnFan(\w{0,4}(?=[A-Z]¦$))AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | return,air,fan,general,reset,alarm | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFan | returnFanXXXX | Return Fan Command | Return Fan XX Command |  | returnFan((?:(?!Lead)(?!Mode)(?!Ovr)\w){0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | return,air,fan,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanCurrent | returnFanXXXXCurrent | Return Fan Current | Return Fan XX Current |  | returnFan(\w{0,4}(?=[A-Z]¦$))Current | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | return,air,fan,current,sensor | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanEnteringPressure | returnFanXXXXEnteringPressure | Return Fan Entering Pressure | Return Fan XX Entering Pressure |  | returnFan(\w{0,4}(?=[A-Z]¦$))EnteringPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | return,air,fan,entering,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanFault | returnFanXXXXFault | Return Fan Fault | Return Fan XX Fault |  | returnFan(\w{0,4}(?=[A-Z]¦$))Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | return,air,fan,fault,common | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanFilterAlarm | returnFanXXXXFilterAlarm | Return Fan Filter Alarm | Return Fan XX Filter Alarm |  | returnFan(\w{0,4}(?=[A-Z]¦$))FilterAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | return,air,fan,filter,common,alarm | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanFilterAlarmReset | returnFanXXXXFilterAlarmReset | Return Fan Filter Alarm Reset | Return Fan XX Filter Alarm Reset |  | returnFan(\w{0,4}(?=[A-Z]¦$))FilterAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | return,air,fan,filter,reset,alarm | AHU,CRAC,CRAH,DHU,DOAS,EC,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanFilterPressureDelta | returnFanXXXXFilterPressureDelta | Return Fan Filter Pressure Delta | Return Fan XX Filter Pressure Delta |  | returnFan(\w{0,4}(?=[A-Z]¦$))FilterPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | return,air,fan,filter,pressure,delta,sensor | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released)
returnFanFilterRuntime | returnFanXXXXFilterRuntime | Return Fan Filter Runtime | Return Fan XX Filter Runtime |  | returnFan(\w{0,4}(?=[A-Z]¦$))FilterRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.15 (Released),2.16 (Pre-Release)
returnFanLead | returnFanLead | Return Fan Lead | Return Fan Lead |  | returnFanLead | Yes | Yes | No | Bool | Lead 1/Lead 2 | Lead 1/Lead 2 | [6 empty] | return,air,fan,lead,sp | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanLeadXor | returnFanLeadXor | Return Fan Lead Change Over | Return Fan Lead Change Over |  | returnFanLeadXor | No | No | No | Bool | On/Off | On/Off | [6 empty] | return,air,fan,lead,changeOver,cmd | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanLeadXorRuntimeSp | returnFanLeadXorRuntimeSp | Return Fan Lead Change Over Runtime Setpoint | Return Fan Lead Change Over Runtime Setpoint |  | returnFanLeadXorRuntimeSp | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanLeavingPressure | returnFanXXXXLeavingPressure | Return Fan Leaving Pressure | Return Fan XX Leaving Pressure |  | returnFan(\w{0,4}(?=[A-Z]¦$))LeavingPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | return,air,fan,leaving,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanMaintSwitch | returnFanXXXXMaintSwitch | Return Fan Maintenance Switch | Return Fan XX Maintenance Switch |  | returnFan(\w{0,4}(?=[A-Z]¦$))MaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | return,air,fan,maintenance,switch,cmd | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanMode | returnFanXXXXMode | Return Fan Mode | Return Fan XX Mode |  | returnFan((?:(?!Hand)\w){0,4}(?=[A-Z]¦$))Mode | Yes | No | No | Str | Continuous/Cycling | Continuous/Cycling | [6 empty] | blacklist | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanModeOvr | returnFanXXXXModeOvr | Return Fan Mode Override | Return Fan XX Mode Override |  | returnFan((?:(?!Hand)\w){0,4}(?=[A-Z]¦$))ModeOvr | Yes | No | No | Str | Continuous/Cycling | Continuous/Cycling | [6 empty] | blacklist | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.15 (Released),2.16 (Pre-Release)
returnFanOvr | returnFanXXXXOvr | Return Fan Override | Return Fan XX Override |  | returnFan((?:(?!Mode)\w){0,4}(?=[A-Z]¦$))Ovr | No | No | No | Bool | On/Off | On/Off | [6 empty] | return,air,fan,status,ovr | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.15 (Released),2.16 (Pre-Release)
returnFanPressureDelta | returnFanXXXXPressureDelta | Return Fan Pressure Delta | Return Fan XX Pressure Delta |  | returnFan(\w{0,4}(?=[A-Z]¦$))PressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | return,air,fan,common,pressure,delta,sensor | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanPressureHiAlarm | returnFanXXXXPressureHiAlarm | Return Fan Pressure High Alarm | Return Fan XX Pressure High Alarm |  | returnFan(\w{0,4}(?=[A-Z]¦$))PressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | return,air,fan,pressure,high,alarm | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanPressureHiSp | returnFanXXXXPressureHiSp | Return Fan Pressure High Setpoint | Return Fan XX Pressure High Setpoint |  | returnFan(\w{0,4}(?=[A-Z]¦$))PressureHiSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | return,air,fan,pressure,high,sp | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanPressureLoAlarm | returnFanXXXXPressureLoAlarm | Return Fan Pressure Low Alarm | Return Fan XX Pressure Low Alarm |  | returnFan(\w{0,4}(?=[A-Z]¦$))PressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | return,air,fan,pressure,low,alarm | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanPressureLoSp | returnFanXXXXPressureLoSp | Return Fan Pressure Low Setpoint | Return Fan XX Pressure Low Setpoint |  | returnFan(\w{0,4}(?=[A-Z]¦$))PressureLoSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | return,air,fan,pressure,low,sp | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanRuntime | returnFanXXXXRuntime | Return Fan Runtime | Return Fan XX Runtime |  | returnFan(\w{0,4}(?=[A-Z]¦$))Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.15 (Released),2.16 (Pre-Release)
returnFanSpeed | returnFanXXXXSpeed | Return Fan Speed | Return Fan XX Speed |  | returnFan(\w{0,4}(?=[A-Z]¦$))Speed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | return,air,fan,speed,common,cmd | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanSpeedFb | returnFanXXXXSpeedFb | Return Fan Speed Feedback | Return Fan XX Speed Feedback |  | returnFan(\w{0,4}(?=[A-Z]¦$))SpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | return,air,fan,speed,sensor | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanSpeedMaxSp | returnFanXXXXSpeedMaxSp | Return Fan Speed Max Setpoint | Return Fan XX Speed Max Setpoint |  | returnFan(\w{0,4}(?=[A-Z]¦$))SpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | return,air,fan,speed,max,sp | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanSpeedMinSp | returnFanXXXXSpeedMinSp | Return Fan Speed Min Setpoint | Return Fan XX Speed Min Setpoint |  | returnFan(\w{0,4}(?=[A-Z]¦$))SpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | return,air,fan,speed,min,sp | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanSpeedMode | returnFanXXXXSpeedMode | Return Fan Speed Mode | Return Fan XX Speed Mode |  | returnFan(\w{0,4}(?=[A-Z]¦$))SpeedMode | Yes | No | No | Str |  | Constant Volume/Fixed Variable Speed/Pressure Controlled | [6 empty] | return,air,fan,speed,mode,sp | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanSpeedOccSp | returnFanXXXXSpeedOccSp | Return Fan Speed Occupied Setpoint | Return Fan XX Speed Occupied Setpoint |  | returnFan(\w{0,4}(?=[A-Z]¦$))SpeedOccSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | return,air,fan,speed,occupied,sp | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanSpeedOffsetSp | returnFanXXXXSpeedOffsetSp | Return Fan Speed Offset Setpoint | Return Fan XX Speed Offset Setpoint |  | returnFan(\w{0,4}(?=[A-Z]¦$))SpeedOffsetSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | return,air,fan,speed,offset,sp | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanSpeedOvr | returnFanXXXXSpeedOvr | Return Fan Speed Override | Return Fan XX Speed Override |  | returnFan(\w{0,4}(?=[A-Z]¦$))SpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | return,air,fan,speed,ovr | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanSpeedSp | returnFanXXXXSpeedSp | Return Fan Speed Setpoint | Return Fan XX Speed Setpoint |  | returnFan(\w{0,4}(?=[A-Z]¦$))SpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | return,air,fan,speed,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanSpeedStage | returnFanXXXXSpeedStage | Return Fan Speed Stage | Return Fan XX Speed Stage |  | returnFan(\w{0,4}(?=[A-Z]¦$))SpeedStage | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | return,air,fan,speed,staging,cmd | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanSpeedSummerSp | returnFanXXXXSpeedSummerSp | Return Fan Speed Summer Setpoint | Return Fan XX Speed Summer Setpoint |  | returnFan(\w{0,4}(?=[A-Z]¦$))SpeedSummerSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | return,air,fan,speed,summer,sp | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanSpeedUnoccSp | returnFanXXXXSpeedUnoccSp | Return Fan Speed Unnocupied Setpoint | Return Fan XX Speed Unnocupied Setpoint |  | returnFan(\w{0,4}(?=[A-Z]¦$))SpeedUnoccSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | return,air,fan,speed,unoccupied,sp | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanSpeedWinterSp | returnFanXXXXSpeedWinterSp | Return Fan Speed Winter Setpoint | Return Fan XX Speed Winter Setpoint |  | returnFan(\w{0,4}(?=[A-Z]¦$))SpeedWinterSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | return,air,fan,speed,winter,sp | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanStageSp | returnFanXXXXStageYYYYSp | Return Fan Stage Setpoint | Return Fan XX Stage YY Setpoint |  | returnFan(\w{0,4}(?=[A-Z]¦$))Stage(\d{0,4})Sp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 | YY |  | return,air,fan,sp | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnFanStatus | returnFanXXXXStatus | Return Fan Status | Return Fan XX Status |  | returnFan(\w{0,4}(?=[A-Z]¦$))Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | return,air,fan,status,sensor | AHU,CRAC,CRAH,DHU,DOAS,EC,FPB,HP,RF,RTU,VAV,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnHumidMaxSp | returnHumidXXXXMaxSp | Return Humidification Max Setpoint | Return Humidification XX Max Setpoint |  | returnHumid(\d{0,4})MaxSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | return,air,humid,max,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnHumidMinSp | returnHumidXXXXMinSp | Return Humidification Min Setpoint | Return Humidification XX Min Setpoint |  | returnHumid(\d{0,4})MinSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | return,air,humid,min,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnHumidSp | returnHumidXXXXSp | Return Humidification Setpoint | Return Humidification XX Setpoint |  | returnHumid(\d{0,4})Sp | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | return,air,humid,effective,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnHumidity | returnHumidityXXXX | Return Humidity | Return Humidity XX |  | returnHumidity(\d{0,4}) | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | return,air,humidity,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnHumidityDb | returnHumidityXXXXDb | Return Humidity Deadband | Return Humidity XX Deadband |  | returnHumidity(\d{0,4})Db | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | return,air,humidity,deadband,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnHumidityHiAlarm | returnHumidityXXXXHiAlarm | Return Humidity High Alarm | Return Humidity XX High Alarm |  | returnHumidity(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | return,air,humidity,high,alarm | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnHumidityHiSp | returnHumidityXXXXHiSp | Return Humidity High Setpoint | Return Humidity XX High Setpoint |  | returnHumidity(\d{0,4})HiSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | return,air,humidity,high,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnHumidityLoAlarm | returnHumidityXXXXLoAlarm | Return Humidity Low Alarm | Return Humidity XX Low Alarm |  | returnHumidity(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | return,air,humidity,low,alarm | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnHumidityLoSp | returnHumidityXXXXLoSp | Return Humidity Low Setpoint | Return Humidity XX Low Setpoint |  | returnHumidity(\d{0,4})LoSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | return,air,humidity,low,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnHumidityMaxSp | returnHumidityXXXXMaxSp | Return Humidity Max Reset Setpoint | Return Humidity XX Max Reset Setpoint |  | returnHumidity(\d{0,4})MaxSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | return,air,humidity,max,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnHumidityMinSp | returnHumidityXXXXMinSp | Return Humidity Min Reset Setpoint | Return Humidity XX Min Reset Setpoint |  | returnHumidity(\d{0,4})MinSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | return,air,humidity,min,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnHumiditySp | returnHumidityXXXXSp | Return Humidity Setpoint | Return Humidity XX Setpoint |  | returnHumidity(\d{0,4})Sp | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | return,air,humidity,effective,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnIsoDamper | returnIsoDamperXXXX | Return Isolation Damper | Return Isolation Damper XX |  | returnIsoDamper(\d{0,4}) | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | return,air,damper,iso,position,cmd | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnIsoDamperFb | returnIsoDamperXXXXFb | Return Isolation Damper Feedback | Return Isolation Damper XX Feedback |  | returnIsoDamper(\d{0,4})Fb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | return,air,damper,iso,position,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnIsoDamperOvr | returnIsoDamperXXXXOvr | Return Isolation Damper Override | Return Isolation Damper XX Override |  | returnIsoDamper(\d{0,4})Ovr | No | No | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | return,air,damper,iso,position,ovr | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnPressure | returnPressureXXXX | Return Pressure | Return Pressure XX |  | returnPressure(\d{0,4}) | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | return,air,static,pressure,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnPressureDb | returnPressureXXXXDb | Return Pressure Deadband | Return Pressure XX Deadband |  | returnPressure(\d{0,4})Db | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | return,air,static,pressure,deadband,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnPressureFault | returnPressureXXXXFault | Return Pressure Fault | Return Pressure XX Fault |  | returnPressure(\d{0,4})Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | return,air,static,pressure,fault | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnPressureHiAlarm | returnPressureXXXXHiAlarm | Return Pressure High Alarm | Return Pressure XX High Alarm |  | returnPressure(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | return,air,static,pressure,high,alarm | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnPressureHiSp | returnPressureXXXXHiSp | Return Pressure High Setpoint | Return Pressure XX High Setpoint |  | returnPressure(\d{0,4})HiSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | return,air,static,pressure,high,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnPressureLoAlarm | returnPressureXXXXLoAlarm | Return Pressure Low Alarm | Return Pressure XX Low Alarm |  | returnPressure(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | return,air,static,pressure,low,alarm | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnPressureLoSp | returnPressureXXXXLoSp | Return Pressure Low Setpoint | Return Pressure XX Low Setpoint |  | returnPressure(\d{0,4})LoSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | return,air,static,pressure,low,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnPressureMaxSp | returnPressureXXXXMaxSp | Return Pressure Max Setpoint | Return Pressure XX Max Setpoint |  | returnPressure(\d{0,4})MaxSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | return,air,static,pressure,max,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnPressureMinSp | returnPressureXXXXMinSp | Return Pressure Min Setpoint | Return Pressure XX Min Setpoint |  | returnPressure(\d{0,4})MinSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | return,air,static,pressure,min,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnPressureOccSp | returnPressureXXXXOccSp | Return Pressure Occupied Setpoint | Return Pressure XX Occupied Setpoint |  | returnPressure(\d{0,4})OccSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | return,air,static,pressure,occupied,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnPressureSp | returnPressureXXXXSp | Return Pressure Setpoint | Return Pressure XX Setpoint |  | returnPressure(\d{0,4})Sp | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | return,air,static,pressure,effective,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnPressureUnoccSp | returnPressureXXXXUnoccSp | Return Pressure Unoccupied Setpoint | Return Pressure XX Unoccupied Setpoint |  | returnPressure(\d{0,4})UnoccSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | return,air,static,pressure,unoccupied,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnSmokeAlarm | returnSmokeXXXXAlarm | Return Smoke Alarm | Return Smoke XX Alarm |  | returnSmoke(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | return,air,smoke,alarm | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnSmokeDamper | returnSmokeDamperXXXX | Return Smoke Damper Command | Return Smoke Damper XX Command |  | returnSmokeDamper(\d{0,4}) | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | return,air,smoke,damper,status,cmd | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnSmokeDamperFb | returnSmokeDamperXXXXFb | Return Smoke Damper Feedback | Return Smoke Damper XX Feedback |  | returnSmokeDamper(\d{0,4})Fb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | return,air,smoke,damper,status,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnSmokeFault | returnSmokeXXXXFault | Return Smoke Fault | Return Smoke XX Fault |  | returnSmoke(\d{0,4})Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | return,air,smoke,fault | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnTemp | returnTempXXXX | Return Temperature | Return Temperature XX |  | returnTemp(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | return,air,temp,sensor | AFMS,AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnCoolSp | returnCoolSp | Return Temperature Cool Setpoint | Return Temperature Cool Setpoint |  | returnCoolSp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | return,air,temp,active,cool,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnTempDb | returnTempXXXXDb | Return Temperature Deadband | Return Temperature XX Deadband |  | returnTemp(\d{0,4})Db | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | return,air,temp,common,deadband,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnTempFault | returnTempXXXXFault | Return Temperature Fault | Return Temperature XX Fault |  | returnTemp(\d{0,4})Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | return,air,temp,fault | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnHeatSp | returnHeatSp | Return Temperature Heat Setpoint | Return Temperature Heat Setpoint |  | returnHeatSp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | return,air,temp,active,heat,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnTempHiAlarm | returnTempXXXXHiAlarm | Return Temperature High Alarm | Return Temperature XX High Alarm |  | returnTemp(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | return,air,temp,high,alarm | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnTempHiSp | returnTempXXXXHiSp | Return Temperature High Setpoint | Return Temperature XX High Setpoint |  | returnTemp(\d{0,4})HiSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | return,air,temp,high,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.15 (Released),2.16 (Pre-Release)
returnTempLoAlarm | returnTempXXXXLoAlarm | Return Temperature Low Alarm | Return Temperature XX Low Alarm |  | returnTemp(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | return,air,temp,low,alarm | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnTempLoSp | returnTempXXXXLoSp | Return Temperature Low Setpoint | Return Temperature XX Low Setpoint |  | returnTemp(\d{0,4})LoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | return,air,temp,low,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.15 (Released),2.16 (Pre-Release)
returnTempMaxSp | returnTempXXXXMaxSp | Return Temperature Max Reset Setpoint | Return Temperature XX Max Reset Setpoint |  | returnTemp(\d{0,4})MaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | return,air,temp,max,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnTempMinSp | returnTempXXXXMinSp | Return Temperature Min Reset Setpoint | Return Temperature XX Min Reset Setpoint |  | returnTemp(\d{0,4})MinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | return,air,temp,min,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnTempOccCoolSpOffset | returnTempXXXXOccCoolSpOffset | Return Temperature Occupied Cool Setpoint Offset | Return Temperature XX Occupied Cool Setpoint Offset |  | returnTemp(\d{0,4})OccCoolSpOffset | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | return,air,temp,occupied,cool,sp,offset | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnTempOccHeatSpOffset | returnTempXXXXOccHeatSpOffset | Return Temperature Occupied Heat Setpoint Offset | Return Temperature XX Occupied Heat Setpoint Offset |  | returnTemp(\d{0,4})OccHeatSpOffset | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | return,air,temp,occupied,heat,sp,offset | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnTempSp | returnTempXXXXSp | Return Temperature Setpoint | Return Temperature XX Setpoint |  | returnTemp(\d{0,4})Sp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | return,air,temp,common,effective,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnTempSummerDb | returnTempSummerDb | Return Temperature Summer Deadband | Return Temperature Summer Deadband |  | returnTempSummerDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | return,air,temp,summer,deadband,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnTempSummerSp | returnTempSummerSp | Return Temperature Summer Setpoint | Return Temperature Summer Setpoint |  | returnTempSummerSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | return,air,temp,summer,effective,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnTempUnoccCoolSpOffset | returnTempXXXXUnoccCoolSpOffset | Return Temperature Unoccupied Cool Setpoint Offset | Return Temperature XX Unoccupied Cool Setpoint Offset |  | returnTemp(\d{0,4})UnoccCoolSpOffset | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | return,air,temp,unoccupied,cool,sp,offset | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnTempUnoccHeatSpOffset | returnTempXXXXUnoccHeatSpOffset | Return Temperature Unoccupied Heat Setpoint Offset | Return Temperature XX Unoccupied Heat Setpoint Offset |  | returnTemp(\d{0,4})UnoccHeatSpOffset | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | return,air,temp,unoccupied,heat,sp,offset | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnTempWinterDb | returnTempWinterDb | Return Temperature Winter Deadband | Return Temperature Winter Deadband |  | returnTempWinterDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | return,air,temp,winter,deadband,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnTempWinterSp | returnTempWinterSp | Return Temperature Winter Setpoint | Return Temperature Winter Setpoint |  | returnTempWinterSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | return,air,temp,winter,effective,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnVelocity | returnVelocity | Return Velocity | Return Velocity |  | returnVelocity | Yes | Yes | No | Number |  |  | feet_per_minute | meters_per_second | 1 | 1 |  |  | return,air,velocity,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnVelocityPressure | returnVelocityPressure | Return Velocity Pressure | Return Velocity Pressure |  | returnVelocityPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | return,air,dynamic,pressure,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnVOC | returnVOCXXXX | Return VOC | Return VOC XX |  | returnVOC(\d{0,4}) | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | return,air,voc,sensor | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
returnVOCHiAlarm | returnVOCXXXXHiAlarm | Return VOC High Alarm | Return VOC XX High Alarm |  | returnVOC(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | return,air,voc,high,alarm | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,HP,RTU,UV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reversingValveAlarm | reversingValveXXXXAlarm | Reversing Valve Alarm | Reversing Valve XX Alarm |  | reversingValve(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | reversing,valve,alarm | AHU,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reversingValve | reversingValveXXXX | Reversing Valve Command | Reversing Valve XX Command |  | reversingValve(\d{0,4}) | Yes | Yes | No | Bool | Cool/Heat | Cool/Heat | [6 empty] | reversing,valve,position,cmd | AHU,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
reversingValveFb | reversingValveXXXXFb | Reversing Valve Feedback | Reversing Valve XX Feedback |  | reversingValve(\d{0,4})Fb | Yes | Yes | No | Bool | Cool/Heat | Cool/Heat | [6 empty] | reversing,valve,position,sensor | AHU,CRAC,CRAH,DHU,DOAS,EC,HP,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sceneButton | sceneButton | Scene Button Command | Scene Button Command |  | sceneButton | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | scene,button,cmd | LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sceneDimLevelSp | sceneDimLevelSp | Scene Dimming Level Setpoint | Scene Dimming Level Setpoint |  | sceneDimLevelSp | Yes | Yes | No | Number |  |  | footcandle | lux | 0 | 0 |  |  | scene,dimming,lightLevel,sp | LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sceneMode | sceneMode | Scene Mode | Scene Mode |  | sceneMode | Yes | Yes | No | Str | Scene 1/Scene 2 | Scene 1/Scene 2/Scene 3/Scene 4/Scene 5 | [6 empty] | scene,mode,common,sp | LTGI | 2.12,2.13,2.14,2.15 (Released)
sceneModeTime | sceneModeTime | Scene Mode Time Remaining | Scene Mode Time Remaining |  | sceneModeTime | Yes | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | scene,mode,time,sensor | LTGI | 2.15 (Released),2.16 (Pre-Release)
sceneModeTimeSp | sceneModeTimeSp | Scene Mode Time Remaining Setpoint | Scene Mode Time Remaining Setpoint |  | sceneModeTimeSp | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | scene,mode,time,sp | LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
scheduleSelector | scheduleSelector | Schedule Selector | Schedule Selector |  | scheduleSelector | Yes | Yes | No | Str |  | scheduleA,scheduleB,scheduleC,scheduleD,scheduleE,scheduleF,scheduleG,scheduleH,scheduleI,scheduleJ,scheduleK,scheduleL,scheduleM,scheduleN,scheduleO,scheduleP,scheduleQ,scheduleR,scheduleS,scheduleT | [6 empty] | scheduleSelector,cmd | AC,AHU,ATS,ATU,BATT,BLND,BLR,BRK,BTU,CF,CHX,CLR,CM,CMP,CRAC,CRAH,CUH,CWS,DAC,DCU,DCWS,DH,DHU,DHWS,DOAS,DOOR,DRY,EC,EF,ELV,ENC,ERU,FC,FCU,FDS,FEXT,FP,FPB,FSD,FSEP,FSS,GBL,GDS,GEN,GEO,GINT,GM,HDS,HHX,HP,HRU,HT,HUM,HVHS,HVLS,HWS,INV,LDS,LS,LTGE,LTGI,MAU,MSC,OF,PDU,PFC,PH,PINT,PIU,PM,PMP,PRLY,PV,PWS,REC,RECT,RF,RFG,ROS,RP,RPC,RPF,RPP,RRS,RTU,SCRB,SEC,SKYL,SM,SMEX,SMP,SMS,STS,TF,TNK,TRN,TVS,TWR,UH,UPS,UV,VAV,VBTU,VGM,VPM,VRF,VWM,WH,WM,WNDW,WS,WSS,WTHR,WTS,XFMR,ZD,ZN,CDA,FCU,HP | 2.14,2.15 (Released)
scrubber | scrubber | Scrubber Command | Scrubber Command |  | scrubber | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | scrubber,status,common,cmd | AHU,SCRB | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
scrubberDischargeFanAlarm | scrubberDischargeFanXXXXAlarm | Scrubber Discharge Fan Alarm | Scrubber Discharge Fan XX Alarm |  | scrubberDischargeFan(\w{0,4}(?=[A-Z]¦$))Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | scrubber,discharge,air,fan,common,alarm | AHU,SCRB | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
scrubberDischargeFanAlarmReset | scrubberDischargeFanXXXXAlarmReset | Scrubber Discharge Fan Alarm Reset | Scrubber Discharge Fan XX Alarm Reset |  | scrubberDischargeFan(\w{0,4}(?=[A-Z]¦$))AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | scrubber,discharge,air,fan,alarm,reset | AHU,SCRB | 2.15 (Released),2.16 (Pre-Release)
scrubberDischargeFan | scrubberDischargeFanXXXX | Scrubber Discharge Fan Command | Scrubber Discharge Fan XX Command |  | scrubberDischargeFan((?:(?!Ovr)\w){0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | scrubber,discharge,air,fan,status,cmd | AHU,SCRB | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
scrubberDischargeFanCurrent | scrubberDischargeFanXXXXCurrent | Scrubber Discharge Fan Current | Scrubber Discharge Fan XX Current |  | scrubberDischargeFan(\w{0,4}(?=[A-Z]¦$))Current | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | scrubber,discharge,air,fan,current,sensor | AHU,SCRB | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
scrubberDischargeFanEnteringPressure | scrubberDischargeFanXXXXEnteringPressure | Scrubber Discharge Fan Entering Pressure | Scrubber Discharge Fan XX Entering Pressure |  | scrubberDischargeFan(\w{0,4}(?=[A-Z]¦$))EnteringPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | scrubber,discharge,air,fan,entering,pressure,sensor | AHU,SCRB | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
scrubberDischargeFanFault | scrubberDischargeFanXXXXFault | Scrubber Discharge Fan Fault | Scrubber Discharge Fan XX Fault |  | scrubberDischargeFan(\w{0,4}(?=[A-Z]¦$))Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | scrubber,discharge,air,fan,fault | AHU,SCRB | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
scrubberDischargeFanLeavingPressure | scrubberDischargeFanXXXXLeavingPressure | Scrubber Discharge Fan Leaving Pressure | Scrubber Discharge Fan XX Leaving Pressure |  | scrubberDischargeFan(\w{0,4}(?=[A-Z]¦$))LeavingPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | scrubber,discharge,air,fan,leaving,pressure,sensor | AHU,SCRB | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
scrubberDischargeFanMaintSwitch | scrubberDischargeFanXXXXMaintSwitch | Scrubber Discharge Fan Maintenance Switch | Scrubber Discharge Fan XX Maintenance Switch |  | scrubberDischargeFan(\w{0,4}(?=[A-Z]¦$))MaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | scrubber,discharge,air,fan,maintenance,switch,cmd | AHU,SCRB | 2.15 (Released),2.16 (Pre-Release)
scrubberDischargeFanOvr | scrubberDischargeFanXXXXOvr | Scrubber Discharge Fan Override | Scrubber Discharge Fan XX Override |  | scrubberDischargeFan(\w{0,4}(?=[A-Z]¦$))Ovr | No | No | No | Bool | On/Off | On/Off | [6 empty] | scrubber,discharge,air,fan,status,ovr | AHU,SCRB | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
scrubberDischargeFanPressureDelta | scrubberDischargeFanXXXXPressureDelta | Scrubber Discharge Fan Pressure Delta | Scrubber Discharge Fan XX Pressure Delta |  | scrubberDischargeFan(\w{0,4}(?=[A-Z]¦$))PressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | scrubber,discharge,air,fan,common,pressure,delta,sensor | AHU,SCRB | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
scrubberDischargeFanPressureHiAlarm | scrubberDischargeFanXXXXPressureHiAlarm | Scrubber Discharge Fan Pressure High Alarm | Scrubber Discharge Fan XX Pressure High Alarm |  | scrubberDischargeFan(\w{0,4}(?=[A-Z]¦$))PressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | scrubber,discharge,air,fan,pressure,high,alarm | AHU,SCRB | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
scrubberDischargeFanPressureHiSp | scrubberDischargeFanXXXXPressureHiSp | Scrubber Discharge Fan Pressure High Setpoint | Scrubber Discharge Fan XX Pressure High Setpoint |  | scrubberDischargeFan(\w{0,4}(?=[A-Z]¦$))PressureHiSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | scrubber,discharge,air,fan,pressure,high,sp | AHU,SCRB | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
scrubberDischargeFanPressureLoAlarm | scrubberDischargeFanXXXXPressureLoAlarm | Scrubber Discharge Fan Pressure Low Alarm | Scrubber Discharge Fan XX Pressure Low Alarm |  | scrubberDischargeFan(\w{0,4}(?=[A-Z]¦$))PressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | scrubber,discharge,air,fan,pressure,low,alarm | AHU,SCRB | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
scrubberDischargeFanPressureLoSp | scrubberDischargeFanXXXXPressureLoSp | Scrubber Discharge Fan Pressure Low Setpoint | Scrubber Discharge Fan XX Pressure Low Setpoint |  | scrubberDischargeFan(\w{0,4}(?=[A-Z]¦$))PressureLoSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | scrubber,discharge,air,fan,pressure,low,sp | AHU,SCRB | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
scrubberDischargeFanRuntime | scrubberDischargeFanXXXXRuntime | Scrubber Discharge Fan Runtime | Scrubber Discharge Fan XX Runtime |  | scrubberDischargeFan(\w{0,4}(?=[A-Z]¦$))Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,SCRB | 2.15 (Released),2.16 (Pre-Release)
scrubberDischargeFanSpeed | scrubberDischargeFanXXXXSpeed | Scrubber Discharge Fan Speed | Scrubber Discharge Fan XX Speed |  | scrubberDischargeFan(\w{0,4}(?=[A-Z]¦$))Speed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | scrubber,discharge,air,fan,speed,cmd | AHU,SCRB | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
scrubberDischargeFanSpeedFb | scrubberDischargeFanXXXXSpeedFb | Scrubber Discharge Fan Speed Feedback | Scrubber Discharge Fan XX Speed Feedback |  | scrubberDischargeFan(\w{0,4}(?=[A-Z]¦$))SpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | scrubber,discharge,air,fan,speed,sensor | AHU,SCRB | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
scrubberDischargeFanSpeedMaxSp | scrubberDischargeFanXXXXSpeedMaxSp | Scrubber Discharge Fan Speed Max Setpoint | Scrubber Discharge Fan XX Speed Max Setpoint |  | scrubberDischargeFan(\w{0,4}(?=[A-Z]¦$))SpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | scrubber,discharge,air,fan,speed,max,sp | AHU,SCRB | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
scrubberDischargeFanSpeedMinSp | scrubberDischargeFanXXXXSpeedMinSp | Scrubber Discharge Fan Speed Min Setpoint | Scrubber Discharge Fan XX Speed Min Setpoint |  | scrubberDischargeFan(\w{0,4}(?=[A-Z]¦$))SpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | scrubber,discharge,air,fan,speed,min,sp | AHU,SCRB | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
scrubberDischargeFanSpeedOvr | scrubberDischargeFanXXXXSpeedOvr | Scrubber Discharge Fan Speed Override | Scrubber Discharge Fan XX Speed Override |  | scrubberDischargeFan(\w{0,4}(?=[A-Z]¦$))SpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | scrubber,discharge,air,fan,speed,ovr | AHU,SCRB | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
scrubberDischargeFanSpeedSp | scrubberDischargeFanXXXXSpeedSp | Scrubber Discharge Fan Speed Setpoint | Scrubber Discharge Fan XX Speed Setpoint |  | scrubberDischargeFan(\w{0,4}(?=[A-Z]¦$))SpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | scrubber,discharge,air,fan,speed,effective,sp | AHU,SCRB | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
scrubberDischargeFanStatus | scrubberDischargeFanXXXXStatus | Scrubber Discharge Fan Status | Scrubber Discharge Fan XX Status |  | scrubberDischargeFan(\w{0,4}(?=[A-Z]¦$))Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | scrubber,discharge,air,fan,status,sensor | AHU,SCRB | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
scrubberDischargeTemp | scrubberDischargeTemp | Scrubber Discharge Temperature | Scrubber Discharge Temperature |  | scrubberDischargeTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | scrubber,discharge,temp,sensor | AHU,SCRB | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
scrubberDischargeVOC | scrubberDischargeVOC | Scrubber Discharge VOC | Scrubber Discharge VOC |  | scrubberDischargeVOC | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | scrubber,discharge,voc,sensor | AHU,SCRB | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
scrubberMode | scrubberMode | Scrubber Mode | Scrubber Mode |  | scrubberMode | Yes | Yes | No | Str |  | Not Cleaning/Cleaning/Off/Regeneration | [6 empty] | scrubber,mode,sp | AHU,SCRB | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
scrubberStatus | scrubberStatus | Scrubber Status | Scrubber Status |  | scrubberStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | scrubber,status,common,sensor | AHU,SCRB | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
seasonMode | seasonMode | Season Mode | Season Mode |  | seasonMode | Yes | Yes | No | Bool | Summer/Winter | Summer/Winter/Spring/Fall | [6 empty] | season,mode,cmd | CWS,HWS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
seasonModeDb | seasonModeDb | Season Mode Deadband | Season Mode Deadband |  | seasonModeDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | season,mode,deadband,sp | CWS,HWS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
seasonModeOvr | seasonModeOvr | Season Mode Override | Season Mode Override |  | seasonModeOvr | No | No | No | Bool | Summer/Winter | Summer/Winter/Spring/Fall | [6 empty] | season,mode,ovr | CWS,HWS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
seasonModeSp | seasonModeSp | Season Mode Setpoint | Season Mode Setpoint |  | seasonModeSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | season,mode,temp,sp | CWS,HWS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secBypassFlow | secBypassFlowXXXX | Secondary Bypass Flow | Secondary Bypass Flow XX |  | secBypassFlow(\d{0,4}) | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | secondary,water,bypass,flow,sensor | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secBypassFlowDb | secBypassFlowXXXXDb | Secondary Bypass Flow Deadband | Secondary Bypass Flow XX Deadband |  | secBypassFlow(\d{0,4})Db | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | secondary,water,bypass,flow,deadband,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secBypassFlowHiSp | secBypassFlowXXXXHiSp | Secondary Bypass Flow High Setpoint | Secondary Bypass Flow XX High Setpoint |  | secBypassFlow(\d{0,4})HiSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | secondary,water,bypass,flow,high,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secBypassFlowLoSp | secBypassFlowXXXXLoSp | Secondary Bypass Flow Low Setpoint | Secondary Bypass Flow XX Low Setpoint |  | secBypassFlow(\d{0,4})LoSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | secondary,water,bypass,flow,low,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secBypassFlowMaxSp | secBypassFlowXXXXMaxSp | Secondary Bypass Flow Max Reset Setpoint | Secondary Bypass Flow XX Max Reset Setpoint |  | secBypassFlow(\d{0,4})MaxSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | secondary,water,bypass,flow,max,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secBypassFlowMinSp | secBypassFlowXXXXMinSp | Secondary Bypass Flow Min Reset Setpoint | Secondary Bypass Flow XX Min Reset Setpoint |  | secBypassFlow(\d{0,4})MinSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | secondary,water,bypass,flow,min,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secBypassFlowSp | secBypassFlowXXXXSp | Secondary Bypass Flow Setpoint | Secondary Bypass Flow XX Setpoint |  | secBypassFlow(\d{0,4})Sp | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | secondary,water,bypass,flow,effective,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secBypassTemp | secBypassTempXXXX | Secondary Bypass Temperature | Secondary Bypass Temperature XX |  | secBypassTemp(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | secondary,water,bypass,temp,sensor | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secBypassValveAlarm | secBypassValveXXXXAlarm | Secondary Bypass Valve Alarm | Secondary Bypass Valve XX Alarm |  | secBypassValve(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | secondary,water,bypass,valve,position,alarm | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secBypassValve | secBypassValveXXXX | Secondary Bypass Valve Command | Secondary Bypass Valve XX Command |  | secBypassValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | secondary,water,bypass,valve,position,cmd | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secBypassValveFb | secBypassValveXXXXFb | Secondary Bypass Valve Feedback | Secondary Bypass Valve XX Feedback |  | secBypassValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | secondary,water,bypass,valve,position,sensor | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secBypassValveMaxSp | secBypassValveXXXXMaxSp | Secondary Bypass Valve Max Reset Setpoint | Secondary Bypass Valve XX Max Reset Setpoint |  | secBypassValve(\d{0,4})MaxSp | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | secondary,water,bypass,valve,position,max,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secBypassValveMinSp | secBypassValveXXXXMinSp | Secondary Bypass Valve Min Reset Setpoint | Secondary Bypass Valve XX Min Reset Setpoint |  | secBypassValve(\d{0,4})MinSp | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | secondary,water,bypass,valve,position,min,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnergy | secEnergy | Secondary Energy | Secondary Energy |  | secEnergy | Yes | Yes | No | Number |  |  | kilobtu | kilobtu | 0 | 0 |  |  | secondary,water,energy,common,sensor | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringBypassValve | secEnteringBypassValveXXXX | Secondary Entering Bypass Valve Command | Secondary Entering Bypass Valve XX Command |  | secEnteringBypassValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | water,valve,position,cmd,entering,secBypass | CWS,GEO,HWS,WS,WSS,HX | 2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringBypassValveFb | secEnteringBypassValveXXXXFb | Secondary Entering Bypass Valve Feedback | Secondary Entering Bypass Valve XX Feedback |  | secEnteringBypassValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | water,valve,position,sensor,entering,secBypass | CWS,GEO,HWS,WS,WSS,HX | 2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringFlow | secEnteringFlowXXXX | Secondary Entering Flow | Secondary Entering Flow XX |  | secEnteringFlow(\d{0,4}) | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | secondary,water,entering,flow,sensor | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringFlowDb | secEnteringFlowXXXXDb | Secondary Entering Flow Deadband | Secondary Entering Flow XX Deadband |  | secEnteringFlow(\d{0,4})Db | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | secondary,water,entering,flow,deadband,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringFlowHiSp | secEnteringFlowXXXXHiSp | Secondary Entering Flow High Setpoint | Secondary Entering Flow XX High Setpoint |  | secEnteringFlow(\d{0,4})HiSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | secondary,water,entering,flow,high,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringFlowLoSp | secEnteringFlowXXXXLoSp | Secondary Entering Flow Low Setpoint | Secondary Entering Flow XX Low Setpoint |  | secEnteringFlow(\d{0,4})LoSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | secondary,water,entering,flow,low,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringFlowMaxSp | secEnteringFlowXXXXMaxSp | Secondary Entering Flow Max Setpoint | Secondary Entering Flow XX Max Setpoint |  | secEnteringFlow(\d{0,4})MaxSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | secondary,water,entering,flow,max,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringFlowMinSp | secEnteringFlowXXXXMinSp | Secondary Entering Flow Min Setpoint | Secondary Entering Flow XX Min Setpoint |  | secEnteringFlow(\d{0,4})MinSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | secondary,water,entering,flow,min,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringFlowSp | secEnteringFlowXXXXSp | Secondary Entering Flow Setpoint | Secondary Entering Flow XX Setpoint |  | secEnteringFlow(\d{0,4})Sp | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | secondary,water,entering,flow,effective,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringIsoValve | secEnteringIsoValveXXXX | Secondary Entering Isolation Valve Command | Secondary Entering Isolation Valve XX Command |  | secEnteringIsoValve(\d{0,4}) | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | secondary,water,iso,entering,valve,position,cmd | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringIsoValveFb | secEnteringIsoValveXXXXFb | Secondary Entering Isolation Valve Feedback | Secondary Entering Isolation Valve XX Feedback |  | secEnteringIsoValve(\d{0,4})Fb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | secondary,water,iso,entering,valve,position,sensor | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringPressure | secEnteringPressureXXXX | Secondary Entering Pressure | Secondary Entering Pressure XX |  | secEnteringPressure(\d{0,4}) | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | secondary,water,entering,pressure,common,sensor | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringPressureDb | secEnteringPressureXXXXDb | Secondary Entering Pressure Deadband | Secondary Entering Pressure XX Deadband |  | secEnteringPressure(\d{0,4})Db | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | secondary,water,entering,pressure,deadband,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringPressureFault | secEnteringPressureXXXXFault | Secondary Entering Pressure Fault | Secondary Entering Pressure XX Fault |  | secEnteringPressure(\d{0,4})Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | secondary,water,entering,pressure,fault | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringPressureHiAlarm | secEnteringPressureXXXXHiAlarm | Secondary Entering Pressure High Alarm | Secondary Entering Pressure XX High Alarm |  | secEnteringPressure(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | secondary,water,entering,pressure,high,alarm | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringPressureHiSp | secEnteringPressureXXXXHiSp | Secondary Entering Pressure High Setpoint | Secondary Entering Pressure XX High Setpoint |  | secEnteringPressure(\d{0,4})HiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | secondary,water,entering,pressure,high,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringPressureLoAlarm | secEnteringPressureXXXXLoAlarm | Secondary Entering Pressure Low Alarm | Secondary Entering Pressure XX Low Alarm |  | secEnteringPressure(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | secondary,water,entering,pressure,low,alarm | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringPressureLoSp | secEnteringPressureXXXXLoSp | Secondary Entering Pressure Low Setpoint | Secondary Entering Pressure XX Low Setpoint |  | secEnteringPressure(\d{0,4})LoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | secondary,water,entering,pressure,low,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringPressureMaxSp | secEnteringPressureXXXXMaxSp | Secondary Entering Pressure Max Reset Setpoint | Secondary Entering Pressure XX Max Reset Setpoint |  | secEnteringPressure(\d{0,4})MaxSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | secondary,water,entering,pressure,max,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringPressureMinSp | secEnteringPressureXXXXMinSp | Secondary Entering Pressure Min Reset Setpoint | Secondary Entering Pressure XX Min Reset Setpoint |  | secEnteringPressure(\d{0,4})MinSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | secondary,water,entering,pressure,min,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringPressureSp | secEnteringPressureXXXXSp | Secondary Entering Pressure Setpoint | Secondary Entering Pressure XX Setpoint |  | secEnteringPressure(\d{0,4})Sp | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | secondary,water,entering,pressure,effective,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringTemp | secEnteringTempXXXX | Secondary Entering Temperature | Secondary Entering Temperature XX |  | secEnteringTemp(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | secondary,water,entering,temp,sensor | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringTempDb | secEnteringTempXXXXDb | Secondary Entering Temperature Deadband | Secondary Entering Temperature XX Deadband |  | secEnteringTemp(\d{0,4})Db | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | secondary,water,entering,temp,deadband,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringTempHiAlarm | secEnteringTempXXXXHiAlarm | Secondary Entering Temperature High Alarm | Secondary Entering Temperature XX High Alarm |  | secEnteringTemp(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | secondary,water,entering,temp,high,alarm | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringTempHiSp | secEnteringTempXXXXHiSp | Secondary Entering Temperature High Setpoint | Secondary Entering Temperature XX High Setpoint |  | secEnteringTemp(\d{0,4})HiSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | secondary,water,entering,temp,high,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringTempLoAlarm | secEnteringTempXXXXLoAlarm | Secondary Entering Temperature Low Alarm | Secondary Entering Temperature XX Low Alarm |  | secEnteringTemp(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | secondary,water,entering,temp,low,alarm | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringTempLoSp | secEnteringTempXXXXLoSp | Secondary Entering Temperature Low Setpoint | Secondary Entering Temperature XX Low Setpoint |  | secEnteringTemp(\d{0,4})LoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | secondary,water,entering,temp,low,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringTempMaxSp | secEnteringTempXXXXMaxSp | Secondary Entering Temperature Max Reset Setpoint | Secondary Entering Temperature XX Max Reset Setpoint |  | secEnteringTemp(\d{0,4})MaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | secondary,water,entering,temp,max,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringTempMinSp | secEnteringTempXXXXMinSp | Secondary Entering Temperature Min Reset Setpoint | Secondary Entering Temperature XX Min Reset Setpoint |  | secEnteringTemp(\d{0,4})MinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | secondary,water,entering,temp,min,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringTempSp | secEnteringTempXXXXSp | Secondary Entering Temperature Setpoint | Secondary Entering Temperature XX Setpoint |  | secEnteringTemp(\d{0,4})Sp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | secondary,water,entering,temp,effective,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringValveAlarm | secEnteringValveXXXXAlarm | Secondary Entering Valve Alarm | Secondary Entering Valve XX Alarm |  | secEnteringValve(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | secondary,water,entering,valve,position,alarm | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringValve | secEnteringValveXXXX | Secondary Entering Valve Command | Secondary Entering Valve XX Command |  | secEnteringValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | secondary,water,entering,valve,common,position,cmd | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secEnteringValveFb | secEnteringValveXXXXFb | Secondary Entering Valve Feedback | Secondary Entering Valve XX Feedback |  | secEnteringValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | secondary,water,entering,valve,common,position,sensor | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secFilterAlarm | secFilterXXXXAlarm | Secondary Filter Alarm | Secondary Filter XX Alarm |  | secFilter(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | secondary,water,filter,general,alarm | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secFilterAlarmReset | secFilterXXXXAlarmReset | Secondary Filter Alarm Reset | Secondary Filter XX Alarm Reset |  | secFilter(\d{0,4})AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | secondary,water,filter,reset,alarm | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secFilterEnable | secFilterXXXXEnable | Secondary Filter Enable | Secondary Filter XX Enable |  | secFilter(\d{0,4})Enable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | secondary,water,filter,enable,cmd | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secFilterPressureDelta | secFilterXXXXPressureDelta | Secondary Filter Pressure Delta | Secondary Filter XX Pressure Delta |  | secFilter(\d{0,4})PressureDelta | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | secondary,water,filter,pressure,delta,sensor | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secFilterPumpStatus | secFilterXXXXPumpStatus | Secondary Filter Pump Status | Secondary Filter XX Pump Status |  | secFilter(\d{0,4})PumpStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | secondary,water,filter,pump,status,sensor | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secFlowStatus | secFlowXXXXStatus | Secondary Flow Status | Secondary Flow XX Status |  | secFlow(\d{0,4})Status | Yes | Yes | No | Bool | Flow/No Flow | Flow/No Flow | [6 empty] | secondary,water,flow,status,sensor | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingBypassValve | secLeavingBypassValveXXXX | Secondary Leaving Bypass Valve Command | Secondary Leaving Bypass Valve XX Command |  | secLeavingBypassValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | water,valve,position,cmd,leaving,secBypass | CWS,GEO,HWS,WS,WSS,HX | 2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingBypassValveFb | secLeavingBypassValveXXXXFb | Secondary Leaving Bypass Valve Feedback | Secondary Leaving Bypass Valve XX Feedback |  | secLeavingBypassValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | water,valve,position,sensor,leaving,secBypass | CWS,GEO,HWS,WS,WSS,HX | 2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingFlow | secLeavingFlowXXXX | Secondary Leaving Flow | Secondary Leaving Flow XX |  | secLeavingFlow(\d{0,4}) | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | secondary,water,leaving,flow,sensor | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingFlowDb | secLeavingFlowXXXXDb | Secondary Leaving Flow Deadband | Secondary Leaving Flow XX Deadband |  | secLeavingFlow(\d{0,4})Db | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | secondary,water,leaving,flow,deadband,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingFlowHiSp | secLeavingFlowXXXXHiSp | Secondary Leaving Flow High Setpoint | Secondary Leaving Flow XX High Setpoint |  | secLeavingFlow(\d{0,4})HiSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | secondary,water,leaving,flow,high,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingFlowLoAlarm | secLeavingFlowXXXXLoAlarm | Secondary Leaving Flow Low Alarm | Secondary Leaving Flow XX Low Alarm |  | secLeavingFlow(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | secondary,water,leaving,flow,low,alarm | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingFlowLoSp | secLeavingFlowXXXXLoSp | Secondary Leaving Flow Low Setpoint | Secondary Leaving Flow XX Low Setpoint |  | secLeavingFlow(\d{0,4})LoSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | secondary,water,leaving,flow,low,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingFlowMaxSp | secLeavingFlowXXXXMaxSp | Secondary Leaving Flow Max Setpoint | Secondary Leaving Flow XX Max Setpoint |  | secLeavingFlow(\d{0,4})MaxSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | secondary,water,leaving,flow,max,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingFlowMinSp | secLeavingFlowXXXXMinSp | Secondary Leaving Flow Min Setpoint | Secondary Leaving Flow XX Min Setpoint |  | secLeavingFlow(\d{0,4})MinSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | secondary,water,leaving,flow,min,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingFlowSp | secLeavingFlowXXXXSp | Secondary Leaving Flow Setpoint | Secondary Leaving Flow XX Setpoint |  | secLeavingFlow(\d{0,4})Sp | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | secondary,water,leaving,flow,effective,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingIsoValve | secLeavingIsoValveXXXX | Secondary Leaving Isolation Valve Command | Secondary Leaving Isolation Valve XX Command |  | secLeavingIsoValve(\d{0,4}) | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | secondary,water,iso,leaving,valve,position,cmd | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingIsoValveFb | secLeavingIsoValveXXXXFb | Secondary Leaving Isolation Valve Feedback | Secondary Leaving Isolation Valve XX Feedback |  | secLeavingIsoValve(\d{0,4})Fb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | secondary,water,iso,leaving,valve,position,sensor | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingPressure | secLeavingPressureXXXX | Secondary Leaving Pressure | Secondary Leaving Pressure XX |  | secLeavingPressure(\d{0,4}) | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | secondary,water,leaving,pressure,common,sensor | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingPressureDb | secLeavingPressureXXXXDb | Secondary Leaving Pressure Deadband | Secondary Leaving Pressure XX Deadband |  | secLeavingPressure(\d{0,4})Db | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | secondary,water,leaving,pressure,deadband,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingPressureFault | secLeavingPressureXXXXFault | Secondary Leaving Pressure Fault | Secondary Leaving Pressure XX Fault |  | secLeavingPressure(\d{0,4})Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | secondary,water,leaving,pressure,fault | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingPressureHiAlarm | secLeavingPressureXXXXHiAlarm | Secondary Leaving Pressure High Alarm | Secondary Leaving Pressure XX High Alarm |  | secLeavingPressure(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | secondary,water,leaving,pressure,high,alarm | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingPressureHiSp | secLeavingPressureXXXXHiSp | Secondary Leaving Pressure High Setpoint | Secondary Leaving Pressure XX High Setpoint |  | secLeavingPressure(\d{0,4})HiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | secondary,water,leaving,pressure,high,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingPressureLoAlarm | secLeavingPressureXXXXLoAlarm | Secondary Leaving Pressure Low Alarm | Secondary Leaving Pressure XX Low Alarm |  | secLeavingPressure(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | secondary,water,leaving,pressure,low,alarm | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingPressureLoSp | secLeavingPressureXXXXLoSp | Secondary Leaving Pressure Low Setpoint | Secondary Leaving Pressure XX Low Setpoint |  | secLeavingPressure(\d{0,4})LoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | secondary,water,leaving,pressure,low,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingPressureMaxSp | secLeavingPressureXXXXMaxSp | Secondary Leaving Pressure Max Reset Setpoint | Secondary Leaving Pressure XX Max Reset Setpoint |  | secLeavingPressure(\d{0,4})MaxSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | secondary,water,leaving,pressure,max,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingPressureMinSp | secLeavingPressureXXXXMinSp | Secondary Leaving Pressure Min Reset Setpoint | Secondary Leaving Pressure XX Min Reset Setpoint |  | secLeavingPressure(\d{0,4})MinSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | secondary,water,leaving,pressure,min,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingPressureSp | secLeavingPressureXXXXSp | Secondary Leaving Pressure Setpoint | Secondary Leaving Pressure XX Setpoint |  | secLeavingPressure(\d{0,4})Sp | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | secondary,water,leaving,pressure,effective,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingTemp | secLeavingTempXXXX | Secondary Leaving Temperature | Secondary Leaving Temperature XX |  | secLeavingTemp(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | secondary,water,leaving,temp,sensor | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingTempDb | secLeavingTempXXXXDb | Secondary Leaving Temperature Deadband | Secondary Leaving Temperature XX Deadband |  | secLeavingTemp(\d{0,4})Db | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | secondary,water,leaving,temp,deadband,general,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingTempFault | secLeavingTempXXXXFault | Secondary Leaving Temperature Fault | Secondary Leaving Temperature XX Fault |  | secLeavingTemp(\d{0,4})Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | secondary,water,leaving,temp,fault | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingTempHiAlarm | secLeavingTempXXXXHiAlarm | Secondary Leaving Temperature High Alarm | Secondary Leaving Temperature XX High Alarm |  | secLeavingTemp(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | secondary,water,leaving,temp,high,alarm | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingTempHiSp | secLeavingTempXXXXHiSp | Secondary Leaving Temperature High Setpoint | Secondary Leaving Temperature XX High Setpoint |  | secLeavingTemp(\d{0,4})HiSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | secondary,water,leaving,temp,high,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingTempLoAlarm | secLeavingTempXXXXLoAlarm | Secondary Leaving Temperature Low Alarm | Secondary Leaving Temperature XX Low Alarm |  | secLeavingTemp(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | secondary,water,leaving,temp,low,alarm | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingTempLoSp | secLeavingTempXXXXLoSp | Secondary Leaving Temperature Low Setpoint | Secondary Leaving Temperature XX Low Setpoint |  | secLeavingTemp(\d{0,4})LoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | secondary,water,leaving,temp,low,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingTempMaxSp | secLeavingTempXXXXMaxSp | Secondary Leaving Temperature Max Reset Setpoint | Secondary Leaving Temperature XX Max Reset Setpoint |  | secLeavingTemp(\d{0,4})MaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | secondary,water,leaving,temp,max,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingTempMinSp | secLeavingTempXXXXMinSp | Secondary Leaving Temperature Min Reset Setpoint | Secondary Leaving Temperature XX Min Reset Setpoint |  | secLeavingTemp(\d{0,4})MinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | secondary,water,leaving,temp,min,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingTempOccSp | secLeavingTempXXXXOccSp | Secondary Leaving Temperature Occupied Setpoint | Secondary Leaving Temperature XX Occupied Setpoint |  | secLeavingTemp(\d{0,4})OccSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | secondary,water,leaving,temp,occupied,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingTempSp | secLeavingTempXXXXSp | Secondary Leaving Temperature Setpoint | Secondary Leaving Temperature XX Setpoint |  | secLeavingTemp(\d{0,4})Sp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | secondary,water,leaving,temp,effective,general,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingTempSpOffset | secLeavingTempXXXXSpOffset | Secondary Leaving Temperature Setpoint Offset | Secondary Leaving Temperature XX Setpoint Offset |  | secLeavingTemp(\d{0,4})SpOffset | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | secondary,water,leaving,temp,offset,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingTempUnoccDb | secLeavingTempXXXXUnoccDb | Secondary Leaving Temperature Unoccupied Deadband | Secondary Leaving Temperature XX Unoccupied Deadband |  | secLeavingTemp(\d{0,4})UnoccDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | secondary,water,leaving,temp,unoccupied,deadband,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingTempUnoccSp | secLeavingTempXXXXUnoccSp | Secondary Leaving Temperature Unoccupied Setpoint | Secondary Leaving Temperature XX Unoccupied Setpoint |  | secLeavingTemp(\d{0,4})UnoccSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | secondary,water,leaving,temp,unoccupied,effective,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingValveAlarm | secLeavingValveXXXXAlarm | Secondary Leaving Valve Alarm | Secondary Leaving Valve XX Alarm |  | secLeavingValve(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | secondary,water,leaving,valve,common,alarm | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingValve | secLeavingValveXXXX | Secondary Leaving Valve Command | Secondary Leaving Valve XX Command |  | secLeavingValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | secondary,water,leaving,valve,common,position,cmd | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secLeavingValveFb | secLeavingValveXXXXFb | Secondary Leaving Valve Feedback | Secondary Leaving Valve XX Feedback |  | secLeavingValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | secondary,water,leaving,valve,common,position,sensor | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secMixingValveAlarm | secMixingValveXXXXAlarm | Secondary Mixing Valve Alarm | Secondary Mixing Valve XX Alarm |  | secMixingValve(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | secondary,water,mixing,valve,alarm | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secMixingValve | secMixingValveXXXX | Secondary Mixing Valve Command | Secondary Mixing Valve XX Command |  | secMixingValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | secondary,water,mixing,valve,position,cmd | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secMixingValveFb | secMixingValveXXXXFb | Secondary Mixing Valve Feedback | Secondary Mixing Valve XX Feedback |  | secMixingValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | secondary,water,mixing,valve,position,sensor | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secMixingValveSp | secMixingValveXXXXSp | Secondary Mixing Valve Setpoint | Secondary Mixing Valve XX Setpoint |  | secMixingValve(\d{0,4})Sp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | secondary,water,mixing,valve,position,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPower | secPower | Secondary Power | Secondary Power |  | secPower | Yes | Yes | No | Number |  |  | kilobtus_per_hour | kilobtus_per_hour | 1 | 1 |  |  | secondary,water,power,common,sensor | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPressureDelta | secPressureDeltaXXXX | Secondary Pressure Differential | Secondary Pressure Differential XX |  | secPressureDelta(\d{0,4}) | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | secondary,water,common,delta,pressure,general,sensor | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPressureDeltaDb | secPressureDeltaXXXXDb | Secondary Pressure Differential Deadband | Secondary Pressure Differential XX Deadband |  | secPressureDelta(\d{0,4})Db | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | secondary,water,common,delta,pressure,deadband,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPressureDeltaHiAlarm | secPressureDeltaXXXXHiAlarm | Secondary Pressure Differential High Alarm | Secondary Pressure Differential XX High Alarm |  | secPressureDelta(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | secondary,water,common,delta,pressure,high,alarm | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPressureDeltaHiSp | secPressureDeltaXXXXHiSp | Secondary Pressure Differential High Setpoint | Secondary Pressure Differential XX High Setpoint |  | secPressureDelta(\d{0,4})HiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | secondary,water,common,delta,pressure,high,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPressureDeltaLoAlarm | secPressureDeltaXXXXLoAlarm | Secondary Pressure Differential Low Alarm | Secondary Pressure Differential XX Low Alarm |  | secPressureDelta(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | secondary,water,common,delta,pressure,low,alarm | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPressureDeltaLoSp | secPressureDeltaXXXXLoSp | Secondary Pressure Differential Low Setpoint | Secondary Pressure Differential XX Low Setpoint |  | secPressureDelta(\d{0,4})LoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | secondary,water,common,delta,pressure,low,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPressureDeltaMaxSp | secPressureDeltaXXXXMaxSp | Secondary Pressure Differential Max Reset Setpoint | Secondary Pressure Differential XX Max Reset Setpoint |  | secPressureDelta(\d{0,4})MaxSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | secondary,water,common,delta,pressure,max,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPressureDeltaMinSp | secPressureDeltaXXXXMinSp | Secondary Pressure Differential Min Reset Setpoint | Secondary Pressure Differential XX Min Reset Setpoint |  | secPressureDelta(\d{0,4})MinSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | secondary,water,common,delta,pressure,min,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPressureDeltaSp | secPressureDeltaXXXXSp | Secondary Pressure Differential Setpoint | Secondary Pressure Differential XX Setpoint |  | secPressureDelta(\d{0,4})Sp | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | secondary,water,common,delta,pressure,effective,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpAlarm | secPumpXXXXAlarm | Secondary Pump Alarm | Secondary Pump XX Alarm |  | secPump(\w{0,4}(?=[A-Z]¦$))Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | secondary,water,pump,common,alarm | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpAlarmReset | secPumpXXXXAlarmReset | Secondary Pump Alarm Reset | Secondary Pump XX Alarm Reset |  | secPump(\w{0,4}(?=[A-Z]¦$))AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | secondary,water,pump,reset,alarm | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPump | secPumpXXXX | Secondary Pump Command | Secondary Pump XX Command |  | secPump((?:(?!Lead)(?!Ovr)\w){0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | secondary,water,pump,status,cmd | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpCurrent | secPumpXXXXCurrent | Secondary Pump Current | Secondary Pump XX Current |  | secPump(\w{0,4}(?=[A-Z]¦$))Current | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | secondary,water,pump,current,sensor | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpEnable | secPumpXXXXEnable | Secondary Pump Enable | Secondary Pump XX Enable |  | secPump(\w{0,4}(?=[A-Z]¦$))Enable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | secondary,water,pump,enable,cmd | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpEnableDb | secPumpXXXXEnableDb | Secondary Pump Enable Deadband | Secondary Pump XX Enable Deadband |  | secPump(\w{0,4}(?=[A-Z]¦$))EnableDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | secondary,water,pump,enable,deadband,sp | CWS,GEO,HWS,WS,WSS,HX | 2.15 (Released),2.16 (Pre-Release)
secPumpEnableSp | secPumpXXXXEnableSp | Secondary Pump Enable Setpoint | Secondary Pump XX Enable Setpoint |  | secPump((?:(?!Lag)\w){0,4}(?=[A-Z]¦$))EnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | secondary,water,pump,enable,effective,sp | CWS,GEO,HWS,WS,WSS,HX | 2.15 (Released),2.16 (Pre-Release)
secPumpEnteringPressure | secPumpXXXXEnteringPressure | Secondary Pump Entering Pressure | Secondary Pump XX Entering Pressure |  | secPump(\w{0,4}(?=[A-Z]¦$))EnteringPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | secondary,water,pump,entering,pressure,sensor | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpFault | secPumpXXXXFault | Secondary Pump Fault | Secondary Pump XX Fault |  | secPump(\w{0,4}(?=[A-Z]¦$))Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | secondary,water,pump,fault,common | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpLagDisableSp | secPumpXXXXLagDisableSp | Secondary Pump Lag Disable Setpoint | Secondary Pump XX Lag Disable Setpoint |  | secPump(\w{0,4}(?=[A-Z]¦$))LagDisableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | secondary,water,pump,lag,disable,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpLagEnableSp | secPumpXXXXLagEnableSp | Secondary Pump Lag Enable Setpoint | Secondary Pump XX Lag Enable Setpoint |  | secPump(\w{0,4}(?=[A-Z]¦$))LagEnableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | secondary,water,pump,lag,enable,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpLagReq | secPumpXXXXLagReq | Secondary Pump Lag Request | Secondary Pump XX Lag Request |  | secPump(\w{0,4}(?=[A-Z]¦$))LagReq | No | No | No | Bool | Request/No Request | Request/No Request | [6 empty] | secondary,water,pump,lag,request,cmd | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpLead | secPumpLead | Secondary Pump Lead | Secondary Pump Lead |  | secPumpLead | Yes | Yes | No | Bool | Lead 1/Lead 2 | Lead 1/Lead 2 | [6 empty] | secondary,water,pump,lead,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpLeadXor | secPumpLeadXor | Secondary Pump Lead Change Over | Secondary Pump Lead Change Over |  | secPumpLeadXor | No | No | No | Bool | On/Off | On/Off | [6 empty] | secondary,water,pump,lead,changeOver,common,cmd | CWS,GEO,HWS,WS,WSS,HX | 2.15 (Released),2.16 (Pre-Release)
secPumpLeadXorDay | secPumpLeadXorDay | Secondary Pump Lead Change Over Day | Secondary Pump Lead Change Over Day |  | secPumpLeadXorDay | No | No | No | Number |  | Sun,Mon,Tue,Wed,Thur,Fri,Sat | day | day | 0 | 0 |  |  | secondary,water,pump,lead,changeOver,day,cmd | CWS,GEO,HWS,WS,WSS,HX | 2.15 (Released),2.16 (Pre-Release)
secPumpLeadXorHour | secPumpLeadXorHour | Secondary Pump Lead Change Over Hour | Secondary Pump Lead Change Over Hour |  | secPumpLeadXorHour | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | secondary,water,pump,lead,changeOver,hour,cmd | CWS,GEO,HWS,WS,WSS,HX | 2.15 (Released),2.16 (Pre-Release)
secPumpLeadXorMode | secPumpLeadXorMode | Secondary Pump Lead Change Over Mode Command | Secondary Pump Lead Change Over Mode Command |  | secPumpLeadXorMode | No | No | No | Str |  | 1Week/2Week/3Week/4Week | [6 empty] | secondary,water,pump,lead,changeOver,mode,cmd | CWS,GEO,HWS,WS,WSS,HX | 2.15 (Released),2.16 (Pre-Release)
secPumpLeadXorRuntimeSp | secPumpLeadXorRuntimeSp | Secondary Pump Lead Change Over Runtime Setpoint | Secondary Pump Lead Change Over Runtime Setpoint |  | secPumpLeadXorRuntimeSp | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpLeavingPressure | secPumpXXXXLeavingPressure | Secondary Pump Leaving Pressure | Secondary Pump XX Leaving Pressure |  | secPump(\w{0,4}(?=[A-Z]¦$))LeavingPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | secondary,water,pump,leaving,pressure,sensor | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpMaint | secPumpXXXXMaint | Secondary Pump Maintenance | Secondary Pump XX Maintenance |  | secPump(\w{0,4}(?=[A-Z]¦$))Maint | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | secondary,water,pump,maintenance,common,cmd | CWS,GEO,HWS,WS,WSS,HX | 2.15 (Released),2.16 (Pre-Release)
secPumpMaintSwitch | secPumpXXXXMaintSwitch | Secondary Pump Maintenance Switch | Secondary Pump XX Maintenance Switch |  | secPump(\w{0,4}(?=[A-Z]¦$))MaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | secondary,water,pump,maintenance,switch,cmd | CWS,GEO,HWS,WS,WSS,HX | 2.15 (Released),2.16 (Pre-Release)
secPumpMinOffSp | secPumpMinOffSp | Secondary Pump Minimum Off Setpoint | Secondary Pump Minimum Off Setpoint |  | secPumpMinOffSp | No | No | No | Number |  |  | second | second | 0 | 0 |  |  | secondary,water,pump,min,off,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpMinOnSp | secPumpMinOnSp | Secondary Pump Minimum On Setpoint | Secondary Pump Minimum On Setpoint |  | secPumpMinOnSp | No | No | No | Number |  |  | second | second | 0 | 0 |  |  | secondary,water,pump,min,on,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpOvr | secPumpXXXXOvr | Secondary Pump Override | Secondary Pump XX Override |  | secPump(\w{0,4}(?=[A-Z]¦$))Ovr | No | No | No | Bool | On/Off | On/Off | [6 empty] | secondary,water,pump,status,ovr | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpPressureDelta | secPumpXXXXPressureDelta | Secondary Pump Pressure Delta | Secondary Pump XX Pressure Delta |  | secPump(\w{0,4}(?=[A-Z]¦$))PressureDelta | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | secondary,water,pump,common,pressure,delta,sensor | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpPressureDeltaSp | secPumpXXXXPressureDeltaSp | Secondary Pump Pressure Delta Setpoint | Secondary Pump XX Pressure Delta Setpoint |  | secPump(\w{0,4}(?=[A-Z]¦$))PressureDeltaSp | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | secondary,water,pump,common,pressure,delta,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpPressureHiAlarm | secPumpXXXXPressureHiAlarm | Secondary Pump Pressure High Alarm | Secondary Pump XX Pressure High Alarm |  | secPump(\w{0,4}(?=[A-Z]¦$))PressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | secondary,water,pump,pressure,high,alarm | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpPressureHiSp | secPumpXXXXPressureHiSp | Secondary Pump Pressure High Setpoint | Secondary Pump XX Pressure High Setpoint |  | secPump(\w{0,4}(?=[A-Z]¦$))PressureHiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | secondary,water,pump,pressure,high,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpPressureLoAlarm | secPumpXXXXPressureLoAlarm | Secondary Pump Pressure Low Alarm | Secondary Pump XX Pressure Low Alarm |  | secPump(\w{0,4}(?=[A-Z]¦$))PressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | secondary,water,pump,pressure,low,alarm | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpPressureLoSp | secPumpXXXXPressureLoSp | Secondary Pump Pressure Low Setpoint | Secondary Pump XX Pressure Low Setpoint |  | secPump(\w{0,4}(?=[A-Z]¦$))PressureLoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | secondary,water,pump,pressure,low,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpRuntime | secPumpXXXXRuntime | Secondary Pump Runtime | Secondary Pump XX Runtime |  | secPump(\w{0,4}(?=[A-Z]¦$))Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | CWS,GEO,HWS,WS,WSS,HX | 2.15 (Released),2.16 (Pre-Release)
secPumpSpeed | secPumpXXXXSpeed | Secondary Pump Speed | Secondary Pump XX Speed |  | secPump(\w{0,4}(?=[A-Z]¦$))Speed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | secondary,water,pump,speed,cmd | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpSpeedFb | secPumpXXXXSpeedFb | Secondary Pump Speed Feedback | Secondary Pump XX Speed Feedback |  | secPump(\w{0,4}(?=[A-Z]¦$))SpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | secondary,water,pump,speed,sensor | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpSpeedMaxSp | secPumpXXXXSpeedMaxSp | Secondary Pump Speed Max Setpoint | Secondary Pump XX Speed Max Setpoint |  | secPump(\w{0,4}(?=[A-Z]¦$))SpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | secondary,water,pump,speed,max,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpSpeedMinSp | secPumpXXXXSpeedMinSp | Secondary Pump Speed Min Setpoint | Secondary Pump XX Speed Min Setpoint |  | secPump(\w{0,4}(?=[A-Z]¦$))SpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | secondary,water,pump,speed,min,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpSpeedOvr | secPumpXXXXSpeedOvr | Secondary Pump Speed Override | Secondary Pump XX Speed Override |  | secPump(\w{0,4}(?=[A-Z]¦$))SpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | secondary,water,pump,speed,ovr | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpSpeedSp | secPumpXXXXSpeedSp | Secondary Pump Speed Setpoint | Secondary Pump XX Speed Setpoint |  | secPump(\w{0,4}(?=[A-Z]¦$))SpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | secondary,water,pump,speed,effective,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpStageDownDelayOnSp | secPumpStageDownDelayOnSp | Secondary Pump Stage Down Delay On Septoint | Secondary Pump Stage Down Delay On Septoint |  | secPumpStageDownDelayOnSp | No | No | No | Number |  |  | minute | minute | 0 | 0 |  |  | secondary,water,pump,stageDown,delay,on,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpStageDownSp | secPumpStageDownSp | Secondary Pump Stage Down Septoint | Secondary Pump Stage Down Septoint |  | secPumpStageDownSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | secondary,water,pump,stageDown,effective,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpStageUpDelayOnSp | secPumpStageUpDelayOnSp | Secondary Pump Stage Up Delay On Septoint | Secondary Pump Stage Up Delay On Septoint |  | secPumpStageUpDelayOnSp | No | No | No | Number |  |  | minute | minute | 0 | 0 |  |  | secondary,water,pump,stageUp,delay,on,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpStageUpSp | secPumpStageUpSp | Secondary Pump Stage Up Septoint | Secondary Pump Stage Up Septoint |  | secPumpStageUpSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | secondary,water,pump,stageUp,effective,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secPumpStatus | secPumpXXXXStatus | Secondary Pump Status | Secondary Pump XX Status |  | secPump(\w{0,4}(?=[A-Z]¦$))Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | secondary,water,pump,status,common,sensor | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secStrainerAlarm | secStrainerAlarm | Secondary Strainer Alarm | Secondary Strainer Alarm |  | secStrainerAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | secondary,water,strainer,alarm | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secStrainerEnable | secStrainerEnable | Secondary Strainer Enable | Secondary Strainer Enable |  | secStrainerEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | secondary,water,strainer,enable,cmd | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secTempDelta | secTempDeltaXXXX | Secondary Temperature Differential | Secondary Temperature Differential XX |  | secTempDelta(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | secondary,water,delta,temp,sensor | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secTempDeltaDb | secTempDeltaXXXXDb | Secondary Temperature Differential Deadband | Secondary Temperature Differential XX Deadband |  | secTempDelta(\d{0,4})Db | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | secondary,water,delta,temp,deadband,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secTempDeltaHiSp | secTempDeltaXXXXHiSp | Secondary Temperature Differential High Setpoint | Secondary Temperature Differential XX High Setpoint |  | secTempDelta(\d{0,4})HiSp | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | secondary,water,delta,temp,high,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secTempDeltaLoSp | secTempDeltaXXXXLoSp | Secondary Temperature Differential Low Setpoint | Secondary Temperature Differential XX Low Setpoint |  | secTempDelta(\d{0,4})LoSp | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | secondary,water,delta,temp,low,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secTempDeltaMaxSp | secTempDeltaXXXXMaxSp | Secondary Temperature Differential Max Reset Setpoint | Secondary Temperature Differential XX Max Reset Setpoint |  | secTempDelta(\d{0,4})MaxSp | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | secondary,water,delta,temp,max,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secTempDeltaMinSp | secTempDeltaXXXXMinSp | Secondary Temperature Differential Min Reset Setpoint | Secondary Temperature Differential XX Min Reset Setpoint |  | secTempDelta(\d{0,4})MinSp | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | secondary,water,delta,temp,min,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secTempDeltaSp | secTempDeltaXXXXSp | Secondary Temperature Differential Setpoint | Secondary Temperature Differential XX Setpoint |  | secTempDelta(\d{0,4})Sp | Yes | Yes | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | secondary,water,delta,temp,effective,sp | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secValveOneThird | secValveOneThird | Secondary Valve 1/3 Command | Secondary Valve 1/3 Command |  | secValveOneThird | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | secondary,water,oneThird,valve,position,cmd | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secValveOneThirdFb | secValveOneThirdFb | Secondary Valve 1/3 Feedback | Secondary Valve 1/3 Feedback |  | secValveOneThirdFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | secondary,water,oneThird,valve,position,sensor | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secValveTwoThird | secValveTwoThird | Secondary Valve 2/3 Command | Secondary Valve 2/3 Command |  | secValveTwoThird | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | secondary,water,twoThird,valve,position,cmd | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secValveTwoThirdFb | secValveTwoThirdFb | Secondary Valve 2/3 Feedback | Secondary Valve 2/3 Feedback |  | secValveTwoThirdFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | secondary,water,twoThird,valve,position,sensor | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secValve | secValveXXXX | Secondary Valve Command | Secondary Valve XX Command |  | secValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | common,secondary,water,valve,general,position,cmd | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
secValveFb | secValveXXXXFb | Secondary Valve Feedback | Secondary Valve XX Feedback |  | secValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | common,secondary,water,valve,general,position,sensor | CWS,GEO,HWS,WS,WSS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
separatorPressureDelta | separatorPressureDelta | Separator Pressure Differential | Separator Pressure Differential |  | separatorPressureDelta | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | separator,pressure,delta,sensor | CMP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
shutdownAlarm | shutdownAlarm | Shutdown Alarm | Shutdown Alarm |  | shutdownAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | shutdown,common,alarm | AHU,ATU,BLR,CLR,CRAC,CRAH,CUH,CWS,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,GEO,HP,HRU,HWS,MAU,RTU,SMS,TWR,UV,VAV,WS,FCU,HP,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
shutdownSwitch | shutdownSwitch | Shutdown Switch | Shutdown Switch |  | shutdownSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | shutdown,switch,common,cmd | AHU,BLR,CLR,CWS,DHWS,GEN,HWS,RTU,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
signalStrength | signalStrength | Signal Strength | Signal Strength |  | signalStrength | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | signal,strength,sensor | MSC,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
slabEnteringTemp | slabEnteringTemp | Slab Entering Temperature | Slab Entering Temperature |  | slabEnteringTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | slab,entering,temp,sensor | FPB,RP,RPF,VAV,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
slabEnteringTempSp | slabEnteringTempSp | Slab Entering Temperature Setpoint | Slab Entering Temperature Setpoint |  | slabEnteringTempSp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | slab,entering,temp,sp | FPB,RP,RPF,VAV,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
slabLeavingTemp | slabLeavingTemp | Slab Leaving Temperature | Slab Leaving Temperature |  | slabLeavingTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | slab,leaving,temp,sensor | FPB,RP,RPF,VAV,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
slabTemp | slabXXXXTemp | Slab Temperature | Slab XX Temperature |  | slab(\d{0,4})Temp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | slab,common,temp,sensor | FPB,RP,RPF,VAV,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
slabTempHiAlarm | slabXXXXTempHiAlarm | Slab Temperature High Alarm | Slab XX Temperature High Alarm |  | slab(\d{0,4})TempHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | slab,temp,high,alarm | FPB,RP,RPF,VAV,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
slabTempHiSp | slabXXXXTempHiSp | Slab Temperature High Setpoint | Slab XX Temperature High Setpoint |  | slab(\d{0,4})TempHiSp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | slab,temp,high,sp | FPB,RP,RPF,VAV,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
slabTempSp | slabXXXXTempSp | Slab Temperature Setpoint | Slab XX Temperature Setpoint |  | slab(\d{0,4})TempSp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | slab,temp,effective,sp | FPB,RP,RPF,VAV,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
smokeDetectAlarm | smokeDetectXXXXAlarm | Smoke Alarm | Smoke Alarm XX |  | smokeDetect(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | smoke,detect,alarm | AHU,ATU,DH,FCU,MAU,RTU,SMEX,FCU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
smokeDamperAlarm | smokeDamperXXXXAlarm | Smoke Damper Alarm | Smoke Damper XX Alarm |  | smokeDamper(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | smoke,damper,alarm | MSC,SMEX,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
smokeDamper | smokeDamperXXXX | Smoke Damper Command | Smoke Damper XX Command |  | smokeDamper(\d{0,4}) | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | smoke,damper,position,cmd | MSC,SMEX,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
smokeDamperFb | smokeDamperXXXXFb | Smoke Damper Feedback | Smoke Damper XX Feedback |  | smokeDamper(\d{0,4})Fb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | smoke,damper,position,sensor | MSC,SMEX,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
smokePurge | smokePurgeXXXX | Smoke Purge | Smoke Purge XX |  | smokePurge(\d{0,4}) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | smoke,purge,cmd | AHU,RTU,SMEX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
snowDetectAlarm | snowDetectAlarm | Snow Detection Alarm | Snow Detection Alarm |  | snowDetectAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | snow,detect,alarm | MSC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
solarRadiation | solarRadiation | Solar Radiation | Solar Radiation |  | solarRadiation | Yes | Yes | No | Number |  |  | watts_per_square_meter | watts_per_square_meter | 2 | 2 |  |  | solar,radiation,flux,sensor | GBL,LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sourceEnteringTemp | sourceEnteringTempXXXX | Source Entering Temperature | Source Entering Temperature XX |  | sourceEnteringTemp(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | source,entering,temp,sensor | CLR,HP,HP,HX | 2.14,2.15 (Released),2.16 (Pre-Release)
sourceFlowStatus | sourceFlowXXXXStatus | Source Flow Status | Source Flow XX Status |  | sourceFlow(\d{0,4})Status | Yes | Yes | No | Bool | Flow/No Flow | Flow/No Flow | [6 empty] | source,flow,status,sensor | CLR,HP,HP,HX | 2.14,2.15 (Released),2.16 (Pre-Release)
sourceLeavingTemp | sourceLeavingTempXXXX | Source Leaving Temperature | Source Leaving Temperature XX |  | sourceLeavingTemp(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | source,leaving,temp,sensor | CLR,HP,HP,HX | 2.14,2.15 (Released),2.16 (Pre-Release)
sprinklerAlarm | sprinklerAlarm | Sprinkler Alarm | Sprinkler Alarm |  | sprinklerAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | sprinkler,alarm | FSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sprinklerIsoValve | sprinklerIsoValve | Sprinkler Isolation Valve Command | Sprinkler Isolation Valve Command |  | sprinklerIsoValve | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | sprinkler,iso,valve,position,cmd | FSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sprinklerIsoValveFb | sprinklerIsoValveFb | Sprinkler Isolation Valve Feedback | Sprinkler Isolation Valve Feedback |  | sprinklerIsoValveFb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | sprinkler,iso,valve,position,sensor | FSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sprinklerPressure | sprinklerPressure | Sprinkler Pressure | Sprinkler Pressure |  | sprinklerPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | sprinkler,pressure,sensor | FSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
standbyDimLevelSp | standbyDimLevelSp | Standby Dimming Level Setpoint | Standby Dimming Level Setpoint |  | standbyDimLevelSp | No | No | No | Number |  |  | footcandle | lux | 0 | 0 |  |  | standby,dimming,lightLevel,sp | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
standbyMode | standbyMode | Standby Mode | Standby Mode |  | standbyMode | Yes | No | No | Bool | On/Off | On/Off | [6 empty] | standby,mode,common,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DOAS,FCU,FPB,HP,MAU,RP,RPC,RPF,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
standbyModeTime | standbyModeTime | Standby Mode Time Remaining | Standby Mode Time Remaining |  | standbyModeTime | Yes | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | standby,mode,time,sensor | AHU,ATU,CRAC,CRAH,CUH,DH,DOAS,FCU,FPB,HP,MAU,RP,RPC,RPF,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
standbyModeTimeSp | standbyModeTimeSp | Standby Mode Time Remaining Setpoint | Standby Mode Time Remaining Setpoint |  | standbyModeTimeSp | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | standby,mode,time,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DOAS,FCU,FPB,HP,MAU,RP,RPC,RPF,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
standbyTempDb | standbyTempDb | Standby Temperature Deadband | Standby Temperature Deadband |  | standbyTempDb | Yes | Yes | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | standby,air,temp,deadband,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RP,RPC,RPF,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
steamPressure | steamPressureXXXX | Steam Pressure | Steam Pressure XX |  | steamPressure(\d{0,4}) | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | steam,pressure,sensor | BLR,SM,SMS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
steamPressureDb | steamPressureXXXXDb | Steam Pressure Deadband | Steam Pressure XX Deadband |  | steamPressure(\d{0,4})Db | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | steam,pressure,deadband,sp | BLR,SMS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
steamPressureHiSp | steamPressureXXXXHiSp | Steam Pressure High Setpoint | Steam Pressure XX High Setpoint |  | steamPressure(\d{0,4})HiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | steam,pressure,high,sp | BLR,SMS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
steamPressureLoSp | steamPressureXXXXLoSp | Steam Pressure Low Setpoint | Steam Pressure XX Low Setpoint |  | steamPressure(\d{0,4})LoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | steam,pressure,low,sp | BLR,SMS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
steamPressureMaxSp | steamPressureXXXXMaxSp | Steam Pressure Max Reset Setpoint | Steam Pressure XX Max Reset Setpoint |  | steamPressure(\d{0,4})MaxSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | steam,pressure,max,sp | BLR,SMS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
steamPressureMinSp | steamPressureXXXXMinSp | Steam Pressure Min Reset Setpoint | Steam Pressure XX Min Reset Setpoint |  | steamPressure(\d{0,4})MinSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | steam,pressure,min,sp | BLR,SMS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
steamPressureSp | steamPressureXXXXSp | Steam Pressure Setpoint | Steam Pressure XX Setpoint |  | steamPressure(\d{0,4})Sp | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | steam,pressure,effective,sp | BLR,SMS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
steamTemp | steamTempXXXX | Steam Temperature | Steam Temperature XX |  | steamTemp(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | steam,temp,sensor | BLR,SM,SMS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
strobe | strobe | Strobe | Strobe |  | strobe | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | strobe,cmd | EF,FP,GDS,HDS,LDS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpHeater | sumpHeater | Sump Heater Command | Sump Heater Command |  | sumpHeater | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | sump,water,heater,status,cmd | LS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpHeaterCurrent | sumpHeaterCurrent | Sump Heater Current | Sump Heater Current |  | sumpHeaterCurrent | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | sump,water,heater,current,sensor | LS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpHeaterStatus | sumpHeaterStatus | Sump Heater Status | Sump Heater Status |  | sumpHeaterStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | sump,water,heater,status,sensor | LS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpLevel | sumpLevel | Sump Level | Sump Level |  | sumpLevel | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | sump,water,level,sensor | LS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpLevelFillAlarm | sumpLevelFillAlarm | Sump Level Fill Alarm | Sump Level Fill Alarm |  | sumpLevelFillAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | sump,water,level,fill,alarm | LS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpLevelHiAlarm | sumpLevelXXXXHiAlarm | Sump Level High Alarm | Sump Level XX High Alarm |  | sumpLevel(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | sump,water,level,high,alarm | LS,SMP,TWR | 2.14,2.15 (Released),2.16 (Pre-Release)
sumpLevelHiSp | sumpLevelHiSp | Sump Level High Setpoint | Sump Level High Setpoint |  | sumpLevelHiSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | sump,water,level,high,sp | LS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpLevelLoAlarm | sumpLevelLoAlarm | Sump Level Low Alarm | Sump Level Low Alarm |  | sumpLevelLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | sump,water,level,low,alarm | LS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpLevelLoSp | sumpLevelLoSp | Sump Level Low Setpoint | Sump Level Low Setpoint |  | sumpLevelLoSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | sump,water,level,low,sp | LS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpPumpAlarm | sumpPumpXXXXAlarm | Sump Pump Alarm | Sump Pump XX Alarm |  | sumpPump(\w{0,4}(?=[A-Z]¦$))Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | sump,water,pump,common,alarm | LS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpPumpAlarmReset | sumpPumpXXXXAlarmReset | Sump Pump Alarm Reset | Sump Pump XX Alarm Reset |  | sumpPump(\w{0,4}(?=[A-Z]¦$))AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | sump,water,pump,reset,alarm | LS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpPump | sumpPumpXXXX | Sump Pump Command | Sump Pump XX Command |  | sumpPump((?:(?!Lead)(?!Ovr)\w){0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | sump,water,pump,status,cmd | LS,SMP,TWR | 2.15 (Released),2.16 (Pre-Release)
sumpPumpCurrent | sumpPumpXXXXCurrent | Sump Pump Current | Sump Pump XX Current |  | sumpPump(\w{0,4}(?=[A-Z]¦$))Current | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | sump,water,pump,current,sensor | LS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpPumpEnable | sumpPumpXXXXEnable | Sump Pump Enable | Sump Pump XX Enable |  | sumpPump(\w{0,4}(?=[A-Z]¦$))Enable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | sump,water,pump,enable,cmd | LS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpPumpEnableDb | sumpPumpXXXXEnableDb | Sump Pump Enable Deadband | Sump Pump XX Enable Deadband |  | sumpPump(\w{0,4}(?=[A-Z]¦$))EnableDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | sump,water,pump,enable,deadband,sp | LS,SMP,TWR | 2.15 (Released),2.16 (Pre-Release)
sumpPumpEnableSp | sumpPumpXXXXEnableSp | Sump Pump Enable Setpoint | Sump Pump XX Enable Setpoint |  | sumpPump((?:(?!Lag)\w){0,4}(?=[A-Z]¦$))EnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | sump,water,pump,enable,effective,sp | LS,SMP,TWR | 2.15 (Released),2.16 (Pre-Release)
sumpPumpEnteringPressure | sumpPumpXXXXEnteringPressure | Sump Pump Entering Pressure | Sump Pump XX Entering Pressure |  | sumpPump(\w{0,4}(?=[A-Z]¦$))EnteringPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | sump,water,pump,entering,pressure,sensor | LS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpPumpFault | sumpPumpXXXXFault | Sump Pump Fault | Sump Pump XX Fault |  | sumpPump(\w{0,4}(?=[A-Z]¦$))Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | sump,water,pump,fault | LS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpPumpLagDisableSp | sumpPumpXXXXLagDisableSp | Sump Pump Lag Disable Setpoint | Sump Pump XX Lag Disable Setpoint |  | sumpPump(\w{0,4}(?=[A-Z]¦$))LagDisableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | sump,water,pump,lag,disable,sp | LS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpPumpLagEnableSp | sumpPumpXXXXLagEnableSp | Sump Pump Lag Enable Setpoint | Sump Pump XX Lag Enable Setpoint |  | sumpPump(\w{0,4}(?=[A-Z]¦$))LagEnableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | sump,water,pump,lag,enable,sp | LS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpPumpLagReq | sumpPumpXXXXLagReq | Sump Pump Lag Request | Sump Pump XX Lag Request |  | sumpPump(\w{0,4}(?=[A-Z]¦$))LagReq | No | No | No | Bool | Request/No Request | Request/No Request | [6 empty] | sump,water,pump,lag,request,cmd | LS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpPumpLead | sumpPumpLead | Sump Pump Lead | Sump Pump Lead |  | sumpPumpLead | Yes | Yes | No | Bool | Lead 1/Lead 2 | Lead 1/Lead 2 | [6 empty] | sump,water,pump,lead,sp | LS,SMP,TWR | 2.15 (Released),2.16 (Pre-Release)
sumpPumpLeadXor | sumpPumpLeadXor | Sump Pump Lead Change Over | Sump Pump Lead Change Over |  | sumpPumpLeadXor | No | No | No | Bool | On/Off | On/Off | [6 empty] | sump,water,pump,lead,changeOver,cmd | LS,SMP,TWR | 2.15 (Released),2.16 (Pre-Release)
sumpPumpLeadXorRuntimeSp | sumpPumpLeadXorRuntimeSp | Sump Pump Lead Change Over Runtime Setpoint | Sump Pump Lead Change Over Runtime Setpoint |  | sumpPumpLeadXorRuntimeSp | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | LS,SMP,TWR | 2.15 (Released),2.16 (Pre-Release)
sumpPumpLeavingPressure | sumpPumpXXXXLeavingPressure | Sump Pump Leaving Pressure | Sump Pump XX Leaving Pressure |  | sumpPump(\w{0,4}(?=[A-Z]¦$))LeavingPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | sump,water,pump,leaving,pressure,sensor | LS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpPumpMaintSwitch | sumpPumpXXXXMaintSwitch | Sump Pump Maintenance Switch | Sump Pump XX Maintenance Switch |  | sumpPump(\w{0,4}(?=[A-Z]¦$))MaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | sump,water,pump,maintenance,switch,cmd | LS,SMP,TWR | 2.15 (Released),2.16 (Pre-Release)
sumpPumpOvr | sumpPumpXXXXOvr | Sump Pump Override | Sump Pump XX Override |  | sumpPump(\w{0,4}(?=[A-Z]¦$))Ovr | No | No | No | Bool | On/Off | On/Off | [6 empty] | sump,water,pump,status,ovr | LS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpPumpPressureDelta | sumpPumpXXXXPressureDelta | Sump Pump Pressure Delta | Sump Pump XX Pressure Delta |  | sumpPump(\w{0,4}(?=[A-Z]¦$))PressureDelta | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | sump,water,pump,common,pressure,delta,sensor | LS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpPumpPressureHiAlarm | sumpPumpXXXXPressureHiAlarm | Sump Pump Pressure High Alarm | Sump Pump XX Pressure High Alarm |  | sumpPump(\w{0,4}(?=[A-Z]¦$))PressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | sump,water,pump,pressure,high,alarm | LS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpPumpPressureHiSp | sumpPumpXXXXPressureHiSp | Sump Pump Pressure High Setpoint | Sump Pump XX Pressure High Setpoint |  | sumpPump(\w{0,4}(?=[A-Z]¦$))PressureHiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | sump,water,pump,pressure,high,sp | LS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpPumpPressureLoAlarm | sumpPumpXXXXPressureLoAlarm | Sump Pump Pressure Low Alarm | Sump Pump XX Pressure Low Alarm |  | sumpPump(\w{0,4}(?=[A-Z]¦$))PressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | sump,water,pump,pressure,low,alarm | LS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpPumpPressureLoSp | sumpPumpXXXXPressureLoSp | Sump Pump Pressure Low Setpoint | Sump Pump XX Pressure Low Setpoint |  | sumpPump(\w{0,4}(?=[A-Z]¦$))PressureLoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | sump,water,pump,pressure,low,sp | LS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpPumpRuntime | sumpPumpXXXXRuntime | Sump Pump Runtime | Sump Pump XX Runtime |  | sumpPump(\w{0,4}(?=[A-Z]¦$))Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | LS,SMP,TWR | 2.15 (Released),2.16 (Pre-Release)
sumpPumpSpeed | sumpPumpXXXXSpeed | Sump Pump Speed | Sump Pump XX Speed |  | sumpPump(\w{0,4}(?=[A-Z]¦$))Speed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | sump,water,pump,speed,cmd | LS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpPumpSpeedFb | sumpPumpXXXXSpeedFb | Sump Pump Speed Feedback | Sump Pump XX Speed Feedback |  | sumpPump(\w{0,4}(?=[A-Z]¦$))SpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | sump,water,pump,speed,sensor | LS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpPumpSpeedMaxSp | sumpPumpXXXXSpeedMaxSp | Sump Pump Speed Max Setpoint | Sump Pump XX Speed Max Setpoint |  | sumpPump(\w{0,4}(?=[A-Z]¦$))SpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | sump,water,pump,speed,max,sp | LS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpPumpSpeedMinSp | sumpPumpXXXXSpeedMinSp | Sump Pump Speed Min Setpoint | Sump Pump XX Speed Min Setpoint |  | sumpPump(\w{0,4}(?=[A-Z]¦$))SpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | sump,water,pump,speed,min,sp | LS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpPumpSpeedOvr | sumpPumpXXXXSpeedOvr | Sump Pump Speed Override | Sump Pump XX Speed Override |  | sumpPump(\w{0,4}(?=[A-Z]¦$))SpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | sump,water,pump,speed,ovr | LS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpPumpSpeedSp | sumpPumpXXXXSpeedSp | Sump Pump Speed Setpoint | Sump Pump XX Speed Setpoint |  | sumpPump(\w{0,4}(?=[A-Z]¦$))SpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | sump,water,pump,speed,effective,sp | LS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpPumpStatus | sumpPumpXXXXStatus | Sump Pump Status | Sump Pump XX Status |  | sumpPump(\w{0,4}(?=[A-Z]¦$))Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | sump,water,pump,status,sensor | LS,SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpTemp | sumpTemp | Sump Temperature | Sump Temperature |  | sumpTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | sump,water,temp,sensor | SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sumpTempLoSp | sumpTempLoSp | Sump Temperature Low Setpoint | Sump Temperature Low Setpoint |  | sumpTempLoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | sump,water,temp,low,sp | SMP,TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sunriseTime | sunriseTime | Sunrise Time | Sunrise Time |  | sunriseTime | Yes | No | No | Str |  | hh:mm | [6 empty] | sunrise,time,sensor | WTHR | 2.15 (Released)
sunsetTime | sunsetTime | Sunset Time | Sunset Time |  | sunsetTime | Yes | No | No | Str |  | hh:mm | [6 empty] | sunset,time,sensor | WTHR | 2.15 (Released)
supervisoryAlarm | supervisoryAlarm | Supervisory Alarm | Supervisory Alarm |  | supervisoryAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | supervisor,alarm | MSC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
sweepTime | sweepTime | Sweep Time | Sweep Time |  | sweepTime | Yes | No | No | Number |  |  | second | second | 0 | 0 |  |  | sweep,time,sensor | RRS | 2.15 (Released),2.16 (Pre-Release)
systemAlarm | systemAlarm | System Alarm | System Alarm |  | systemAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | system,common,alarm | CWS,FC,GEO,GINT,HDS,HWS,PINT,RFG,ROS,SEC,SMEX,SMS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
systemAlarmReset | systemAlarmReset | System Alarm Reset | System Alarm Reset |  | systemAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | system,reset,alarm | CWS,FC,GEO,GINT,HDS,HWS,PINT,RFG,ROS,SEC,SMEX,SMS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
systemBypassSwitch | systemBypassSwitch | System Bypass Switch | System Bypass Switch |  | systemBypassSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | system,bypass,switch,cmd | CWS,FC,GEO,GINT,HDS,HWS,PINT,RFG,ROS,SMEX,SMS,UPS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
systemDisableSp | systemDisableSp | System Disable Setpoint | System Disable Setpoint |  | systemDisableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | system,disable,sp | CWS,FC,GEO,GINT,HDS,HWS,PINT,RFG,ROS,SMEX,SMS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
systemEfficiency | systemEfficiency | System Efficiency | System Efficiency |  | systemEfficiency | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | system,efficiency,sensor | CWS,FC,GEO,GINT,HDS,HWS,PINT,RFG,ROS,SMEX,SMS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
systemEnable | systemEnable | System Enable Command | System Enable Command |  | systemEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | system,enable,cmd | CWS,FC,GEO,GINT,HDS,HWS,PINT,RFG,ROS,SMEX,SMS,WS,CDA | 2.14,2.15 (Released),2.16 (Pre-Release)
systemEnableDb | systemEnableDb | System Enable Deadband | System Enable Deadband |  | systemEnableDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | system,enable,deadband,sp | CWS,FC,GEO,GINT,HDS,HWS,PINT,RFG,ROS,SMEX,SMS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
systemEnableOvr | systemEnableOvr | System Enable Override | System Enable Override |  | systemEnableOvr | No | No | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | system,enable,ovr | CWS,FC,GEO,GINT,HDS,HWS,PINT,RFG,ROS,SMEX,SMS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
systemEnableSp | systemEnableSp | System Enable Setpoint | System Enable Setpoint |  | systemEnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | system,enable,effective,sp | CWS,FC,GEO,GINT,HDS,HWS,PINT,RFG,ROS,SMEX,SMS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
systemFault | systemFault | System Fault | System Fault |  | systemFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | system,fault | CWS,FC,GEO,GINT,HDS,HWS,PINT,RFG,ROS,SMEX,SMS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
systemHandMode | systemHandMode | System Hand Mode | System Hand Mode |  | systemHandMode | Yes | Yes | No | Bool | Hand/Auto | Hand/Auto | [6 empty] | system,handMode,sensor | CWS,FC,GEO,GINT,HDS,HWS,PINT,RFG,ROS,SMEX,SMS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
systemLoad | systemLoad | System Load | System Load |  | systemLoad | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | system,load,sensor | CWS,FC,GEO,GINT,HDS,HWS,PINT,RFG,ROS,SMEX,SMS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
systemMaintAlarm | systemMaintAlarm | System Maintenance Alarm | System Maintenance Alarm |  | systemMaintAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | system,maintenance,alarm | CWS,FC,GEO,GINT,HDS,HWS,PINT,RFG,ROS,SMEX,SMS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
systemMode | systemMode | System Mode | System Mode |  | systemMode | Yes | Yes | No | Str | On/Off | On/Off/Idle/Hand | [6 empty] | system,mode,sp | CWS,FC,GEO,GINT,HDS,HWS,PINT,RFG,ROS,SEC,SMEX,SMS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
systemPressureAlarm | systemPressureAlarm | System Pressure Alarm | System Pressure Alarm |  | systemPressureAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | system,pressure,alarm | CWS,FC,GEO,GINT,HDS,HWS,PINT,RFG,ROS,SMEX,SMS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
systemRegeneration | systemRegeneration | System Regeneration Command | System Regeneration Command |  | systemRegeneration | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | system,regeneration,status,cmd | CWS,FC,GEO,GINT,HDS,HWS,PINT,RFG,ROS,SMEX,SMS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
systemRuntime | systemRuntime | System Runtime | System Runtime |  | systemRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | CWS,FC,GEO,GINT,HDS,HWS,PINT,RFG,ROS,SMEX,SMS,WS | 2.15 (Released),2.16 (Pre-Release)
systemShutdown | systemShutdown | System Shutdown | System Shutdown |  | systemShutdown | Yes | Yes | No | Bool | Shutdown/Auto | Shutdown/Auto | [6 empty] | system,shutdown,sp | CWS,FC,GEO,GINT,HDS,HWS,PINT,RFG,ROS,SMEX,SMS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
systemTrouble | systemTrouble | System Trouble | System Trouble |  | systemTrouble | Yes | Yes | No | Bool | Trouble/Normal | Trouble/Normal | [6 empty] | system,trouble,sensor | CWS,FC,GEO,GINT,HDS,HWS,PINT,RFG,ROS,SEC,SMEX,SMS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
systemWarning | systemWarning | System Warning | System Warning |  | systemWarning | Yes | Yes | No | Bool | Warning/Normal | Warning/Normal | [6 empty] | system,warning | CWS,FC,GEO,GINT,HDS,HWS,PINT,RFG,ROS,SMEX,SMS,WS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankTempBottom | tankTempBottom | Tank Bottom Temperature | Tank Bottom Temperature |  | tankTempBottom | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | tank,water,bottom,temp,sensor | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankBypassValve | tankBypassValveXXXX | Tank Bypass Valve Command | Tank Bypass Valve XX Command |  | tankBypassValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | tank,water,bypass,valve,position,cmd | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankBypassValveFb | tankBypassValveXXXXFb | Tank Bypass Valve Feedback | Tank Bypass Valve XX Feedback |  | tankBypassValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | tank,water,bypass,valve,position,sensor | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankEnteringPressure | tankEnteringPressure | Tank Entering Pressure | Tank Entering Pressure |  | tankEnteringPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | tank,entering,pressure,sensor | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankEnteringPressureAlarm | tankEnteringPressureAlarm | Tank Entering Pressure Alarm | Tank Entering Pressure Alarm |  | tankEnteringPressureAlarm | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | tank,entering,pressure,common,alarm | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankEnteringPressureHiAlarm | tankEnteringPressureHiAlarm | Tank Entering Pressure High Alarm | Tank Entering Pressure High Alarm |  | tankEnteringPressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | tank,entering,pressure,high,alarm | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankEnteringPressureLoAlarm | tankEnteringPressureLoAlarm | Tank Entering Pressure Low Alarm | Tank Entering Pressure Low Alarm |  | tankEnteringPressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | tank,entering,pressure,low,alarm | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankEnteringTemp | tankEnteringTemp | Tank Entering Temperature | Tank Entering Temperature |  | tankEnteringTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | tank,water,entering,temp,sensor | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankEnteringTempHiAlarm | tankEnteringTempHiAlarm | Tank Entering Temperature High Alarm | Tank Entering Temperature High Alarm |  | tankEnteringTempHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | tank,entering,temp,high,alarm | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankEnteringTempLoAlarm | tankEnteringTempLoAlarm | Tank Entering Temperature Low Alarm | Tank Entering Temperature Low Alarm |  | tankEnteringTempLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | tank,entering,temp,low,alarm | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankFillValve | tankFillValve | Tank Fill Valve Command | Tank Fill Valve Command |  | tankFillValve | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | tank,water,fill,valve,position,cmd | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankFillValveFb | tankFillValveFb | Tank Fill Valve Feedback | Tank Fill Valve Feedback |  | tankFillValveFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | tank,water,fill,valve,position,sensor | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankFillVolume | tankFillVolume | Tank Fill Volume | Tank Fill Volume |  | tankFillVolume | Yes | Yes | No | Number |  |  | gallon | liter | 0 | 0 |  |  | tank,water,fill,volume,sensor | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankFillVolumeSp | tankFillVolumeSp | Tank Fill Volume Setpoint | Tank Fill Volume Setpoint |  | tankFillVolumeSp | Yes | Yes | No | Number |  |  | gallon | liter | 0 | 0 |  |  | tank,water,fill,volume,sp | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankLeavingPressure | tankLeavingPressure | Tank Leaving Pressure | Tank Leaving Pressure |  | tankLeavingPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | tank,leaving,pressure,sensor | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankLeavingPressureDb | tankLeavingPressureDb | Tank Leaving Pressure Deadband | Tank Leaving Pressure Deadband |  | tankLeavingPressureDb | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | tank,leaving,pressure,deadband,sp | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankLeavingPressureHiSp | tankLeavingPressureHiSp | Tank Leaving Pressure High Setpoint | Tank Leaving Pressure High Setpoint |  | tankLeavingPressureHiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | tank,leaving,pressure,high,sp | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankLeavingPressureLoSp | tankLeavingPressureLoSp | Tank Leaving Pressure Low Setpoint | Tank Leaving Pressure Low Setpoint |  | tankLeavingPressureLoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | tank,leaving,pressure,low,sp | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankLeavingPressureSp | tankLeavingPressureSp | Tank Leaving Pressure Setpoint | Tank Leaving Pressure Setpoint |  | tankLeavingPressureSp | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | tank,leaving,pressure,effective,sp | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankLeavingTemp | tankLeavingTemp | Tank Leaving Temperature | Tank Leaving Temperature |  | tankLeavingTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | tank,water,leaving,temp,sensor | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankLevel | tankLevelXXXX | Tank Level | Tank Level XX |  | tankLevel(\d{0,4}) | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | tank,water,level,sensor | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankLevelAlarm | tankLevelXXXXAlarm | Tank Level Alarm | Tank Level XX Alarm |  | tankLevel(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | tank,water,level,common,alarm | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankLevelFault | tankLevelXXXXFault | Tank Level Fault | Tank Level XX Fault |  | tankLevel(\d{0,4})Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | tank,water,level,fault | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankLevelHiAlarm | tankLevelXXXXHiAlarm | Tank Level High Alarm | Tank Level XX High Alarm |  | tankLevel(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | tank,water,level,high,alarm | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankLevelHiSp | tankLevelXXXXHiSp | Tank Level High Setpoint | Tank Level XX High Setpoint |  | tankLevel(\d{0,4})HiSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | tank,water,level,high,sp | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankLevelLoAlarm | tankLevelXXXXLoAlarm | Tank Level Low Alarm | Tank Level XX Low Alarm |  | tankLevel(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | tank,water,level,low,alarm | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankLevelLoSp | tankLevelXXXXLoSp | Tank Level Low Setpoint | Tank Level XX Low Setpoint |  | tankLevel(\d{0,4})LoSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | tank,water,level,low,sp | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankTempMid | tankTempMid | Tank Middle Temperature | Tank Middle Temperature |  | tankTempMid | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | tank,water,mid,temp,sensor | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankPressure | tankPressure | Tank Pressure | Tank Pressure |  | tankPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | tank,static,pressure,sensor | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankPressureDb | tankPressureDb | Tank Pressure Deadband | Tank Pressure Deadband |  | tankPressureDb | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | tank,static,pressure,deadband,sp | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankPressureDelta | tankPressureDelta | Tank Pressure Delta | Tank Pressure Delta |  | tankPressureDelta | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | tank,delta,pressure,sensor | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankPressureHiAlarm | tankPressureHiAlarm | Tank Pressure High Alarm | Tank Pressure High Alarm |  | tankPressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | tank,static,pressure,high,alarm | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankPressureHiSp | tankPressureHiSp | Tank Pressure High Setpoint | Tank Pressure High Setpoint |  | tankPressureHiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | tank,static,pressure,high,sp | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankPressureLoSp | tankPressureLoSp | Tank Pressure Low Setpoint | Tank Pressure Low Setpoint |  | tankPressureLoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | tank,static,pressure,low,sp | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankPressureSp | tankPressureSp | Tank Pressure Setpoint | Tank Pressure Setpoint |  | tankPressureSp | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | tank,static,pressure,effective,sp | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankTemp | tankTemp | Tank Temperature | Tank Temperature |  | tankTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | tank,water,common,temp,sensor | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankTempFault | tankTempFault | Tank Temperature Fault | Tank Temperature Fault |  | tankTempFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | tank,water,temp,fault | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankTempHiAlarm | tankTempHiAlarm | Tank Temperature High Alarm | Tank Temperature High Alarm |  | tankTempHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | tank,water,temp,high,alarm | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankTempHiSp | tankTempHiSp | Tank Temperature High Setpoint | Tank Temperature High Setpoint |  | tankTempHiSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | tank,water,temp,high,sp | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankTempLoAlarm | tankTempLoAlarm | Tank Temperature Low Alarm | Tank Temperature Low Alarm |  | tankTempLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | tank,water,temp,low,alarm | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankTempLoSp | tankTempLoSp | Tank Temperature Low Setpoint | Tank Temperature Low Setpoint |  | tankTempLoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | tank,water,temp,low,sp | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankTempSp | tankTempSp | Tank Temperature Setpoint | Tank Temperature Setpoint |  | tankTempSp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | tank,water,effective,temp,sp | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
tankTempTop | tankTempTop | Tank Top Temperature | Tank Top Temperature |  | tankTempTop | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | tank,water,top,temp,sensor | TNK | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
thermoExpansionValve | thermoExpansionValveXXXX | Thermo Expansion Valve Command | Thermo Expansion Valve XX Command |  | thermoExpansionValve(\d{0,4}) | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | thermo,expansion,valve,status,cmd | AC,AHU,ATU,CLR,CMP,FCU,HP,RTU,UV,VRF,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
thermoExpansionValveFb | thermoExpansionValveXXXXFb | Thermo Expansion Valve Feedback | Thermo Expansion Valve XX Feedback |  | thermoExpansionValve(\d{0,4})Fb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | thermo,expansion,valve,status,sensor | AC,AHU,ATU,CLR,CMP,FCU,HP,RTU,UV,VRF,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
totalHarmonicDistortion | totalHarmonicDistortion | Total Harmonic Distortion | Total Harmonic Distortion |  | totalHarmonicDistortion | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | total,harmonic,distortion,sensor | PM,PRLY,PV,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
flowTotalizer | flowTotalizer | Totalized Flow | Totalized Flow |  | flowTotalizer | Yes | Yes | Yes | Number |  |  | gallon | liter | 0 | 1 |  |  | common,flowConsumption,sensor | BLR,BTU,CLR,CM,CWS,GEO,GM,HWS,SM,SMS,TWR,VBTU,VGM,VWM,WM,WS,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrBypassFlow | twrBypassFlowXXXX | Tower Bypass Flow | Tower Bypass Flow XX |  | twrBypassFlow(\d{0,4}) | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,bypass,flow,cmd,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrBypassFlowDb | twrBypassFlowXXXXDb | Tower Bypass Flow Deadband | Tower Bypass Flow XX Deadband |  | twrBypassFlow(\d{0,4})Db | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,bypass,flow,deadband,sp,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrBypassFlowHiSp | twrBypassFlowXXXXHiSp | Tower Bypass Flow High Setpoint | Tower Bypass Flow XX High Setpoint |  | twrBypassFlow(\d{0,4})HiSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,bypass,flow,high,sp,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrBypassFlowLoSp | twrBypassFlowXXXXLoSp | Tower Bypass Flow Low Setpoint | Tower Bypass Flow XX Low Setpoint |  | twrBypassFlow(\d{0,4})LoSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,bypass,flow,low,sp,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrBypassFlowMaxSp | twrBypassFlowXXXXMaxSp | Tower Bypass Flow Max Reset Setpoint | Tower Bypass Flow XX Max Reset Setpoint |  | twrBypassFlow(\d{0,4})MaxSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,bypass,flow,max,sp,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrBypassFlowMinSp | twrBypassFlowXXXXMinSp | Tower Bypass Flow Min Reset Setpoint | Tower Bypass Flow XX Min Reset Setpoint |  | twrBypassFlow(\d{0,4})MinSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,bypass,flow,min,sp,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrBypassFlowSp | twrBypassFlowXXXXSp | Tower Bypass Flow Setpoint | Tower Bypass Flow XX Setpoint |  | twrBypassFlow(\d{0,4})Sp | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,bypass,flow,effective,sp,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrBypassTemp | twrBypassTempXXXX | Tower Bypass Temperature | Tower Bypass Temperature XX |  | twrBypassTemp(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | condensed,water,bypass,temp,sensor,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrBypassValve | twrBypassValveXXXX | Tower Bypass Valve Command | Tower Bypass Valve XX Command |  | twrBypassValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | condensed,water,bypass,valve,position,cmd,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrBypassValveFb | twrBypassValveXXXXFb | Tower Bypass Valve Feedback | Tower Bypass Valve XX Feedback |  | twrBypassValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | condensed,water,bypass,valve,position,sensor,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrBypassValveOvr | twrBypassValveXXXXOvr | Tower Bypass Valve Override | Tower Bypass Valve XX Override |  | twrBypassValve(\d{0,4})Ovr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | condensed,water,bypass,valve,position,ovr,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrDamper | twrDamperXXXX | Tower Damper Command | Tower Damper XX Command |  | twrDamper(\d{0,4}) | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | tower,damper,air,position,cmd | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrDamperFb | twrDamperXXXXFb | Tower Damper Feedback | Tower Damper XX Feedback |  | twrDamper(\d{0,4})Fb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | tower,damper,air,position,sensor | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrDefrost | twrDefrost | Tower Defrost | Tower Defrost |  | twrDefrost | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | tower,defrost,cmd | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrDrainValve | twrDrainValve | Tower Drain Valve Command | Tower Drain Valve Command |  | twrDrainValve | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | condensed,water,drain,valve,position,cmd,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrDrainValveFb | twrDrainValveFb | Tower Drain Valve Feedback | Tower Drain Valve Feedback |  | twrDrainValveFb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | condensed,water,drain,valve,position,sensor,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrEnable | twrEnable | Tower Enable | Tower Enable |  | twrEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | condensed,water,enable,cmd,tower | TWR | 2.14,2.15 (Released),2.16 (Pre-Release)
twrEnableSp | twrEnableSp | Tower Enable Setpoint | Tower Enable Setpoint |  | twrEnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | condensed,water,enable,sp,tower | TWR | 2.14,2.15 (Released),2.16 (Pre-Release)
twrLeavingFlow | twrLeavingFlow | Tower Entering Flow | Tower Entering Flow |  | twrLeavingFlow | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,leaving,flow,sensor | TWR | 2.12,2.13,2.14,2.15 (Released)
twrEnteringFlow | twrEnteringFlow | Tower Entering Flow | Tower Entering Flow |  | twrEnteringFlow | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,entering,flow,sensor,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrEnteringFlowMinSp | twrEnteringFlowMinSp | Tower Entering Flow Min Setpoint | Tower Entering Flow Min Setpoint |  | twrEnteringFlowMinSp | No | No | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,entering,flow,min,sp,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrEnteringIsoValve | twrEnteringIsoValveXXXX | Tower Entering Isolation Valve Command | Tower Entering Isolation Valve XX Command |  | twrEnteringIsoValve(\d{0,4}) | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | condensed,water,entering,iso,valve,position,cmd,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrEnteringIsoValveFb | twrEnteringIsoValveXXXXFb | Tower Entering Isolation Valve Feedback | Tower Entering Isolation Valve XX Feedback |  | twrEnteringIsoValve(\d{0,4})Fb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | condensed,water,entering,iso,valve,position,sensor,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrEnteringIsoValveOvr | twrEnteringIsoValveXXXXOvr | Tower Entering Isolation Valve Override | Tower Entering Isolation Valve XX Override |  | twrEnteringIsoValve(\d{0,4})Ovr | No | No | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | condensed,water,entering,iso,valve,position,ovr,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrEnteringPressure | twrEnteringPressure | Tower Entering Pressure | Tower Entering Pressure |  | twrEnteringPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | condensed,water,entering,pressure,sensor,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrEnteringPressureDb | twrEnteringPressureXXXXDb | Tower Entering Pressure Deadband | Tower Entering Pressure XX Deadband |  | twrEnteringPressure(\d{0,4})Db | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | condensed,water,entering,pressure,deadband,sp,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrEnteringPressureHiSp | twrEnteringPressureXXXXHiSp | Tower Entering Pressure High Setpoint | Tower Entering Pressure XX High Setpoint |  | twrEnteringPressure(\d{0,4})HiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | condensed,water,entering,pressure,high,sp,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrEnteringPressureLoSp | twrEnteringPressureXXXXLoSp | Tower Entering Pressure Low Setpoint | Tower Entering Pressure XX Low Setpoint |  | twrEnteringPressure(\d{0,4})LoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | condensed,water,entering,pressure,low,sp,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrEnteringPressureMaxSp | twrEnteringPressureXXXXMaxSp | Tower Entering Pressure Max Reset Setpoint | Tower Entering Pressure XX Max Reset Setpoint |  | twrEnteringPressure(\d{0,4})MaxSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | condensed,water,entering,pressure,max,sp,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrEnteringPressureMinSp | twrEnteringPressureXXXXMinSp | Tower Entering Pressure Min Reset Setpoint | Tower Entering Pressure XX Min Reset Setpoint |  | twrEnteringPressure(\d{0,4})MinSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | condensed,water,entering,pressure,min,sp,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrEnteringPressureSp | twrEnteringPressureSp | Tower Entering Pressure Setpoint | Tower Entering Pressure Setpoint |  | twrEnteringPressureSp | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | condensed,water,entering,pressure,effective,sp,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrEnteringTemp | twrEnteringTemp | Tower Entering Temperature | Tower Entering Temperature |  | twrEnteringTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | condensed,water,entering,temp,sensor,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrFanAlarm | twrFanXXXXAlarm | Tower Fan Alarm | Tower Fan XX Alarm |  | twrFan(\w{0,4}(?=[A-Z]¦$))Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | tower,air,fan,alarm,common | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrFanAlarmReset | twrFanXXXXAlarmReset | Tower Fan Alarm Reset | Tower Fan XX Alarm Reset |  | twrFan(\w{0,4}(?=[A-Z]¦$))AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | tower,air,fan,alarm,reset | TWR | 2.14,2.15 (Released),2.16 (Pre-Release)
twrFan | twrFanXXXX | Tower Fan Command | Tower Fan XX Command |  | twrFan((?:(?!Lead)(?!Ovr)\w){0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | tower,air,fan,status,cmd | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrFanCurrent | twrFanXXXXCurrent | Tower Fan Current | Tower Fan XX Current |  | twrFan(\w{0,4}(?=[A-Z]¦$))Current | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | tower,air,fan,current,sensor | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrFanDirection | twrFanXXXXDirection | Tower Fan Direction | Tower Fan XX Direction |  | twrFan(\w{0,4}(?=[A-Z]¦$))Direction | Yes | Yes | No | Bool | Forward/Reverse | Forward/Reverse | [6 empty] | tower,air,fan,direction,cmd | TWR | 2.15 (Released),2.16 (Pre-Release)
twrFanDirectionOvr | twrFanXXXXDirectionOvr | Tower Fan Direction Override | Tower Fan XX Direction Override |  | twrFan(\w{0,4}(?=[A-Z]¦$))DirectionOvr | Yes | Yes | No | Bool | Forward/Reverse | Forward/Reverse | [6 empty] | tower,air,fan,direction,ovr | TWR | 2.15 (Released),2.16 (Pre-Release)
twrFanDirectionStatus | twrFanXXXXDirectionStatus | Tower Fan Direction Status | Tower Fan XX Direction Status |  | twrFan(\w{0,4}(?=[A-Z]¦$))DirectionStatus | Yes | Yes | No | Bool | Forward/Reverse | Forward/Reverse | [6 empty] | tower,air,fan,direction,sensor | TWR | 2.15 (Released),2.16 (Pre-Release)
twrFanEnteringPressure | twrFanXXXXEnteringPressure | Tower Fan Entering Pressure | Tower Fan XX Entering Pressure |  | twrFan(\w{0,4}(?=[A-Z]¦$))EnteringPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | tower,air,fan,entering,pressure,sensor | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrFanFault | twrFanXXXXFault | Tower Fan Fault | Tower Fan XX Fault |  | twrFan(\w{0,4}(?=[A-Z]¦$))Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | tower,air,fan,fault | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrFanLead | twrFanXXXXLead | Tower Fan Lead | Tower Fan XX Lead |  | twrFan(\w{0,4}(?=[A-Z]¦$))Lead | Yes | Yes | No | Bool | Lead 1/Lead 2 | Lead 1/Lead 2 | [6 empty] | tower,air,fan,lead,sp | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrFanLeadXor | twrFanLeadXor | Tower Fan Lead Change Over | Tower Fan Lead Change Over |  | twrFanLeadXor | No | No | No | Bool | On/Off | On/Off | [6 empty] | tower,air,fan,lead,changeOver,cmd | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrFanLeadXorRuntimeSp | twrFanLeadXorRuntimeSp | Tower Fan Lead Change Over Runtime Setpoint | Tower Fan Lead Change Over Runtime Setpoint |  | twrFanLeadXorRuntimeSp | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrFanLeavingPressure | twrFanXXXXLeavingPressure | Tower Fan Leaving Pressure | Tower Fan XX Leaving Pressure |  | twrFan(\w{0,4}(?=[A-Z]¦$))LeavingPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | tower,air,fan,leaving,pressure,sensor | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrFanMaintSwitch | twrFanXXXXMaintSwitch | Tower Fan Maintenance Switch | Tower Fan XX Maintenance Switch |  | twrFan(\w{0,4}(?=[A-Z]¦$))MaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | tower,air,fan,maintenance,switch,cmd | TWR | 2.15 (Released),2.16 (Pre-Release)
twrFanOvr | twrFanXXXXOvr | Tower Fan Override | Tower Fan XX Override |  | twrFan(\w{0,4}(?=[A-Z]¦$))Ovr | No | No | No | Bool | On/Off | On/Off | [6 empty] | tower,air,fan,status,ovr | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrFanPressureDelta | twrFanXXXXPressureDelta | Tower Fan Pressure Delta | Tower Fan XX Pressure Delta |  | twrFan(\w{0,4}(?=[A-Z]¦$))PressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | tower,air,fan,common,pressure,delta,sensor | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrFanPressureHiAlarm | twrFanXXXXPressureHiAlarm | Tower Fan Pressure High Alarm | Tower Fan XX Pressure High Alarm |  | twrFan(\w{0,4}(?=[A-Z]¦$))PressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | tower,air,fan,pressure,high,alarm | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrFanPressureHiSp | twrFanXXXXPressureHiSp | Tower Fan Pressure High Setpoint | Tower Fan XX Pressure High Setpoint |  | twrFan(\w{0,4}(?=[A-Z]¦$))PressureHiSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | tower,air,fan,pressure,high,sp | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrFanPressureLoAlarm | twrFanXXXXPressureLoAlarm | Tower Fan Pressure Low Alarm | Tower Fan XX Pressure Low Alarm |  | twrFan(\w{0,4}(?=[A-Z]¦$))PressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | tower,air,fan,pressure,low,alarm | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrFanPressureLoSp | twrFanXXXXPressureLoSp | Tower Fan Pressure Low Setpoint | Tower Fan XX Pressure Low Setpoint |  | twrFan(\w{0,4}(?=[A-Z]¦$))PressureLoSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | tower,air,fan,pressure,low,sp | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrFanRuntime | twrFanXXXXRuntime | Tower Fan Runtime | Tower Fan XX Runtime |  | twrFan(\w{0,4}(?=[A-Z]¦$))Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | TWR | 2.15 (Released),2.16 (Pre-Release)
twrFanSpeed | twrFanXXXXSpeed | Tower Fan Speed | Tower Fan XX Speed |  | twrFan(\w{0,4}(?=[A-Z]¦$))Speed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | tower,air,fan,speed,cmd | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrFanSpeedFb | twrFanXXXXSpeedFb | Tower Fan Speed Feedback | Tower Fan XX Speed Feedback |  | twrFan(\w{0,4}(?=[A-Z]¦$))SpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | tower,air,fan,speed,sensor | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrFanSpeedMaxSp | twrFanXXXXSpeedMaxSp | Tower Fan Speed Max Setpoint | Tower Fan XX Speed Max Setpoint |  | twrFan(\w{0,4}(?=[A-Z]¦$))SpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | tower,air,fan,speed,max,sp | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrFanSpeedMinSp | twrFanXXXXSpeedMinSp | Tower Fan Speed Min Setpoint | Tower Fan XX Speed Min Setpoint |  | twrFan(\w{0,4}(?=[A-Z]¦$))SpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | tower,air,fan,speed,min,sp | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrFanSpeedOvr | twrFanXXXXSpeedOvr | Tower Fan Speed Override | Tower Fan XX Speed Override |  | twrFan(\w{0,4}(?=[A-Z]¦$))SpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | tower,air,fan,speed,ovr | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrFanSpeedSp | twrFanXXXXSpeedSp | Tower Fan Speed Setpoint | Tower Fan XX Speed Setpoint |  | twrFan(\w{0,4}(?=[A-Z]¦$))SpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | tower,air,fan,speed,effective,sp | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrFanSpeedStage | twrFanXXXXSpeedStage | Tower Fan Speed Stage Command | Tower Fan XX Speed Stage Command |  | twrFan(\w{0,4}(?=[A-Z]¦$))SpeedStage | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | tower,air,fan,speed,stage | TWR | 2.15 (Released),2.16 (Pre-Release)
twrFanStageSp | twrFanXXXXStageYYYYSp | Tower Fan Stage Setpoint | Tower Fan XX Stage YY Setpoint |  | twrFan(\w{0,4}(?=[A-Z]¦$))Stage(\d{0,4})Sp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 | YY |  | tower,air,fan,sp | TWR | 2.15 (Released),2.16 (Pre-Release)
twrFanStatus | twrFanXXXXStatus | Tower Fan Status | Tower Fan XX Status |  | twrFan(\w{0,4}(?=[A-Z]¦$))Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | tower,air,fan,status,sensor | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrFillFlow | twrFillFlow | Tower Fill Flow | Tower Fill Flow |  | twrFillFlow | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | tower,water,fill,flow,sensor | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrFillValve | twrFillValve | Tower Fill Valve Command | Tower Fill Valve Command |  | twrFillValve | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | condensed,water,fill,valve,position,cmd,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrFillValveFb | twrFillValveFb | Tower Fill Valve Feedback | Tower Fill Valve Feedback |  | twrFillValveFb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | condensed,water,fill,valve,position,sensor,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrFillVolume | twrFillVolume | Tower Fill Volume | Tower Fill Volume |  | twrFillVolume | Yes | Yes | No | Number |  |  | gallon | liter | 0 | 0 |  |  | tower,water,fill,volume,sensor | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrFlowDelta | twrFlowDelta | Tower Flow Differential | Tower Flow Differential |  | twrFlowDelta | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | condensed,water,delta,flow,sensor,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrLagReq | twrLagReq | Tower Lag Request | Tower Lag Request |  | twrLagReq | No | No | No | Bool | Request/No Request | Request/No Request | [6 empty] | tower,common,lag,request,cmd | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrLead | twrLead | Tower Lead | Tower Lead |  | twrLead | Yes | Yes | No | Bool | Lead 1/Lead 2 | Lead 1/Lead 2 | [6 empty] | tower,common,lead,sp | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrLeadXor | twrLeadXor | Tower Lead Change Over | Tower Lead Change Over |  | twrLeadXor | No | No | No | Bool | On/Off | On/Off | [6 empty] | tower,common,lead,changeOver,cmd | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrLeadXorRuntimeSp | twrLeadXorRuntimeSp | Tower Lead Change Over Runtime Setpoint | Tower Lead Change Over Runtime Setpoint |  | twrLeadXorRuntimeSp | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrLeavingIsoValve | twrLeavingIsoValveXXXX | Tower Leaving Isolation Valve Command | Tower Leaving Isolation Valve XX Command |  | twrLeavingIsoValve(\d{0,4}) | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | condensed,water,leaving,iso,valve,position,cmd,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrLeavingIsoValveFb | twrLeavingIsoValveXXXXFb | Tower Leaving Isolation Valve Feedback | Tower Leaving Isolation Valve XX Feedback |  | twrLeavingIsoValve(\d{0,4})Fb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | condensed,water,leaving,iso,valve,position,sensor,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrLeavingIsoValveOvr | twrLeavingIsoValveXXXXOvr | Tower Leaving Isolation Valve Override | Tower Leaving Isolation Valve XX Override |  | twrLeavingIsoValve(\d{0,4})Ovr | No | No | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | condensed,water,leaving,iso,valve,position,ovr,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrLeavingPressure | twrLeavingPressure | Tower Leaving Pressure | Tower Leaving Pressure |  | twrLeavingPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | condensed,water,leaving,pressure,sensor,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrLeavingTemp | twrLeavingTemp | Tower Leaving Temperature | Tower Leaving Temperature |  | twrLeavingTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | condensed,water,leaving,temp,sensor,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrLeavingTempDb | twrLeavingTempDb | Tower Leaving Temperature Deadband | Tower Leaving Temperature Deadband |  | twrLeavingTempDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | condensed,water,leaving,temp,deadband,sp,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrLeavingTempHiAlarm | twrLeavingTempHiAlarm | Tower Leaving Temperature High Alarm | Tower Leaving Temperature High Alarm |  | twrLeavingTempHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | condensed,water,leaving,temp,high,alarm,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrLeavingTempHiSp | twrLeavingTempHiSp | Tower Leaving Temperature High Setpoint | Tower Leaving Temperature High Setpoint |  | twrLeavingTempHiSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | condensed,water,leaving,temp,high,sp,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrLeavingTempLoAlarm | twrLeavingTempLoAlarm | Tower Leaving Temperature Low Alarm | Tower Leaving Temperature Low Alarm |  | twrLeavingTempLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | condensed,water,leaving,temp,low,alarm,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrLeavingTempLoSp | twrLeavingTempLoSp | Tower Leaving Temperature Low Setpoint | Tower Leaving Temperature Low Setpoint |  | twrLeavingTempLoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | condensed,water,leaving,temp,low,sp,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrLeavingTempMaxSp | twrLeavingTempMaxSp | Tower Leaving Temperature Max Reset Setpoint | Tower Leaving Temperature Max Reset Setpoint |  | twrLeavingTempMaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | condensed,water,leaving,temp,max,sp,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrLeavingTempMinSp | twrLeavingTempMinSp | Tower Leaving Temperature Min Reset Setpoint | Tower Leaving Temperature Min Reset Setpoint |  | twrLeavingTempMinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | condensed,water,leaving,temp,min,sp,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrLeavingTempSp | twrLeavingTempSp | Tower Leaving Temperature Setpoint | Tower Leaving Temperature Setpoint |  | twrLeavingTempSp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | condensed,water,leaving,temp,effective,sp,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrLoad | twrLoad | Tower Load | Tower Load |  | twrLoad | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | tower,load,sensor | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrPressureDelta | twrPressureDelta | Tower Pressure Differential | Tower Pressure Differential |  | twrPressureDelta | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | condensed,water,delta,pressure,sensor,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrPumpAlarm | twrPumpXXXXAlarm | Tower Pump Alarm | Tower Pump XX Alarm |  | twrPump(\w{0,4}(?=[A-Z]¦$))Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | tower,water,pump,common,alarm | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrPumpAlarmReset | twrPumpXXXXAlarmReset | Tower Pump Alarm Reset | Tower Pump XX Alarm Reset |  | twrPump(\w{0,4}(?=[A-Z]¦$))AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | tower,water,pump,reset,alarm | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrPump | twrPumpXXXX | Tower Pump Command | Tower Pump XX Command |  | twrPump((?:(?!Lead)(?!Ovr)\w){0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | tower,water,pump,status,cmd | TWR | 2.15 (Released),2.16 (Pre-Release)
twrPumpCurrent | twrPumpXXXXCurrent | Tower Pump Current | Tower Pump XX Current |  | twrPump(\w{0,4}(?=[A-Z]¦$))Current | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | tower,water,pump,current,sensor | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrPumpEnable | twrPumpXXXXEnable | Tower Pump Enable Command | Tower Pump XX Enable Command |  | twrPump(\w{0,4}(?=[A-Z]¦$))Enable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | tower,water,pump,enable,cmd | TWR | 2.15 (Released),2.16 (Pre-Release)
twrPumpEnableDb | twrPumpXXXXEnableDb | Tower Pump Enable Deadband | Tower Pump XX Enable Deadband |  | twrPump(\w{0,4}(?=[A-Z]¦$))EnableDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | tower,water,pump,enable,deadband,sp | TWR | 2.15 (Released),2.16 (Pre-Release)
twrPumpEnableSp | twrPumpXXXXEnableSp | Tower Pump Enable Setpoint | Tower Pump XX Enable Setpoint |  | twrPump((?:(?!Lag)\w){0,4}(?=[A-Z]¦$))EnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | tower,water,pump,enable,effective,sp | TWR | 2.15 (Released),2.16 (Pre-Release)
twrPumpEnteringPressure | twrPumpXXXXEnteringPressure | Tower Pump Entering Pressure | Tower Pump XX Entering Pressure |  | twrPump(\w{0,4}(?=[A-Z]¦$))EnteringPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | tower,water,pump,entering,pressure,sensor | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrPumpFault | twrPumpXXXXFault | Tower Pump Fault | Tower Pump XX Fault |  | twrPump(\w{0,4}(?=[A-Z]¦$))Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | tower,water,pump,fault,common | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrPumpLagDisableSp | twrPumpXXXXLagDisableSp | Tower Pump Lag Disable Setpoint | Tower Pump XX Lag Disable Setpoint |  | twrPump(\w{0,4}(?=[A-Z]¦$))LagDisableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | tower,water,pump,lag,disable,sp | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrPumpLagEnableSp | twrPumpXXXXLagEnableSp | Tower Pump Lag Enable Setpoint | Tower Pump XX Lag Enable Setpoint |  | twrPump(\w{0,4}(?=[A-Z]¦$))LagEnableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | tower,water,pump,lag,enable,sp | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrPumpLagReq | twrPumpXXXXLagReq | Tower Pump Lag Request | Tower Pump XX Lag Request |  | twrPump(\w{0,4}(?=[A-Z]¦$))LagReq | No | No | No | Bool | Request/No Request | Request/No Request | [6 empty] | tower,water,pump,lag,request,cmd | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrPumpLead | twrPumpLead | Tower Pump Lead | Tower Pump Lead |  | twrPumpLead | Yes | Yes | No | Bool | Lead 1/Lead 2 | Lead 1/Lead 2 | [6 empty] | tower,water,pump,lead,sp | TWR | 2.15 (Released),2.16 (Pre-Release)
twrPumpLeadXor | twrPumpLeadXor | Tower Pump Lead Change Over | Tower Pump Lead Change Over |  | twrPumpLeadXor | No | No | No | Bool | On/Off | On/Off | [6 empty] | tower,water,pump,lead,changeOver,cmd | TWR | 2.15 (Released),2.16 (Pre-Release)
twrPumpLeadXorRuntimeSp | twrPumpLeadXorRuntimeSp | Tower Pump Lead Change Over Runtime Setpoint | Tower Pump Lead Change Over Runtime Setpoint |  | twrPumpLeadXorRuntimeSp | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | TWR | 2.15 (Released),2.16 (Pre-Release)
twrPumpLeavingPressure | twrPumpXXXXLeavingPressure | Tower Pump Leaving Pressure | Tower Pump XX Leaving Pressure |  | twrPump(\w{0,4}(?=[A-Z]¦$))LeavingPressure | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | tower,water,pump,leaving,pressure,sensor | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrPumpMaintSwitch | twrPumpXXXXMaintSwitch | Tower Pump Maintenance Switch | Tower Pump XX Maintenance Switch |  | twrPump(\w{0,4}(?=[A-Z]¦$))MaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | tower,water,pump,maintenance,switch,cmd | TWR | 2.15 (Released),2.16 (Pre-Release)
twrPumpOvr | twrPumpXXXXOvr | Tower Pump Override | Tower Pump XX Override |  | twrPump(\w{0,4}(?=[A-Z]¦$))Ovr | No | No | No | Bool | On/Off | On/Off | [6 empty] | tower,water,pump,status,ovr | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrPumpPressureDelta | twrPumpXXXXPressureDelta | Tower Pump Pressure Delta | Tower Pump XX Pressure Delta |  | twrPump(\w{0,4}(?=[A-Z]¦$))PressureDelta | Yes | Yes | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | tower,water,pump,common,pressure,delta,sensor | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrPumpPressureHiAlarm | twrPumpXXXXPressureHiAlarm | Tower Pump Pressure High Alarm | Tower Pump XX Pressure High Alarm |  | twrPump(\w{0,4}(?=[A-Z]¦$))PressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | tower,water,pump,pressure,high,alarm | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrPumpPressureHiSp | twrPumpXXXXPressureHiSp | Tower Pump Pressure High Setpoint | Tower Pump XX Pressure High Setpoint |  | twrPump(\w{0,4}(?=[A-Z]¦$))PressureHiSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | tower,water,pump,pressure,high,sp | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrPumpPressureLoAlarm | twrPumpXXXXPressureLoAlarm | Tower Pump Pressure Low Alarm | Tower Pump XX Pressure Low Alarm |  | twrPump(\w{0,4}(?=[A-Z]¦$))PressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | tower,water,pump,pressure,low,alarm | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrPumpPressureLoSp | twrPumpXXXXPressureLoSp | Tower Pump Pressure Low Setpoint | Tower Pump XX Pressure Low Setpoint |  | twrPump(\w{0,4}(?=[A-Z]¦$))PressureLoSp | No | No | No | Number |  |  | pounds_per_square_inch | kilopascal | 1 | 1 |  |  | tower,water,pump,pressure,low,sp | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrPumpRuntime | twrPumpXXXXRuntime | Tower Pump Runtime | Tower Pump XX Runtime |  | twrPump(\w{0,4}(?=[A-Z]¦$))Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | TWR | 2.15 (Released),2.16 (Pre-Release)
twrPumpSpeed | twrPumpXXXXSpeed | Tower Pump Speed | Tower Pump XX Speed |  | twrPump(\w{0,4}(?=[A-Z]¦$))Speed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | tower,water,pump,speed,cmd | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrPumpSpeedFb | twrPumpXXXXSpeedFb | Tower Pump Speed Feedback | Tower Pump XX Speed Feedback |  | twrPump(\w{0,4}(?=[A-Z]¦$))SpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | tower,water,pump,speed,sensor | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrPumpSpeedMaxSp | twrPumpXXXXSpeedMaxSp | Tower Pump Speed Max Setpoint | Tower Pump XX Speed Max Setpoint |  | twrPump(\w{0,4}(?=[A-Z]¦$))SpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | tower,water,pump,speed,max,sp | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrPumpSpeedMinSp | twrPumpXXXXSpeedMinSp | Tower Pump Speed Min Setpoint | Tower Pump XX Speed Min Setpoint |  | twrPump(\w{0,4}(?=[A-Z]¦$))SpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | tower,water,pump,speed,min,sp | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrPumpSpeedOvr | twrPumpXXXXSpeedOvr | Tower Pump Speed Override | Tower Pump XX Speed Override |  | twrPump(\w{0,4}(?=[A-Z]¦$))SpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | tower,water,pump,speed,ovr | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrPumpSpeedSp | twrPumpXXXXSpeedSp | Tower Pump Speed Setpoint | Tower Pump XX Speed Setpoint |  | twrPump(\w{0,4}(?=[A-Z]¦$))SpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | tower,water,pump,speed,effective,sp | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrPumpStatus | twrPumpXXXXStatus | Tower Pump Status | Tower Pump XX Status |  | twrPump(\w{0,4}(?=[A-Z]¦$))Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | tower,water,pump,status,sensor | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrStageOffSp | twrStageXXXXOffSp | Tower Stage Off Setpoint | Tower Stage XX Off Setpoint |  | twrStage(\d{0,4})OffSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 | XX |  | tower,stage,off,sp | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrStageOnSp | twrStageXXXXOnSp | Tower Stage On Setpoint | Tower Stage XX On Setpoint |  | twrStage(\d{0,4})OnSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 | XX |  | tower,stage,on,sp | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
twrTempDelta | twrTempDelta | Tower Temperature Differential | Tower Temperature Differential |  | twrTempDelta | Yes | Yes | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | condensed,water,delta,temp,sensor,tower | TWR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
transferFan | transferFanXXXX | Transfer Fan | Transfer Fan |  | transferFan(\w{0,4}(?=[A-Z]¦$)) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | transfer,air,fan,status,cmd | TF | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
transferFanAlarm | transferFanXXXXAlarm | Transfer Fan Alarm | Transfer Fan Alarm |  | transferFan(\w{0,4}(?=[A-Z]¦$))Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | transfer,air,fan,alarm | TF | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
transferFanHandMode | transferFanXXXXHandMode | Transfer Fan Hand Mode | Transfer Fan Hand Mode |  | transferFan(\w{0,4}(?=[A-Z]¦$))HandMode | Yes | Yes | No | Bool | Hand/Auto | Hand/Auto | [6 empty] | transfer,air,fan,handMode,sensor | TF | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
transferFanStatus | transferFanXXXXStatus | Transfer Fan Status | Transfer Fan Status |  | transferFan(\w{0,4}(?=[A-Z]¦$))Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | transfer,air,fan,status,sensor | TF | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
xfmrTemp | xfmrTemp | Transformer Temperature | Transformer Temperature |  | xfmrTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | transformer,temp,common,sensor | XFMR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
xfmrTempPhaseA | xfmrTempPhaseA | Transformer Temperature (Phase A) | Transformer Temperature (Phase A) |  | xfmrTempPhaseA | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  | A | transformer,temp,sensor | XFMR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
xfmrTempPhaseB | xfmrTempPhaseB | Transformer Temperature (Phase B) | Transformer Temperature (Phase B) |  | xfmrTempPhaseB | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  | B | transformer,temp,sensor | XFMR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
xfmrTempPhaseC | xfmrTempPhaseC | Transformer Temperature (Phase C) | Transformer Temperature (Phase C) |  | xfmrTempPhaseC | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  | C | transformer,temp,sensor | XFMR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
xfmrTempPhaseN | xfmrTempPhaseN | Transformer Temperature (Phase N) | Transformer Temperature (Phase N) |  | xfmrTempPhaseN | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  | N | transformer,temp,sensor | XFMR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
xfmrTempHiAlarm | xfmrTempHiAlarm | Transformer Temperature High Alarm | Transformer Temperature High Alarm |  | xfmrTempHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | transformer,temp,high,common,alarm | XFMR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
xfmrTempLevelAlarm | xfmrTempLevelAlarm | Transformer Temperature Level Alarm | Transformer Temperature Level Alarm |  | xfmrTempLevelAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | transformer,temp,level,common,alarm | XFMR | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
xfmrTempPhaseALevelAlarm | xfmrTempPhaseALevelAlarm | Transformer Temperature Level Alarm (Phase A) | Transformer Temperature Level Alarm (Phase A) |  | xfmrTempPhaseALevelAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [5 empty] | A | transformer,temp,level,alarm | XFMR | 2.12,2.13,2.14,2.15 (Released)
xfmrTempPhaseBLevelAlarm | xfmrTempPhaseBLevelAlarm | Transformer Temperature Level Alarm (Phase B) | Transformer Temperature Level Alarm (Phase B) |  | xfmrTempPhaseBLevelAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [5 empty] | B | transformer,temp,level,alarm | XFMR | 2.12,2.13,2.14,2.15 (Released)
xfmrTempPhaseCLevelAlarm | xfmrTempPhaseCLevelAlarm | Transformer Temperature Level Alarm (Phase C) | Transformer Temperature Level Alarm (Phase C) |  | xfmrTempPhaseCLevelAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [5 empty] | C | transformer,temp,level,alarm | XFMR | 2.12,2.13,2.14,2.15 (Released)
xfmrTempPhaseNLevelAlarm | xfmrTempPhaseNLevelAlarm | Transformer Temperature Level Alarm (Phase N) | Transformer Temperature Level Alarm (Phase N) |  | xfmrTempPhaseNLevelAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [5 empty] | N | transformer,temp,level,alarm | XFMR | 2.12,2.13,2.14,2.15 (Released)
xfmrTempLevelSp | xfmrTempLevelSp | Transformer Temperature Level Setpoint | Transformer Temperature Level Setpoint |  | xfmrTempLevelSp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | transformer,temp,level,common,sp | XFMR | 2.12,2.13,2.14,2.15 (Released)
uvFilterAlarm | uvFilterXXXXAlarm | Ultraviolet Filter Alarm | Ultraviolet Filter XX Alarm |  | uvFilter(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | ultraviolet,light,common,alarm | AHU,CRAC,CRAH,DHU,DOAS,EC,MAU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
uvFilterAlarmReset | uvFilterXXXXAlarmReset | Ultraviolet Filter Alarm Reset | Ultraviolet Filter XX Alarm Reset |  | uvFilter(\d{0,4})AlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | ultraviolet,filter,reset,alarm | AHU,CRAC,CRAH,DHU,DOAS,EC,MAU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
uvFilter | uvFilterXXXX | Ultraviolet Filter Command | Ultraviolet Filter XX Command |  | uvFilter(\d{0,4}) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | ultraviolet,light,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,EC,MAU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
uvFilterRuntime | uvFilterXXXXRuntime | Ultraviolet Filter Runtime | Ultraviolet Filter XX Runtime |  | uvFilter(\d{0,4})Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,EC,MAU,RTU | 2.15 (Released),2.16 (Pre-Release)
uvFilterStatus | uvFilterXXXXStatus | Ultraviolet Filter Status | Ultraviolet Filter XX Status |  | uvFilter(\d{0,4})Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | ultraviolet,light,status,sensor | AHU,CRAC,CRAH,DHU,DOAS,EC,MAU,RTU | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
unitAlarm | unitAlarm | Unit Alarm | Unit Alarm |  | unitAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | unitPoint,alarm,common,general | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CU,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,WTHR,ZD,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
unitAlarmJson | unitAlarmJson | Unit Alarm (JSON) | Unit Alarm (JSON) |  | unitAlarmJson | No | No | No | Str | [8 empty] | unitPoint,alarm,json | AC,AHU,ATS,ATU,BATT,BLND,BLR,BRK,BTU,CF,CLR,CM,CMP,CRAC,CRAH,CU,CUH,CWS,DAC,DCU,DCWS,DH,DHU,DHWS,DOAS,DOOR,DRY,EC,EF,ELV,ENC,ERU,FC,FCU,FDS,FEXT,FP,FPB,FSD,FSEP,FSS,GBL,GDS,GEN,GEO,GINT,GM,HDS,HP,HRU,HT,HUM,HVHS,HVLS,HWS,INV,LDS,LS,LTGE,LTGI,MAU,MSC,OF,PDU,PFC,PH,PINT,PIU,PM,PMP,PRLY,PV,PWS,REC,RECT,RF,RFG,ROS,RP,RPC,RPF,RPP,RRS,RTU,SCRB,SEC,SKYL,SM,SMEX,SMP,SMS,STS,TF,TNK,TRN,TVS,TWR,UH,UPS,UV,VAV,VBTU,VGM,VPM,VRF,VWM,WH,WM,WNDW,WS,WSS,WTHR,WTS,XFMR,ZD,ZN,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
unitAlarmMsg | unitAlarmMsg | Unit Alarm (MSG) | Unit Alarm (MSG) |  | unitAlarmMsg | Yes | No | No | Str | [8 empty] | unitPoint,alarm,msg | AC,AHU,ATS,ATU,BATT,BLND,BLR,BRK,BTU,CF,CLR,CM,CMP,CRAC,CRAH,CU,CUH,CWS,DAC,DCU,DCWS,DH,DHU,DHWS,DOAS,DOOR,DRY,EC,EF,ELV,ENC,ERU,FC,FCU,FDS,FEXT,FP,FPB,FSD,FSEP,FSS,GBL,GDS,GEN,GEO,GINT,GM,HDS,HP,HRU,HT,HUM,HVHS,HVLS,HWS,INV,LDS,LS,LTGE,LTGI,MAU,MSC,OF,PDU,PFC,PH,PINT,PIU,PM,PMP,PRLY,PV,PWS,REC,RECT,RF,RFG,ROS,RP,RPC,RPF,RPP,RRS,RTU,SCRB,SEC,SKYL,SM,SMEX,SMP,SMS,STS,TF,TNK,TRN,TVS,TWR,UH,UPS,UV,VAV,VBTU,VGM,VPM,VRF,VWM,WH,WM,WNDW,WS,WSS,WTHR,WTS,XFMR,ZD,ZN,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
unitAlarmCode | unitAlarmCode | Unit Alarm Code | Unit Alarm Code |  | unitAlarmCode | Yes | Yes | No | Str | [8 empty] | unitPoint,alarm,code | AC,AHU,ATU,BLR,BRK,CHX,CLR,CMP,CRAC,CRAH,CU,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HHX,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,WTHR,ZD,FCU,HP,ODU | 2.15 (Released)
unitAlarmReset | unitAlarmReset | Unit Alarm Reset | Unit Alarm Reset |  | unitAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | unitPoint,alarm,reset,common | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CU,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,WTHR,ZD,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
unitBypassSwitch | unitBypassSwitch | Unit Bypass Switch | Unit Bypass Switch |  | unitBypassSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | unitPoint,bypass,switch,cmd | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,ZD,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
unitControlSource | unitControlSource | Unit Control Source | Unit Control Source |  | unitControlSource | No | No | No | Str | BAS/Local | BAS/Local | [6 empty] | blacklist | CRAC,CRAH,DHU,EC,ODU | 2.15 (Released),2.16 (Pre-Release)
unitDemand | unitDemand | Unit Demand | Unit Demand |  | unitDemand | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | unitPoint,demand,sensor | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,ZD,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
unitEfficiency | unitEfficiency | Unit Efficiency | Unit Efficiency |  | unitEfficiency | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | unitPoint,efficiency,sensor | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,ZD,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
unitEnableBAS | unitEnableBAS | Unit Enable BAS | Unit Enable BAS |  | unitEnableBAS | No | No | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | unitPoint,enable,bas,cmd | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,ZD,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
unitEnable | unitEnable | Unit Enable Command | Unit Enable Command |  | unitEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | unitPoint,enable,common,cmd | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,ZD,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
unitEnableOvr | unitEnableOvr | Unit Enable Command Override | Unit Enable Command Override |  | unitEnableOvr | No | No | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | unitPoint,enable,ovr | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,ZD,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
unitEnableSp | unitEnableSp | Unit Enable Setpoint | Unit Enable Setpoint |  | unitEnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | unitPoint,enable,sp | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,ZD,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
unitFanAlarm | unitFanAlarm | Unit Fan Alarm | Unit Fan Alarm |  | unitFanAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | unitPoint,fan,alarm | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,ZD,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
unitFault | unitFault | Unit Fault | Unit Fault |  | unitFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | unitPoint,fault,common | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CU,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,WTHR,ZD,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
unitFaultCode | unitFaultCode | Unit Fault Code | Unit Fault Code |  | unitFaultCode | Yes | Yes | No | Str | [8 empty] | unitPoint,fault,code | AC,AHU,ATU,BLR,BRK,CHX,CLR,CMP,CRAC,CRAH,CU,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HHX,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,WTHR,ZD,FCU,HP,ODU | 2.15 (Released)
unitFaultReset | unitFaultReset | Unit Fault Reset | Unit Fault Reset |  | unitFaultReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | unitPoint,fault,reset | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,WTHR,ZD,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
unitFilterAlarm | unitFilterAlarm | Unit Filter Alarm | Unit Filter Alarm |  | unitFilterAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | unitPoint,filter,general,alarm | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,ZD,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
unitFilterAlarmReset | unitFilterAlarmReset | Unit Filter Alarm Reset | Unit Filter Alarm Reset |  | unitFilterAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | unitPoint,filter,reset,alarm | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,GEN,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,ZD,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
unitGroundFault | unitGroundFault | Unit Ground Fault | Unit Ground Fault |  | unitGroundFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | unitPoint,ground,fault | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,ZD,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
unitGroup | unitGroup | Unit Group | Unit Group |  | unitGroup | No | No | No | Str |  | Group 1/Group 2/Group 3/Group 4/Group 5/Group 6/Group 7/Group 8/Group 9/Group 10 | [6 empty] | unitPoint,group,sp | CF,DHU,EC,HVHS,HVLS,ODU | 2.15 (Released),2.16 (Pre-Release)
unitHandMode | unitHandMode | Unit Hand/Auto Mode | Unit Hand/Auto Mode |  | unitHandMode | Yes | Yes | No | Bool | Hand/Auto | Hand/Auto | [6 empty] | unitPoint,handMode,sensor | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,ZD,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
unitLead | unitLead | Unit Lead | Unit Lead |  | unitLead | Yes | Yes | No | Bool | Lead 1/Lead 2 | Lead 1/Lead 2 | [6 empty] | unitPoint,lead,sp | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,ZD,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
unitLeadXor | unitLeadXor | Unit Lead Change Over | Unit Lead Change Over |  | unitLeadXor | No | No | No | Bool | On/Off | On/Off | [6 empty] | unitPoint,lead,changeOver,cmd | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,ZD,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
unitLeadXorRuntimeSp | unitLeadXorRuntimeSp | Unit Lead Change Over Runtime Setpoint | Unit Lead Change Over Runtime Setpoint |  | unitLeadXorRuntimeSp | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,ZD,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
unitLevelAlarm | unitLevelXXXXAlarm | Unit Level Alarm | Unit Level XX Alarm |  | unitLevel(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | unitPoint,level,alarm | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,WTHR,ZD,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
unitLoad | unitLoad | Unit Load | Unit Load |  | unitLoad | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | unitPoint,load,sensor | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,ZD,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
unitMaintAlarm | unitMaintAlarm | Unit Maintenance Alarm | Unit Maintenance Alarm |  | unitMaintAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | unitPoint,maintenance,alarm | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,WTHR,ZD,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
unitMode | unitMode | Unit Mode | Unit Mode |  | unitMode | Yes | Yes | No | Str | On/Off | On/Off/Idle/Hand | [6 empty] | unitPoint,mode,sp | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,ZD,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
unitOscillation | unitOscillation | Unit Oscillation | Unit Oscillation |  | unitOscillation | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | unitPoint,oscillation,sensor | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,ZD,FCU,HP,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
unitOscillationOvr | unitOscillationOvr | Unit Oscillation Override | Unit Oscillation Override |  | unitOscillationOvr | No | No | No | Bool | On/Off | On/Off | [6 empty] | unitPoint,oscillation,ovr | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,ZD,FCU,HP,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
unitOverloadAlarm | unitOverloadAlarm | Unit Overload Alarm | Unit Overload Alarm |  | unitOverloadAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | unitPoint,overload,alarm | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,ZD,FCU,HP,HX | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
unitProblemCode | unitProblemCode | Unit Problem Code | Unit Problem Code |  | unitProblemCode | Yes | Yes | No | Str | [8 empty] | unitPoint,problem,code | AC,AHU,ATU,BLR,BRK,CHX,CLR,CMP,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HHX,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,WTHR,ZD,FCU,HP,ODU | 2.15 (Released)
unitRegeneration | unitRegeneration | Unit Regeneration Command | Unit Regeneration Command |  | unitRegeneration | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | unitPoint,regeneration,status,cmd | SCRB | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
unitRuntime | unitRuntime | Unit Runtime | Unit Runtime |  | unitRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,ZD,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
unitShutdown | unitShutdown | Unit Shutdown | Unit Shutdown |  | unitShutdown | Yes | Yes | No | Bool | Shutdown/Auto | Shutdown/Auto | [6 empty] | unitPoint,shutdown,sp | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,ZD,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
unitStatus | unitStatus | Unit Status | Unit Status |  | unitStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | unitPoint,status,sensor | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,WTHR,ZD,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
unitWarning | unitWarning | Unit Warning | Unit Warning |  | unitWarning | Yes | Yes | No | Bool | Warning/Normal | Warning/Normal | [6 empty] | unitPoint,warning,common | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,WTHR,ZD,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
unitWarningCode | unitWarningCode | Unit Warning Code | Unit Warning Code |  | unitWarningCode | Yes | Yes | No | Str | [8 empty] | unitPoint,warning,code | AC,AHU,ATU,BLR,BRK,CHX,CLR,CMP,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HHX,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,WTHR,ZD,FCU,HP,ODU | 2.15 (Released)
unitWarningReset | unitWarningReset | Unit Warning Reset | Unit Warning Reset |  | unitWarningReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | unitPoint,warning,reset | AC,AHU,ATU,BLR,BRK,CLR,CMP,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ELV,ERU,FCU,FPB,GEN,HP,HRU,HUM,HVHS,HVLS,INV,MAU,MSC,PFC,PIU,REC,RECT,RF,ROS,RP,RPC,RPF,RRS,RTU,SCRB,SMP,TF,TNK,TWR,UH,UPS,UV,VAV,VRF,WTHR,ZD,FCU,HP,ODU,HX | 2.15 (Released),2.16 (Pre-Release)
unoccupiedCoolSp | unoccupiedCoolSp | Unoccupied Cool Setpoint | Unoccupied Cool Setpoint |  | unoccupiedCoolSp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,temp,unoccupied,cool,sp | AHU,ATU,CRAC,CRAH,DHU,DOAS,EC,FCU,FPB,HP,HVHS,HVLS,MAU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
nightSetupMode | nightSetupMode | Unoccupied Cooling Mode | Unoccupied Cooling Mode |  | nightSetupMode | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | unoccupied,cool,mode,cmd | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
unoccupiedDehumidSp | unoccupiedDehumidSp | Unoccupied Dehumidification Setpoint | Unoccupied Dehumidification Setpoint |  | unoccupiedDehumidSp | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | zone,air,dehumid,unoccupied,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
unoccupiedDimLevelSp | unoccupiedDimLevelSp | Unoccupied Dimming Level Setpoint | Unoccupied Dimming Level Setpoint |  | unoccupiedDimLevelSp | No | No | No | Number |  |  | footcandle | lux | 0 | 0 |  |  | unoccupied,dimming,lightLevel,sp | CRAC,CRAH,DHU,DOAS,EC,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
unoccupiedHeatSp | unoccupiedHeatSp | Unoccupied Heat Setpoint | Unoccupied Heat Setpoint |  | unoccupiedHeatSp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,temp,unoccupied,heat,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,HVHS,HVLS,MAU,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
nightSetbackMode | nightSetbackMode | Unoccupied Heating Mode | Unoccupied Heating Mode |  | nightSetbackMode | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | unoccupied,heat,mode,cmd | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
unoccupiedHumidSp | unoccupiedHumidSp | Unoccupied Humidification Setpoint | Unoccupied Humidification Setpoint |  | unoccupiedHumidSp | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | zone,air,humid,unoccupied,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
unoccupiedTempDb | unoccupiedTempDb | Unoccupied Temperature Deadband | Unoccupied Temperature Deadband |  | unoccupiedTempDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | zone,air,temp,unoccupied,deadband,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,EF,FCU,FPB,HP,HVHS,HVLS,MAU,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
unoccupiedTempSp | unoccupiedTempSp | Unoccupied Temperature Setpoint | Unoccupied Temperature Setpoint |  | unoccupiedTempSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,temp,unoccupied,effective,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,EF,FCU,FPB,HP,HVHS,HVLS,MAU,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
ventilationMode | ventilationMode | Ventilation Mode Command | Ventilation Mode Command |  | ventilationMode | Yes | Yes | No | Bool | Ventilating/Not Ventilating | Ventilating/Not Ventilating | [6 empty] | ventilation,mode,sp | FPB,VAV,ZD | 2.14,2.15 (Released),2.16 (Pre-Release)
vibrationAlarm | vibrationAlarm | Vibration Alarm | Vibration Alarm |  | vibrationAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | vibration,alarm | MSC | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
vibrationLevel | vibrationLevel | Vibration Level | Vibration Level XX |  | vibrationLevel | Yes | Yes | No | Number |  |  | meters_per_second_squared | meters_per_second_squared | 1 | 1 |  |  | vibration,sensor | MSC,TWR,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
voltageHiAlarm | voltageHiAlarm | Voltage High Alarm | Voltage High Alarm |  | voltageHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | common,volt,high,alarm | ATS,BRK,INV,PFC,PM,PRLY,PV,RECT,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
voltageImbalance | voltageImbalance | Voltage Imbalance | Voltage Imbalance |  | voltageImbalance | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | common,volt,imbalance,sensor | PRLY | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
voltageLL | voltageLL | Voltage Line to Line (Average) | Voltage Line to Line (Average) |  | voltageLL | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  | LL | common,volt,sensor | ATS,BRK,CU,INV,PFC,PM,PRLY,PV,RECT,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
voltagePhaseAB | voltagePhaseAB | Voltage Line to Line (Phase AB) | Voltage Line to Line (Phase AB) |  | voltagePhaseAB | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  | AB | common,volt,sensor | ATS,BRK,CU,INV,PFC,PM,PRLY,PV,RECT,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
voltagePhaseBC | voltagePhaseBC | Voltage Line to Line (Phase BC) | Voltage Line to Line (Phase BC) |  | voltagePhaseBC | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  | BC | common,volt,sensor | ATS,BRK,CU,INV,PFC,PM,PRLY,PV,RECT,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
voltagePhaseCA | voltagePhaseCA | Voltage Line to Line (Phase CA) | Voltage Line to Line (Phase CA) |  | voltagePhaseCA | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  | CA | common,volt,sensor | ATS,BRK,CU,INV,PFC,PM,PRLY,PV,RECT,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
voltageLN | voltageLN | Voltage Line to Neutral (Average) | Voltage Line to Neutral (Average) |  | voltageLN | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  | N | common,volt,sensor | ATS,BRK,CU,INV,PFC,PM,PRLY,PV,RECT,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
voltagePhaseAN | voltagePhaseAN | Voltage Line to Neutral (Phase A) | Voltage Line to Neutral (Phase A) |  | voltagePhaseAN | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  | A | common,volt,sensor | ATS,BRK,CU,INV,PFC,PM,PRLY,PV,RECT,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
voltagePhaseBN | voltagePhaseBN | Voltage Line to Neutral (Phase B) | Voltage Line to Neutral (Phase B) |  | voltagePhaseBN | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  | B | common,volt,sensor | ATS,BRK,CU,INV,PFC,PM,PRLY,PV,RECT,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
voltagePhaseCN | voltagePhaseCN | Voltage Line to Neutral (Phase C) | Voltage Line to Neutral (Phase C) |  | voltagePhaseCN | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  | C | common,volt,sensor | ATS,BRK,CU,INV,PFC,PM,PRLY,PV,RECT,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
voltageLoAlarm | voltageLoAlarm | Voltage Low Alarm | Voltage Low Alarm |  | voltageLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | common,volt,low,alarm | ATS,BRK,INV,PFC,PM,PRLY,PV,RECT,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
voltageSeqNeg | voltageSeqNeg | Voltage Sequence Negative | Voltage Sequence Negative |  | voltageSeqNeg | Yes | Yes | No | Number |  |  | volt | volt | 1 | 1 |  |  | common,volt,seqNeg,sensor | PRLY | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
voltageToleranceAlarm | voltageToleranceAlarm | Voltage Tolerance Alarm | Voltage Tolerance Alarm |  | voltageToleranceAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | common,volt,tolerance,alarm | ATS,BRK,GEN,INV,PDU,PFC,PM,PRLY,PV,RECT,RP,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
voltageTHDAlarm | voltageTHDAlarm | Voltage Total Harmonic Distortion Alarm | Voltage Total Harmonic Distortion Alarm |  | voltageTHDAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | common,volt,thd,alarm | ATS,BRK,GEN,INV,PDU,PFC,PM,PRLY,PV,RECT,RP,STS,TVS,UPS,VPM | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterCoilEnteringTemp | waterCoilEnteringTemp | Water Coil Entering Temperature | Water Coil Entering Temperature |  | waterCoilEnteringTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | water,coil,general,entering,temp,sensor | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterConductivity | waterConductivity | Water Conductivity | Water Conductivity |  | waterConductivity | Yes | Yes | No | Number |  |  | siemens_per_meter | siemens_per_meter | 1 | 1 |  |  | water,conductivity,sensor | BLR,CWS,DHWS,HWS,WH,WS,WSS,WTS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterConductivityAlarm | waterConductivityAlarm | Water Conductivity Alarm | Water Conductivity Alarm |  | waterConductivityAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | water,conductivity,alarm | BLR,CWS,DHWS,HWS,WH,WS,WSS,WTS | 2.15 (Released),2.16 (Pre-Release)
waterDetectAlarm | waterDetectAlarm | Water Detection Alarm | Water Detection Alarm |  | waterDetectAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | common,water,detect,alarm | CRAC,CRAH,LDS,PWS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterEnteringFlow | waterEnteringFlowXXXX | Water Entering Flow | Water Entering Flow XX |  | waterEnteringFlow(\d{0,4}) | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | common,water,entering,flow,general,sensor | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterEnteringFlowStatus | waterEnteringFlowXXXXStatus | Water Entering Flow Status | Water Entering Flow XX Status |  | waterEnteringFlow(\d{0,4})Status | Yes | Yes | No | Bool | Flow/No Flow | Flow/No Flow | [6 empty] | common,water,entering,flow,status,sensor | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterEnteringIsoValve | waterEnteringIsoValveXXXX | Water Entering Isolation Valve | Water Entering Isolation Valve XX |  | waterEnteringIsoValve(\d{0,4}) | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | common,water,entering,iso,valve,cmd | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterEnteringIsoValveFb | waterEnteringIsoValveXXXXFb | Water Entering Isolation Valve Feedback | Water Entering Isolation Valve XX Feedback |  | waterEnteringIsoValve(\d{0,4})Fb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | common,water,entering,iso,valve,sensor | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterEnteringTemp | waterEnteringTempXXXX | Water Entering Temperature | Water Entering Temperature XX |  | waterEnteringTemp(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,water,entering,temp,sensor | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterEnteringTempHiAlarm | waterEnteringTempXXXXHiAlarm | Water Entering Temperature High Alarm | Water Entering Temperature XX High Alarm |  | waterEnteringTemp(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | common,water,entering,temp,high,alarm | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterEnteringTempLoAlarm | waterEnteringTempXXXXLoAlarm | Water Entering Temperature Low Alarm | Water Entering Temperature XX Low Alarm |  | waterEnteringTemp(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | common,water,entering,temp,low,alarm | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS | 2.15 (Released),2.16 (Pre-Release)
waterHeaterAlarm | waterHeaterAlarm | Water Heater Alarm | Water Heater Alarm |  | waterHeaterAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | waterHeater,common,alarm | WH | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterHeater | waterHeater | Water Heater Command | Water Heater Command |  | waterHeater | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | waterHeater,status,cmd | WH | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterHeaterStatus | waterHeaterStatus | Water Heater Status | Water Heater Status |  | waterHeaterStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | waterHeater,status,sensor | WH | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterLeakAlarm | waterLeakAlarm | Water Leak Alarm | Water Leak Alarm |  | waterLeakAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | common,water,leak,alarm | BLR,BTU,CM,DCWS,DHWS,LDS,PWS,ROS,VBTU,WH,WSS,WTS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterLeakDelta | waterLeakDelta | Water Leak Delta | Water Leak Delta |  | waterLeakDelta | Yes | Yes | No | Number |  |  | gallon | liter | 0 | 0 |  |  | common,water,leak,delta,sensor | BLR,BTU,CM,DCWS,DHWS,LDS,PWS,ROS,VBTU,WH,WSS,WTS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterLeakDeltaHiSp | waterLeakDeltaHiSp | Water Leak Delta High Setpoint | Water Leak Delta High Setpoint |  | waterLeakDeltaHiSp | No | No | No | Number |  |  | gallon | liter | 0 | 0 |  |  | common,water,leak,delta,high,sp | BLR,BTU,CM,DCWS,DHWS,LDS,PWS,ROS,VBTU,WH,WSS,WTS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterLeakDistance | waterLeakDistance | Water Leak Distance | Water Leak Distance |  | waterLeakDistance | Yes | Yes | No | Number |  |  | foot | meter | 1 | 1 |  |  | common,water,leak,distance,sensor | BLR,BTU,CM,DCWS,DHWS,LDS,PWS,ROS,VBTU,WH,WSS,WTS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterLeavingFlow | waterLeavingFlowXXXX | Water Leaving Flow | Water Leaving Flow XX |  | waterLeavingFlow(\d{0,4}) | Yes | Yes | No | Number |  |  | gallons_per_minute | liters_per_minute | 1 | 1 |  |  | common,water,leaving,flow,general,sensor | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS,WTS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterLeavingFlowStatus | waterLeavingFlowXXXXStatus | Water Leaving Flow Status | Water Leaving Flow XX Status |  | waterLeavingFlow(\d{0,4})Status | Yes | Yes | No | Bool | Flow/No Flow | Flow/No Flow | [6 empty] | common,water,leaving,flow,status,sensor | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS,WTS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterLeavingIsoValve | waterLeavingIsoValveXXXX | Water Leaving Isolation Valve | Water Leaving Isolation Valve XX |  | waterLeavingIsoValve(\d{0,4}) | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | common,water,leaving,iso,valve,cmd | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS,WTS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterLeavingIsoValveFb | waterLeavingIsoValveXXXXFb | Water Leaving Isolation Valve Feedback | Water Leaving Isolation Valve XX Feedback |  | waterLeavingIsoValve(\d{0,4})Fb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | common,water,leaving,iso,valve,sensor | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS,WTS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterLeavingPressureHiAlarm | waterLeavingPressureXXXXHiAlarm | Water Leaving Pressure High Alarm | Water Leaving Pressure XX High Alarm |  | waterLeavingPressure(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | common,water,leaving,pressure,high,alarm | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS,WTS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterLeavingPressureLoAlarm | waterLeavingPressureXXXXLoAlarm | Water Leaving Pressure Low Alarm | Water Leaving Pressure XX Low Alarm |  | waterLeavingPressure(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | common,water,leaving,pressure,low,alarm | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS,WTS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterLeavingTemp | waterLeavingTempXXXX | Water Leaving Temperature | Water Leaving Temperature XX |  | waterLeavingTemp(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,water,leaving,temp,sensor | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS,WTS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterLeavingTempDb | waterLeavingTempXXXXDb | Water Leaving Temperature Deadband | Water Leaving Temperature XX Deadband |  | waterLeavingTemp(\d{0,4})Db | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | common,water,leaving,temp,deadband,sp | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS,WTS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterLeavingTempHiAlarm | waterLeavingTempXXXXHiAlarm | Water Leaving Temperature High Alarm | Water Leaving Temperature XX High Alarm |  | waterLeavingTemp(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | common,water,leaving,temp,high,alarm | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS,WTS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterLeavingTempHiSp | waterLeavingTempXXXXHiSp | Water Leaving Temperature High Setpoint | Water Leaving Temperature XX High Setpoint |  | waterLeavingTemp(\d{0,4})HiSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,water,leaving,temp,high,sp | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS,WTS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterLeavingTempLoAlarm | waterLeavingTempXXXXLoAlarm | Water Leaving Temperature Low Alarm | Water Leaving Temperature XX Low Alarm |  | waterLeavingTemp(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | common,water,leaving,temp,low,alarm | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS,WTS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterLeavingTempLoSp | waterLeavingTempXXXXLoSp | Water Leaving Temperature Low Setpoint | Water Leaving Temperature XX Low Setpoint |  | waterLeavingTemp(\d{0,4})LoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,water,leaving,temp,low,sp | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS,WTS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterLeavingTempMaxSp | waterLeavingTempXXXXMaxSp | Water Leaving Temperature Max Setpoint | Water Leaving Temperature XX Max Setpoint |  | waterLeavingTemp(\d{0,4})MaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,water,leaving,temp,max,sp | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS,WTS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterLeavingTempMinSp | waterLeavingTempXXXXMinSp | Water Leaving Temperature Min Setpoint | Water Leaving Temperature XX Min Setpoint |  | waterLeavingTemp(\d{0,4})MinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,water,leaving,temp,min,sp | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS,WTS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterLeavingTempSp | waterLeavingTempXXXXSp | Water Leaving Temperature Setpoint | Water Leaving Temperature XX Setpoint |  | waterLeavingTemp(\d{0,4})Sp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,water,leaving,temp,effective,sp | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS,WTS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterLeavingTempSpOffset | waterLeavingTempXXXXSpOffset | Water Leaving Temperature Setpoint Offset | Water Leaving Temperature XX Setpoint Offset |  | waterLeavingTemp(\d{0,4})SpOffset | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | common,water,leaving,temp,offset,sp | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS,WTS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterLevelHiAlarm | waterLevelHiAlarm | Water Level High Alarm | Water Level High Alarm |  | waterLevelHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | common,water,level,high,alarm | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS,WTS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterLevelLoAlarm | waterLevelLoAlarm | Water Level Low Alarm | Water Level Low Alarm |  | waterLevelLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | common,water,level,low,alarm | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS,WTS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterORP | waterORP | Water Oxidation Reduction Potential | Water Oxidation Reduction Potential |  | waterORP | Yes | Yes | No | Number |  |  | millivolt | millivolt | 1 | 1 |  |  | water,orp,sensor | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS,WTS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterTempDelta | waterTempDelta | Water Temperature Delta | Water Temperature Delta |  | waterTempDelta | Yes | Yes | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | common,water,delta,temp,sensor | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS,WTS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterTempDeltaAlarm | waterTempDeltaAlarm | Water Temperature Delta Alarm | Water Temperature Delta Alarm |  | waterTempDeltaAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | common,water,delta,temp,alarm | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS,WTS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterTOC | waterTOC | Water Total Organic Compounds | Water Total Organic Compounds |  | waterTOC | Yes | Yes | No | Number |  |  | milligrams_per_liter | milligrams_per_liter | 0 | 0 |  |  | water,toc,sensor | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS,WTS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterTurbidity | waterTurbidity | Water Turbidity | Water Turbidity |  | waterTurbidity | Yes | Yes | No | Number |  |  | nephelometric_turbidity_units | nephelometric_turbidity_units | 2 | 2 |  |  | water,turbidity,sensor | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS,WTS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterUVT | waterUVT | Water Ultraviolet Transmittance | Water Ultraviolet Transmittance |  | waterUVT | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | water,ultraviolet,transmittance,sensor | BLR,BTU,CM,DCWS,DHWS,PWS,ROS,VBTU,WH,WSS,WTS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterValve | waterValveXXXX | Water Valve Command | Water Valve XX Command |  | waterValve(\d{0,4}) | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | common,water,valve,position,cmd | AHU,CRAC,CRAH,DHU,DOAS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterValveFb | waterValveXXXXFb | Water Valve Feedback | Water Valve XX Feedback |  | waterValve(\d{0,4})Fb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | common,water,valve,position,sensor | AHU,CRAC,CRAH,DHU,DOAS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterValveMode | waterValveXXXXMode | Water Valve Heating/Cooling Changeover Mode | Water Valve XX Heating/Cooling Changeover Mode |  | waterValve(\d{0,4})Mode | Yes | Yes | No | Bool | Cool/Heat | Cool/Heat | [6 empty] | common,water,valve,mode,cmd | AHU,CRAC,CRAH,DHU,DOAS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
waterValveOvr | waterValveXXXXOvr | Water Valve Override | Water Valve XX Override |  | waterValve(\d{0,4})Ovr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | common,water,valve,position,ovr | AHU,CRAC,CRAH,DHU,DOAS | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelAlarm | wheelXXXXAlarm | Wheel Alarm | Wheel XX Alarm |  | wheel(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | common,wheel,general,alarm | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelBypass | wheelXXXXBypass | Wheel Bypass | Wheel XX Bypass |  | wheel(\d{0,4})Bypass | Yes | Yes | No | Bool | Bypass/Normal | Bypass/Normal | [6 empty] | common,wheel,bypass,general,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelBypassDamper | wheelXXXXBypassDamper | Wheel Bypass Damper Command | Wheel XX Bypass Damper Command |  | wheel(\d{0,4})BypassDamper | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | common,wheel,bypass,damper,position,cmd | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelBypassDamperFb | wheelXXXXBypassDamperFb | Wheel Bypass Damper Feedback | Wheel XX Bypass Damper Feedback |  | wheel(\d{0,4})BypassDamperFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | common,wheel,bypass,damper,position,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheel | wheelXXXX | Wheel Command | Wheel XX Command |  | wheel(\d{0,4}) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | common,wheel,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelCurrent | wheelXXXXCurrent | Wheel Current | Wheel XX Current |  | wheel(\d{0,4})Current | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | common,wheel,current,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDefrost | wheelXXXXDefrost | Wheel Defrost | Wheel XX Defrost |  | wheel(\d{0,4})Defrost | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | wheel,defrost,cmd | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDefrostEnableSp | wheelXXXXDefrostEnableSp | Wheel Defrost Enable Setpoint | Wheel XX Defrost Enable Setpoint |  | wheel(\d{0,4})DefrostEnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | wheel,defrost,enable,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeEnthalpy | wheelXXXXDischargeEnthalpy | Wheel Discharge Enthalpy | Wheel XX Discharge Enthalpy |  | wheel(\d{0,4})DischargeEnthalpy | Yes | Yes | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | wheel,discharge,air,enthalpy,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeFanAlarm | wheelXXXXDischargeFanAlarm | Wheel Discharge Fan Alarm | Wheel XX Discharge Fan Alarm |  | wheel(\d{0,4})DischargeFanAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | wheel,discharge,air,fan,common,alarm | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeFanAlarmReset | wheelXXXXDischargeFanAlarmReset | Wheel Discharge Fan Alarm Reset | Wheel XX Discharge Fan Alarm Reset |  | wheel(\d{0,4})DischargeFanAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | wheel,discharge,air,fan,alarm,reset | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.15 (Released),2.16 (Pre-Release)
wheelDischargeFan | wheelXXXXDischargeFan | Wheel Discharge Fan Command | Wheel XX Discharge Fan Command |  | wheel(\d{0,4})DischargeFan | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | wheel,discharge,air,fan,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeFanCurrent | wheelXXXXDischargeFanCurrent | Wheel Discharge Fan Current | Wheel XX Discharge Fan Current |  | wheel(\d{0,4})DischargeFanCurrent | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | wheel,discharge,air,fan,current,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeFanEnteringPressure | wheelXXXXDischargeFanEnteringPressure | Wheel Discharge Fan Entering Pressure | Wheel XX Discharge Fan Entering Pressure |  | wheel(\d{0,4})DischargeFanEnteringPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | wheel,discharge,air,fan,entering,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeFanFault | wheelXXXXDischargeFanFault | Wheel Discharge Fan Fault | Wheel XX Discharge Fan Fault |  | wheel(\d{0,4})DischargeFanFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | wheel,discharge,air,fan,fault,common | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeFanLeavingPressure | wheelXXXXDischargeFanLeavingPressure | Wheel Discharge Fan Leaving Pressure | Wheel XX Discharge Fan Leaving Pressure |  | wheel(\d{0,4})DischargeFanLeavingPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | wheel,discharge,air,fan,leaving,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeFanMaintSwitch | wheelXXXXDischargeFanMaintSwitch | Wheel Discharge Fan Maintenance Switch | Wheel XX Discharge Fan Maintenance Switch |  | wheel(\d{0,4})DischargeFanMaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | wheel,discharge,air,fan,maintenance,switch,cmd | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.15 (Released),2.16 (Pre-Release)
wheelDischargeFanOvr | wheelXXXXDischargeFanOvr | Wheel Discharge Fan Override | Wheel XX Discharge Fan Override |  | wheel(\d{0,4})DischargeFanOvr | No | No | No | Bool | On/Off | On/Off | [6 empty] | wheel,discharge,air,fan,status,ovr | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeFanPressureDelta | wheelXXXXDischargeFanPressureDelta | Wheel Discharge Fan Pressure Delta | Wheel XX Discharge Fan Pressure Delta |  | wheel(\d{0,4})DischargeFanPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | wheel,discharge,air,fan,common,pressure,delta,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeFanPressureHiAlarm | wheelXXXXDischargeFanPressureHiAlarm | Wheel Discharge Fan Pressure High Alarm | Wheel XX Discharge Fan Pressure High Alarm |  | wheel(\d{0,4})DischargeFanPressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | wheel,discharge,air,fan,pressure,high,alarm | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeFanPressureHiSp | wheelXXXXDischargeFanPressureHiSp | Wheel Discharge Fan Pressure High Setpoint | Wheel XX Discharge Fan Pressure High Setpoint |  | wheel(\d{0,4})DischargeFanPressureHiSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | wheel,discharge,air,fan,pressure,high,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeFanPressureLoAlarm | wheelXXXXDischargeFanPressureLoAlarm | Wheel Discharge Fan Pressure Low Alarm | Wheel XX Discharge Fan Pressure Low Alarm |  | wheel(\d{0,4})DischargeFanPressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | wheel,discharge,air,fan,pressure,low,alarm | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeFanPressureLoSp | wheelXXXXDischargeFanPressureLoSp | Wheel Discharge Fan Pressure Low Setpoint | Wheel XX Discharge Fan Pressure Low Setpoint |  | wheel(\d{0,4})DischargeFanPressureLoSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | wheel,discharge,air,fan,pressure,low,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeFanRuntime | wheelXXXXDischargeFanRuntime | Wheel Discharge Fan Runtime | Wheel XX Discharge Fan Runtime |  | wheel(\d{0,4})DischargeFanRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.15 (Released),2.16 (Pre-Release)
wheelDischargeFanSpeed | wheelXXXXDischargeFanSpeed | Wheel Discharge Fan Speed | Wheel XX Discharge Fan Speed |  | wheel(\d{0,4})DischargeFanSpeed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | wheel,discharge,air,fan,speed,cmd | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeFanSpeedFb | wheelXXXXDischargeFanSpeedFb | Wheel Discharge Fan Speed Feedback | Wheel XX Discharge Fan Speed Feedback |  | wheel(\d{0,4})DischargeFanSpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | wheel,discharge,air,fan,speed,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeFanSpeedMaxSp | wheelXXXXDischargeFanSpeedMaxSp | Wheel Discharge Fan Speed Max Setpoint | Wheel XX Discharge Fan Speed Max Setpoint |  | wheel(\d{0,4})DischargeFanSpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | wheel,discharge,air,fan,speed,max,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeFanSpeedMinSp | wheelXXXXDischargeFanSpeedMinSp | Wheel Discharge Fan Speed Min Setpoint | Wheel XX Discharge Fan Speed Min Setpoint |  | wheel(\d{0,4})DischargeFanSpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | wheel,discharge,air,fan,speed,min,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeFanSpeedOvr | wheelXXXXDischargeFanSpeedOvr | Wheel Discharge Fan Speed Override | Wheel XX Discharge Fan Speed Override |  | wheel(\d{0,4})DischargeFanSpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | wheel,discharge,air,fan,speed,ovr | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeFanSpeedSp | wheelXXXXDischargeFanSpeedSp | Wheel Discharge Fan Speed Setpoint | Wheel XX Discharge Fan Speed Setpoint |  | wheel(\d{0,4})DischargeFanSpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | wheel,discharge,air,fan,speed,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeFanStatus | wheelXXXXDischargeFanStatus | Wheel Discharge Fan Status | Wheel XX Discharge Fan Status |  | wheel(\d{0,4})DischargeFanStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | wheel,discharge,air,fan,status,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeFlow | wheelXXXXDischargeFlow | Wheel Discharge Flow | Wheel XX Discharge Flow |  | wheel(\d{0,4})DischargeFlow | Yes | Yes | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | wheel,discharge,air,flow,sensor | AFMS,AHU,CRAC,CRAH,CU,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeHumidity | wheelXXXXDischargeHumidity | Wheel Discharge Humidity | Wheel XX Discharge Humidity |  | wheel(\d{0,4})DischargeHumidity | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | wheel,discharge,air,humidity,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeIsoDamper | wheelXXXXDischargeIsoDamper | Wheel Discharge Isolation Damper Command | Wheel XX Discharge Isolation Damper Command |  | wheel(\d{0,4})DischargeIsoDamper | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | wheel,discharge,iso,air,damper,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeIsoDamperFb | wheelXXXXDischargeIsoDamperFb | Wheel Discharge Isolation Damper Feedback | Wheel XX Discharge Isolation Damper Feedback |  | wheel(\d{0,4})DischargeIsoDamperFb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | wheel,discharge,iso,air,damper,status,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargePressure | wheelXXXXDischargePressure | Wheel Discharge Pressure | Wheel XX Discharge Pressure |  | wheel(\d{0,4})DischargePressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | wheel,discharge,air,static,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeTemp | wheelXXXXDischargeTemp | Wheel Discharge Temperature | Wheel XX Discharge Temperature |  | wheel(\d{0,4})DischargeTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | wheel,discharge,air,temp,sensor | AFMS,AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeTempDb | wheelXXXXDischargeTempDb | Wheel Discharge Temperature Deadband | Wheel XX Discharge Temperature Deadband |  | wheel(\d{0,4})DischargeTempDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | wheel,discharge,air,temp,deadband,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeTempHiSp | wheelXXXXDischargeTempHiSp | Wheel Discharge Temperature High Setpoint | Wheel XX Discharge Temperature High Setpoint |  | wheel(\d{0,4})DischargeTempHiSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | wheel,discharge,air,temp,high,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeTempLoAlarm | wheelXXXXDischargeTempLoAlarm | Wheel Discharge Temperature Low Alarm | Wheel XX Discharge Temperature Low Alarm |  | wheel(\d{0,4})DischargeTempLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | wheel,discharge,air,temp,low,alarm | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeTempLoSp | wheelXXXXDischargeTempLoSp | Wheel Discharge Temperature Low Setpoint | Wheel XX Discharge Temperature Low Setpoint |  | wheel(\d{0,4})DischargeTempLoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | wheel,discharge,air,temp,low,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeTempMaxSp | wheelXXXXDischargeTempMaxSp | Wheel Discharge Temperature Max Reset Setpoint | Wheel XX Discharge Temperature Max Reset Setpoint |  | wheel(\d{0,4})DischargeTempMaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | wheel,discharge,air,temp,max,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeTempMinSp | wheelXXXXDischargeTempMinSp | Wheel Discharge Temperature Min Reset Setpoint | Wheel XX Discharge Temperature Min Reset Setpoint |  | wheel(\d{0,4})DischargeTempMinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | wheel,discharge,air,temp,min,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeTempSp | wheelXXXXDischargeTempSp | Wheel Discharge Temperature Setpoint | Wheel XX Discharge Temperature Setpoint |  | wheel(\d{0,4})DischargeTempSp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | wheel,discharge,air,temp,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelDischargeVelPressure | wheelXXXXDischargeVelPressure | Wheel Discharge Velocity Pressure | Wheel XX Discharge Velocity Pressure |  | wheel(\d{0,4})DischargeVelPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | wheel,discharge,air,dynamic,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelEnable | wheelXXXXEnable | Wheel Enable | Wheel XX Enable |  | wheel(\d{0,4})Enable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | wheel,common,enable,cmd | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelEnableSp | wheelXXXXEnableSp | Wheel Enable Setpoint | Wheel XX Enable Setpoint |  | wheel(\d{0,4})EnableSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | wheel,common,enable,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelEnergy | wheelXXXXEnergy | Wheel Energy | Wheel XX Energy |  | wheel(\d{0,4})Energy | Yes | Yes | No | Number |  |  | kilowatt_hour | kilowatt_hour | 0 | 0 |  |  | common,wheel,energy,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelExhaustBypassDamper | wheelXXXXExhaustBypassDamper | Wheel Exhaust Bypass Damper Command | Wheel XX Exhaust Bypass Damper Command |  | wheel(\d{0,4})ExhaustBypassDamper | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | wheel,exhaust,bypass,damper,position,cmd | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelExhaustDamper | wheelXXXXExhaustDamper | Wheel Exhaust Damper | Wheel XX Exhaust Damper |  | wheel(\d{0,4})ExhaustDamper | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | wheel,exhaust,damper,common,position,cmd | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelExhaustDamperFb | wheelXXXXExhaustDamperFb | Wheel Exhaust Damper Feedback | Wheel XX Exhaust Damper Feedback |  | wheel(\d{0,4})ExhaustDamperFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | wheel,exhaust,damper,common,position,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelExhaustEnthalpy | wheelXXXXExhaustEnthalpy | Wheel Exhaust Enthalpy | Wheel XX Exhaust Enthalpy |  | wheel(\d{0,4})ExhaustEnthalpy | Yes | Yes | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | wheel,exhaust,air,enthalpy,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelExhaustFanAlarm | wheelXXXXExhaustFanAlarm | Wheel Exhaust Fan Alarm | Wheel XX Exhaust Fan Alarm |  | wheel(\d{0,4})ExhaustFanAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | wheel,exhaust,air,fan,common,alarm | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelExhaustFanAlarmReset | wheelXXXXExhaustFanAlarmReset | Wheel Exhaust Fan Alarm Reset | Wheel XX Exhaust Fan Alarm Reset |  | wheel(\d{0,4})ExhaustFanAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | wheel,air,fan,alarm,reset,exhaust | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.15 (Released),2.16 (Pre-Release)
wheelExhaustFan | wheelXXXXExhaustFan | Wheel Exhaust Fan Command | Wheel XX Exhaust Fan Command |  | wheel(\d{0,4})ExhaustFan | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | wheel,exhaust,air,fan,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelExhaustFanCurrent | wheelXXXXExhaustFanCurrent | Wheel Exhaust Fan Current | Wheel XX Exhaust Fan Current |  | wheel(\d{0,4})ExhaustFanCurrent | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | wheel,exhaust,air,fan,current,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelExhaustFanEnteringPressure | wheelXXXXExhaustFanEnteringPressure | Wheel Exhaust Fan Entering Pressure | Wheel XX Exhaust Fan Entering Pressure |  | wheel(\d{0,4})ExhaustFanEnteringPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | wheel,exhaust,air,fan,entering,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelExhaustFanFault | wheelXXXXExhaustFanFault | Wheel Exhaust Fan Fault | Wheel XX Exhaust Fan Fault |  | wheel(\d{0,4})ExhaustFanFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | wheel,exhaust,air,fan,fault,common | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelExhaustFanLeavingPressure | wheelXXXXExhaustFanLeavingPressure | Wheel Exhaust Fan Leaving Pressure | Wheel XX Exhaust Fan Leaving Pressure |  | wheel(\d{0,4})ExhaustFanLeavingPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | wheel,exhaust,air,fan,leaving,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelExhaustFanMaintSwitch | wheelXXXXExhaustFanMaintSwitch | Wheel Exhaust Fan Maintenance Switch | Wheel XX Exhaust Fan Maintenance Switch |  | wheel(\d{0,4})ExhaustFanMaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | wheel,air,fan,exhaust,maintenance,switch,cmd | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.15 (Released),2.16 (Pre-Release)
wheelExhaustFanOvr | wheelXXXXExhaustFanOvr | Wheel Exhaust Fan Override | Wheel XX Exhaust Fan Override |  | wheel(\d{0,4})ExhaustFanOvr | No | No | No | Bool | On/Off | On/Off | [6 empty] | wheel,exhaust,air,fan,status,ovr | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelExhaustFanPressureDelta | wheelXXXXExhaustFanPressureDelta | Wheel Exhaust Fan Pressure Delta | Wheel XX Exhaust Fan Pressure Delta |  | wheel(\d{0,4})ExhaustFanPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | wheel,exhaust,air,fan,common,pressure,delta,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelExhaustFanPressureHiAlarm | wheelXXXXExhaustFanPressureHiAlarm | Wheel Exhaust Fan Pressure High Alarm | Wheel XX Exhaust Fan Pressure High Alarm |  | wheel(\d{0,4})ExhaustFanPressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | wheel,exhaust,air,fan,pressure,high,alarm | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelExhaustFanPressureHiSp | wheelXXXXExhaustFanPressureHiSp | Wheel Exhaust Fan Pressure High Setpoint | Wheel XX Exhaust Fan Pressure High Setpoint |  | wheel(\d{0,4})ExhaustFanPressureHiSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | wheel,exhaust,air,fan,pressure,high,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelExhaustFanPressureLoAlarm | wheelXXXXExhaustFanPressureLoAlarm | Wheel Exhaust Fan Pressure Low Alarm | Wheel XX Exhaust Fan Pressure Low Alarm |  | wheel(\d{0,4})ExhaustFanPressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | wheel,exhaust,air,fan,pressure,low,alarm | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelExhaustFanPressureLoSp | wheelXXXXExhaustFanPressureLoSp | Wheel Exhaust Fan Pressure Low Setpoint | Wheel XX Exhaust Fan Pressure Low Setpoint |  | wheel(\d{0,4})ExhaustFanPressureLoSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | wheel,exhaust,air,fan,pressure,low,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelExhaustFanRuntime | wheelXXXXExhaustFanRuntime | Wheel Exhaust Fan Runtime | Wheel XX Exhaust Fan Runtime |  | wheel(\d{0,4})ExhaustFanRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.15 (Released),2.16 (Pre-Release)
wheelExhaustFanSpeed | wheelXXXXExhaustFanSpeed | Wheel Exhaust Fan Speed | Wheel XX Exhaust Fan Speed |  | wheel(\d{0,4})ExhaustFanSpeed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | wheel,exhaust,air,fan,speed,cmd | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelExhaustFanSpeedFb | wheelXXXXExhaustFanSpeedFb | Wheel Exhaust Fan Speed Feedback | Wheel XX Exhaust Fan Speed Feedback |  | wheel(\d{0,4})ExhaustFanSpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | wheel,exhaust,air,fan,speed,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelExhaustFanSpeedMaxSp | wheelXXXXExhaustFanSpeedMaxSp | Wheel Exhaust Fan Speed Max Setpoint | Wheel XX Exhaust Fan Speed Max Setpoint |  | wheel(\d{0,4})ExhaustFanSpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | wheel,exhaust,air,fan,speed,max,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelExhaustFanSpeedMinSp | wheelXXXXExhaustFanSpeedMinSp | Wheel Exhaust Fan Speed Min Setpoint | Wheel XX Exhaust Fan Speed Min Setpoint |  | wheel(\d{0,4})ExhaustFanSpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | wheel,exhaust,air,fan,speed,min,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelExhaustFanSpeedOvr | wheelXXXXExhaustFanSpeedOvr | Wheel Exhaust Fan Speed Override | Wheel XX Exhaust Fan Speed Override |  | wheel(\d{0,4})ExhaustFanSpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | wheel,exhaust,air,fan,speed,ovr | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelExhaustFanSpeedSp | wheelXXXXExhaustFanSpeedSp | Wheel Exhaust Fan Speed Setpoint | Wheel XX Exhaust Fan Speed Setpoint |  | wheel(\d{0,4})ExhaustFanSpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | wheel,exhaust,air,fan,speed,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelExhaustFanStatus | wheelXXXXExhaustFanStatus | Wheel Exhaust Fan Status | Wheel XX Exhaust Fan Status |  | wheel(\d{0,4})ExhaustFanStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | wheel,exhaust,air,fan,status,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelExhaustFlow | wheelXXXXExhaustFlow | Wheel Exhaust Flow | Wheel XX Exhaust Flow |  | wheel(\d{0,4})ExhaustFlow | Yes | Yes | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | wheel,exhaust,air,flow,sensor | AFMS,AHU,CRAC,CRAH,CU,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelExhaustHumidity | wheelXXXXExhaustHumidity | Wheel Exhaust Humidity | Wheel XX Exhaust Humidity |  | wheel(\d{0,4})ExhaustHumidity | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | wheel,exhaust,air,humidity,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelExhaustIsoDamper | wheelXXXXExhaustIsoDamper | Wheel Exhaust Isolation Damper Command | Wheel XX Exhaust Isolation Damper Command |  | wheel(\d{0,4})ExhaustIsoDamper | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | wheel,exhaust,iso,air,damper,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelExhaustIsoDamperFb | wheelXXXXExhaustIsoDamperFb | Wheel Exhaust Isolation Damper Feedback | Wheel XX Exhaust Isolation Damper Feedback |  | wheel(\d{0,4})ExhaustIsoDamperFb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | wheel,exhaust,iso,air,damper,status,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelExhaustPressure | wheelXXXXExhaustPressure | Wheel Exhaust Pressure | Wheel XX Exhaust Pressure |  | wheel(\d{0,4})ExhaustPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | wheel,exhaust,air,static,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelExhaustTemp | wheelXXXXExhaustTemp | Wheel Exhaust Temperature | Wheel XX Exhaust Temperature |  | wheel(\d{0,4})ExhaustTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | wheel,exhaust,air,temp,sensor | AFMS,AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelExhaustVelPressure | wheelXXXXExhaustVelPressure | Wheel Exhaust Velocity Pressure | Wheel XX Exhaust Velocity Pressure |  | wheel(\d{0,4})ExhaustVelPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | wheel,exhaust,air,dynamic,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelFaceBypassDamper | wheelXXXXFaceBypassDamper | Wheel Face Bypass Damper Command | Wheel XX Face Bypass Damper Command |  | wheel(\d{0,4})FaceBypassDamper | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | common,wheel,faceBypass,damper,position,cmd | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelFaceBypassDamperFb | wheelXXXXFaceBypassDamperFb | Wheel Face Bypass Damper Feedback | Wheel XX Face Bypass Damper Feedback |  | wheel(\d{0,4})FaceBypassDamperFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | common,wheel,faceBypass,damper,position,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelFaceDamper | wheelXXXXFaceDamper | Wheel Face Damper Command | Wheel XX Face Damper Command |  | wheel(\d{0,4})FaceDamper | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | common,wheel,face,damper,position,cmd | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelFaceDamperFb | wheelXXXXFaceDamperFb | Wheel Face Damper Feedback | Wheel XX Face Damper Feedback |  | wheel(\d{0,4})FaceDamperFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | common,wheel,face,damper,position,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelFault | wheelXXXXFault | Wheel Fault | Wheel XX Fault |  | wheel(\d{0,4})Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | common,wheel,fault,general | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelFaultCode | wheelXXXXFaultCode | Wheel Fault Code | Wheel XX Fault Code |  | wheel(\d{0,4})FaultCode | Yes | Yes | No | Str | [8 empty] | common,wheel,fault,code | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.15 (Released)
wheelFaultReset | wheelXXXXFaultReset | Wheel Fault Reset | Wheel XX Fault Reset |  | wheel(\d{0,4})FaultReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | common,wheel,fault,reset | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelFrequency | wheelXXXXFrequency | Wheel Frequency | Wheel XX Frequency |  | wheel(\d{0,4})Frequency | Yes | Yes | No | Number |  |  | hertz | hertz | 1 | 1 |  |  | common,wheel,freq,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelHandMode | wheelXXXXHandMode | Wheel Hand/Auto Mode | Wheel XX Hand/Auto Mode |  | wheelHandMode | Yes | Yes | No | Bool | Hand/Auto | Hand/Auto | [6 empty] | common,wheel,handMode,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelMaintSwitch | wheelXXXXMaintSwitch | Wheel Maintenance Switch | Wheel XX Maintenance Switch |  | wheel(\d{0,4})MaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | common,wheel,maintenance,switch,cmd | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelMode | wheelXXXXMode | Wheel Mode Command | Wheel XX Mode Command |  | wheel(\d{0,4})Mode | Yes | Yes | No | Str | Reclaim/Off | Reclaim/Partial Reclaim/Off | [6 empty] | common,wheel,mode,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideBypassDamper | wheelXXXXOutsideBypassDamper | Wheel Outside Bypass Damper Command | Wheel XX Outside Bypass Damper Command |  | wheel(\d{0,4})OutsideBypassDamper | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | wheel,outside,bypass,damper,position,cmd | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideBypassDamperFb | wheelXXXXOutsideBypassDamperFb | Wheel Outside Bypass Damper Feedback | Wheel XX Outside Bypass Damper Feedback |  | wheel(\d{0,4})OutsideBypassDamperFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | wheel,outside,bypass,damper,position,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideDamper | wheelXXXXOutsideDamper | Wheel Outside Damper | Wheel XX Outside Damper |  | wheel(\d{0,4})OutsideDamper | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | wheel,outside,damper,common,position,cmd | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideDamperFb | wheelXXXXOutsideDamperFb | Wheel Outside Damper Feedback | Wheel XX Outside Damper Feedback |  | wheel(\d{0,4})OutsideDamperFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | wheel,outside,damper,common,position,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideEnthalpy | wheelXXXXOutsideEnthalpy | Wheel Outside Enthalpy | Wheel XX Outside Enthalpy |  | wheel(\d{0,4})OutsideEnthalpy | Yes | Yes | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | wheel,outside,air,enthalpy,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideFanAlarm | wheelXXXXOutsideFanAlarm | Wheel Outside Fan Alarm | Wheel XX Outside Fan Alarm |  | wheel(\d{0,4})OutsideFanAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | wheel,outside,air,fan,common,alarm | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideFanAlarmReset | wheelXXXXOutsideFanAlarmReset | Wheel Outside Fan Alarm Reset | Wheel XX Outside Fan Alarm Reset |  | wheel(\d{0,4})OutsideFanAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | wheel,air,fan,alarm,reset,outside | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.15 (Released),2.16 (Pre-Release)
wheelOutsideFan | wheelXXXXOutsideFan | Wheel Outside Fan Command | Wheel XX Outside Fan Command |  | wheel(\d{0,4})OutsideFan | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | wheel,outside,air,fan,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideFanCurrent | wheelXXXXOutsideFanCurrent | Wheel Outside Fan Current | Wheel XX Outside Fan Current |  | wheel(\d{0,4})OutsideFanCurrent | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | wheel,outside,air,fan,current,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideFanEnteringPressure | wheelXXXXOutsideFanEnteringPressure | Wheel Outside Fan Entering Pressure | Wheel XX Outside Fan Entering Pressure |  | wheel(\d{0,4})OutsideFanEnteringPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | wheel,outside,air,fan,entering,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideFanFault | wheelXXXXOutsideFanFault | Wheel Outside Fan Fault | Wheel XX Outside Fan Fault |  | wheel(\d{0,4})OutsideFanFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | wheel,outside,air,fan,fault,common | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideFanLeavingPressure | wheelXXXXOutsideFanLeavingPressure | Wheel Outside Fan Leaving Pressure | Wheel XX Outside Fan Leaving Pressure |  | wheel(\d{0,4})OutsideFanLeavingPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | wheel,outside,air,fan,leaving,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideFanMaintSwitch | wheelXXXXOutsideFanMaintSwitch | Wheel Outside Fan Maintenance Switch | Wheel XX Outside Fan Maintenance Switch |  | wheel(\d{0,4})OutsideFanMaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | wheel,air,fan,outside,maintenance,switch,cmd | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.15 (Released),2.16 (Pre-Release)
wheelOutsideFanOvr | wheelXXXXOutsideFanOvr | Wheel Outside Fan Override | Wheel XX Outside Fan Override |  | wheel(\d{0,4})OutsideFanOvr | No | No | No | Bool | On/Off | On/Off | [6 empty] | wheel,outside,air,fan,status,ovr | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideFanPressureDelta | wheelXXXXOutsideFanPressureDelta | Wheel Outside Fan Pressure Delta | Wheel XX Outside Fan Pressure Delta |  | wheel(\d{0,4})OutsideFanPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | wheel,outside,air,fan,common,pressure,delta,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideFanPressureHiAlarm | wheelXXXXOutsideFanPressureHiAlarm | Wheel Outside Fan Pressure High Alarm | Wheel XX Outside Fan Pressure High Alarm |  | wheel(\d{0,4})OutsideFanPressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | wheel,outside,air,fan,pressure,high,alarm | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideFanPressureHiSp | wheelXXXXOutsideFanPressureHiSp | Wheel Outside Fan Pressure High Setpoint | Wheel XX Outside Fan Pressure High Setpoint |  | wheel(\d{0,4})OutsideFanPressureHiSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | wheel,outside,air,fan,pressure,high,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideFanPressureLoAlarm | wheelXXXXOutsideFanPressureLoAlarm | Wheel Outside Fan Pressure Low Alarm | Wheel XX Outside Fan Pressure Low Alarm |  | wheel(\d{0,4})OutsideFanPressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | wheel,outside,air,fan,pressure,low,alarm | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideFanPressureLoSp | wheelXXXXOutsideFanPressureLoSp | Wheel Outside Fan Pressure Low Setpoint | Wheel XX Outside Fan Pressure Low Setpoint |  | wheel(\d{0,4})OutsideFanPressureLoSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | wheel,outside,air,fan,pressure,low,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideFanRuntime | wheelXXXXOutsideFanRuntime | Wheel Outside Fan Runtime | Wheel XX Outside Fan Runtime |  | wheel(\d{0,4})OutsideFanRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.15 (Released),2.16 (Pre-Release)
wheelOutsideFanSpeed | wheelXXXXOutsideFanSpeed | Wheel Outside Fan Speed | Wheel XX Outside Fan Speed |  | wheel(\d{0,4})OutsideFanSpeed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | wheel,outside,air,fan,speed,cmd | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideFanSpeedFb | wheelXXXXOutsideFanSpeedFb | Wheel Outside Fan Speed Feedback | Wheel XX Outside Fan Speed Feedback |  | wheel(\d{0,4})OutsideFanSpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | wheel,outside,air,fan,speed,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideFanSpeedMaxSp | wheelXXXXOutsideFanSpeedMaxSp | Wheel Outside Fan Speed Max Setpoint | Wheel XX Outside Fan Speed Max Setpoint |  | wheel(\d{0,4})OutsideFanSpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | wheel,outside,air,fan,speed,max,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideFanSpeedMinSp | wheelXXXXOutsideFanSpeedMinSp | Wheel Outside Fan Speed Min Setpoint | Wheel XX Outside Fan Speed Min Setpoint |  | wheel(\d{0,4})OutsideFanSpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | wheel,outside,air,fan,speed,min,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideFanSpeedOvr | wheelXXXXOutsideFanSpeedOvr | Wheel Outside Fan Speed Override | Wheel XX Outside Fan Speed Override |  | wheel(\d{0,4})OutsideFanSpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | wheel,outside,air,fan,speed,ovr | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideFanSpeedSp | wheelXXXXOutsideFanSpeedSp | Wheel Outside Fan Speed Setpoint | Wheel XX Outside Fan Speed Setpoint |  | wheel(\d{0,4})OutsideFanSpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | wheel,outside,air,fan,speed,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideFanStatus | wheelXXXXOutsideFanStatus | Wheel Outside Fan Status | Wheel XX Outside Fan Status |  | wheel(\d{0,4})OutsideFanStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | wheel,outside,air,fan,status,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideFilterAlarm | wheelXXXXOutsideFilterYYYYAlarm | Wheel Outside Filter Alarm | Wheel XX Outside Filter YY Alarm |  | wheel(\d{0,4})OutsideFilter(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | wheel,outside,air,filter,general,alarm | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideFilterAlarmReset | wheelXXXXOutsideFilterAlarmReset | Wheel Outside Filter Alarm Reset | Wheel XX Outside Filter Alarm Reset |  | wheel(\d{0,4})OutsideFilterAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | wheel,outside,air,filter,reset,alarm | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideFilterPressureDelta | wheelXXXXOutsideFilterPressureDelta | Wheel Outside Filter Pressure Delta | Wheel XX Outside Filter Pressure Delta |  | wheel(\d{0,4})OutsideFilterPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | wheel,outside,air,filter,pressure,delta,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released)
wheelOutsideFilterRuntime | wheelXXXXOutsideFilterRuntime | Wheel Outside Filter Runtime | Wheel XX Outside Filter Runtime |  | wheel(\d{0,4})OutsideFilterRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.15 (Released),2.16 (Pre-Release)
wheelOutsideFlow | wheelXXXXOutsideFlow | Wheel Outside Flow | Wheel XX Outside Flow |  | wheel(\d{0,4})OutsideFlow | Yes | Yes | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | wheel,outside,air,flow,sensor | AFMS,AHU,CRAC,CRAH,CU,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideHumidity | wheelXXXXOutsideHumidity | Wheel Outside Humidity | Wheel XX Outside Humidity |  | wheel(\d{0,4})OutsideHumidity | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | wheel,outside,air,humidity,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideIsoDamper | wheelXXXXOutsideIsoDamper | Wheel Outside Isolation Damper Command | Wheel XX Outside Isolation Damper Command |  | wheel(\d{0,4})OutsideIsoDamper | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | wheel,outside,iso,air,damper,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideIsoDamperFb | wheelXXXXOutsideIsoDamperFb | Wheel Outside Isolation Damper Feedback | Wheel XX Outside Isolation Damper Feedback |  | wheel(\d{0,4})OutsideIsoDamperFb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | wheel,outside,iso,air,damper,status,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsidePressure | wheelXXXXOutsidePressure | Wheel Outside Pressure | Wheel XX Outside Pressure |  | wheel(\d{0,4})OutsidePressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | wheel,outside,air,static,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideTemp | wheelXXXXOutsideTemp | Wheel Outside Temperature | Wheel XX Outside Temperature |  | wheel(\d{0,4})OutsideTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | wheel,outside,air,temp,sensor | AFMS,AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideTempLoAlarm | wheelXXXXOutsideTempLoAlarm | Wheel Outside Temperature Low Alarm | Wheel XX Outside Temperature Low Alarm |  | wheel(\d{0,4})OutsideTempLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | wheel,outside,air,temp,low,alarm | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOutsideVelPressure | wheelXXXXOutsideVelPressure | Wheel Outside Velocity Pressure | Wheel XX Outside Velocity Pressure |  | wheel(\d{0,4})OutsideVelPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | wheel,outside,air,dynamic,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelOvr | wheelXXXXOvr | Wheel Override | Wheel XX Override |  | wheel(\d{0,4})Ovr | No | No | No | Bool | On/Off | On/Off | [6 empty] | common,wheel,status,ovr | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelPreHeatingCoilEnteringTemp | wheelXXXXPreHeatingCoilEnteringTemp | Wheel Pre-Heating Coil Entering Temperature | Wheel XX Pre-Heating Coil Entering Temperature |  | wheel(\d{0,4})PreHeatingCoilEnteringTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | wheel,preHeat,coil,entering,temp,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelPreHeatingCoilLeavingTemp | wheelXXXXPreHeatingCoilLeavingTemp | Wheel Pre-Heating Coil Leaving Temperature | Wheel XX Pre-Heating Coil Leaving Temperature |  | wheel(\d{0,4})PreHeatingCoilLeavingTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | wheel,preHeat,coil,leaving,temp,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelPreHeatingStage | wheelXXXXPreHeatingStage | Wheel Pre-Heating Stage Command | Wheel XX Pre-Heating Stage Command |  | wheel(\d{0,4})PreHeatingStage | Yes | Yes | No | Bool | On/Off | On/Off |  |  |  |  | 1 |  | wheel,preHeat,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelPreHeatingStageOvr | wheelXXXXPreHeatingStageOvr | Wheel Pre-Heating Stage Override | Wheel XX Pre-Heating Stage Override |  | wheel(\d{0,4})PreHeatingStageOvr | No | No | No | Bool | On/Off | On/Off |  |  |  |  | 1 |  | wheel,preHeat,status,ovr | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelPreHeatingStageStatus | wheelXXXXPreHeatingStageStatus | Wheel Pre-Heating Stage Status | Wheel XX Pre-Heating Stage Status |  | wheel(\d{0,4})PreHeatingStageStatus | Yes | Yes | No | Bool | On/Off | On/Off |  |  |  |  | 1 |  | wheel,preHeat,status,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelPreHeatingValve | wheelXXXXPreHeatingValve | Wheel Pre-Heating Valve Command | Wheel XX Pre-Heating Valve Command |  | wheel(\d{0,4})PreHeatingValve | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | wheel,preHeat,valve,position,cmd | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelPreHeatingValveFb | wheelXXXXPreHeatingValveFb | Wheel Pre-Heating Valve Feedback | Wheel XX Pre-Heating Valve Feedback |  | wheel(\d{0,4})PreHeatingValveFb | Yes | Yes | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | wheel,preHeat,valve,position,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelPreHeatingValveOvr | wheelXXXXPreHeatingValveOvr | Wheel Pre-Heating Valve Override | Wheel XX Pre-Heating Valve Override |  | wheel(\d{0,4})PreHeatingValveOvr | No | No | No | Number | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | wheel,preHeat,valve,position,ovr | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelPressureDelta | wheelXXXXPressureDeltaYYYY | Wheel Pressure Delta | Wheel XX Pressure Delta YY |  | wheel(\d{0,4})PressureDelta(\d{0,4}) | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | wheel,general,air,pressure,delta,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelPressureDeltaHiAlarm | wheelXXXXPressureDeltaYYYYHiAlarm | Wheel Pressure Delta High Alarm | Wheel XX Pressure Delta YY High Alarm |  | wheel(\d{0,4})PressureDelta(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | wheel,air,pressure,delta,high,alarm | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelPowerReal | wheelXXXXPowerReal | Wheel Real Power | Wheel XX Real Power |  | wheel(\d{0,4})PowerReal | Yes | Yes | No | Number |  |  | kilowatt | kilowatt | 1 | 1 |  | N | common,wheel,power,real,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelReturnEnthalpy | wheelXXXXReturnEnthalpy | Wheel Return Enthalpy | Wheel XX Return Enthalpy |  | wheel(\d{0,4})ReturnEnthalpy | Yes | Yes | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | wheel,return,air,enthalpy,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelReturnFanAlarm | wheelXXXXReturnFanAlarm | Wheel Return Fan Alarm | Wheel XX Return Fan Alarm |  | wheel(\d{0,4})ReturnFanAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | wheel,return,air,fan,common,alarm | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelReturnFanAlarmReset | wheelXXXXReturnFanAlarmReset | Wheel Return Fan Alarm Reset | Wheel XX Return Fan Alarm Reset |  | wheel(\d{0,4})ReturnFanAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | wheel,air,fan,alarm,reset,return | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.15 (Released),2.16 (Pre-Release)
wheelReturnFan | wheelXXXXReturnFan | Wheel Return Fan Command | Wheel XX Return Fan Command |  | wheel(\d{0,4})ReturnFan | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | wheel,return,air,fan,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelReturnFanCurrent | wheelXXXXReturnFanCurrent | Wheel Return Fan Current | Wheel XX Return Fan Current |  | wheel(\d{0,4})ReturnFanCurrent | Yes | Yes | No | Number |  |  | ampere | ampere | 1 | 1 |  | N | wheel,return,air,fan,current,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelReturnFanEnteringPressure | wheelXXXXReturnFanEnteringPressure | Wheel Return Fan Entering Pressure | Wheel XX Return Fan Entering Pressure |  | wheel(\d{0,4})ReturnFanEnteringPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | wheel,return,air,fan,entering,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelReturnFanFault | wheelXXXXReturnFanFault | Wheel Return Fan Fault | Wheel XX Return Fan Fault |  | wheel(\d{0,4})ReturnFanFault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | wheel,return,air,fan,fault,common | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelReturnFanLeavingPressure | wheelXXXXReturnFanLeavingPressure | Wheel Return Fan Leaving Pressure | Wheel XX Return Fan Leaving Pressure |  | wheel(\d{0,4})ReturnFanLeavingPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | wheel,return,air,fan,leaving,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelReturnFanMaintSwitch | wheelXXXXReturnFanMaintSwitch | Wheel Return Fan Maintenance Switch | Wheel XX Return Fan Maintenance Switch |  | wheel(\d{0,4})ReturnFanMaintSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | wheel,air,fan,return,maintenance,switch,cmd | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.15 (Released),2.16 (Pre-Release)
wheelReturnFanOvr | wheelXXXXReturnFanOvr | Wheel Return Fan Override | Wheel XX Return Fan Override |  | wheel(\d{0,4})ReturnFanOvr | No | No | No | Bool | On/Off | On/Off | [6 empty] | wheel,return,air,fan,status,ovr | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelReturnFanPressureDelta | wheelXXXXReturnFanPressureDelta | Wheel Return Fan Pressure Delta | Wheel XX Return Fan Pressure Delta |  | wheel(\d{0,4})ReturnFanPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | wheel,return,air,fan,common,pressure,delta,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelReturnFanPressureHiAlarm | wheelXXXXReturnFanPressureHiAlarm | Wheel Return Fan Pressure High Alarm | Wheel XX Return Fan Pressure High Alarm |  | wheel(\d{0,4})ReturnFanPressureHiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | wheel,return,air,fan,pressure,high,alarm | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelReturnFanPressureHiSp | wheelXXXXReturnFanPressureHiSp | Wheel Return Fan Pressure High Setpoint | Wheel XX Return Fan Pressure High Setpoint |  | wheel(\d{0,4})ReturnFanPressureHiSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | wheel,return,air,fan,pressure,high,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelReturnFanPressureLoAlarm | wheelXXXXReturnFanPressureLoAlarm | Wheel Return Fan Pressure Low Alarm | Wheel XX Return Fan Pressure Low Alarm |  | wheel(\d{0,4})ReturnFanPressureLoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | wheel,return,air,fan,pressure,low,alarm | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelReturnFanPressureLoSp | wheelXXXXReturnFanPressureLoSp | Wheel Return Fan Pressure Low Setpoint | Wheel XX Return Fan Pressure Low Setpoint |  | wheel(\d{0,4})ReturnFanPressureLoSp | No | No | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | wheel,return,air,fan,pressure,low,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelReturnFanRuntime | wheelXXXXReturnFanRuntime | Wheel Return Fan Runtime | Wheel XX Return Fan Runtime |  | wheel(\d{0,4})ReturnFanRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.15 (Released),2.16 (Pre-Release)
wheelReturnFanSpeed | wheelXXXXReturnFanSpeed | Wheel Return Fan Speed | Wheel XX Return Fan Speed |  | wheel(\d{0,4})ReturnFanSpeed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | wheel,return,air,fan,speed,cmd | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelReturnFanSpeedFb | wheelXXXXReturnFanSpeedFb | Wheel Return Fan Speed Feedback | Wheel XX Return Fan Speed Feedback |  | wheel(\d{0,4})ReturnFanSpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | wheel,return,air,fan,speed,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelReturnFanSpeedMaxSp | wheelXXXXReturnFanSpeedMaxSp | Wheel Return Fan Speed Max Setpoint | Wheel XX Return Fan Speed Max Setpoint |  | wheel(\d{0,4})ReturnFanSpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | wheel,return,air,fan,speed,max,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelReturnFanSpeedMinSp | wheelXXXXReturnFanSpeedMinSp | Wheel Return Fan Speed Min Setpoint | Wheel XX Return Fan Speed Min Setpoint |  | wheel(\d{0,4})ReturnFanSpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | wheel,return,air,fan,speed,min,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelReturnFanSpeedOvr | wheelXXXXReturnFanSpeedOvr | Wheel Return Fan Speed Override | Wheel XX Return Fan Speed Override |  | wheel(\d{0,4})ReturnFanSpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | wheel,return,air,fan,speed,ovr | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelReturnFanSpeedSp | wheelXXXXReturnFanSpeedSp | Wheel Return Fan Speed Setpoint | Wheel XX Return Fan Speed Setpoint |  | wheel(\d{0,4})ReturnFanSpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | wheel,return,air,fan,speed,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelReturnFanStatus | wheelXXXXReturnFanStatus | Wheel Return Fan Status | Wheel XX Return Fan Status |  | wheel(\d{0,4})ReturnFanStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | wheel,return,air,fan,status,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelReturnFilterAlarm | wheelXXXXReturnFilterAlarm | Wheel Return Filter Alarm | Wheel XX Return Filter Alarm |  | wheel(\d{0,4})ReturnFilterAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | wheel,return,air,filter,general,alarm | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelReturnFilterAlarmReset | wheelXXXXReturnFilterAlarmReset | Wheel Return Filter Alarm Reset | Wheel XX Return Filter Alarm Reset |  | wheel(\d{0,4})ReturnFilterAlarmReset | No | No | No | Bool | Reset/Normal | Reset/Normal | [6 empty] | wheel,return,air,filter,reset,alarm | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelReturnFilterPressureDelta | wheelXXXXReturnFilterPressureDelta | Wheel Return Filter Pressure Delta | Wheel XX Return Filter Pressure Delta |  | wheel(\d{0,4})ReturnFilterPressureDelta | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | wheel,return,air,filter,pressure,delta,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released)
wheelReturnFilterRuntime | wheelXXXXReturnFilterRuntime | Wheel Return Filter Runtime | Wheel XX Return Filter Runtime |  | wheel(\d{0,4})ReturnFilterRuntime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.15 (Released),2.16 (Pre-Release)
wheelReturnFlow | wheelXXXXReturnFlow | Wheel Return Flow | Wheel XX Return Flow |  | wheel(\d{0,4})ReturnFlow | Yes | Yes | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | wheel,return,air,flow,sensor | AFMS,AHU,CRAC,CRAH,CU,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelReturnHumidity | wheelXXXXReturnHumidity | Wheel Return Humidity | Wheel XX Return Humidity |  | wheel(\d{0,4})ReturnHumidity | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | wheel,return,air,humidity,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelReturnIsoDamper | wheelXXXXReturnIsoDamper | Wheel Return Isolation Damper Command | Wheel XX Return Isolation Damper Command |  | wheel(\d{0,4})ReturnIsoDamper | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | wheel,return,iso,air,damper,status,cmd | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelReturnIsoDamperFb | wheelXXXXReturnIsoDamperFb | Wheel Return Isolation Damper Feedback | Wheel XX Return Isolation Damper Feedback |  | wheel(\d{0,4})ReturnIsoDamperFb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | wheel,return,iso,air,damper,status,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelReturnPressure | wheelXXXXReturnPressure | Wheel Return Pressure | Wheel XX Return Pressure |  | wheel(\d{0,4})ReturnPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | wheel,return,air,static,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelReturnTemp | wheelXXXXReturnTemp | Wheel Return Temperature | Wheel XX Return Temperature |  | wheel(\d{0,4})ReturnTemp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | wheel,return,air,temp,sensor | AFMS,AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelReturnVelPressure | wheelXXXXReturnVelPressure | Wheel Return Velocity Pressure | Wheel XX Return Velocity Pressure |  | wheel(\d{0,4})ReturnVelPressure | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 2 | 1 |  |  | wheel,return,air,dynamic,pressure,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelReturnVOC | wheelXXXXReturnVOC | Wheel Return VOC | Wheel XX Return VOC |  | wheel(\d{0,4})ReturnVOC | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | wheel,return,air,voc,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelRuntime | wheelXXXXRuntime | Wheel Runtime | Wheel XX Runtime |  | wheel(\d{0,4})Runtime | No | No | No | Number |  |  | hour | hour | 1 | 1 |  |  | blacklist | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.15 (Released),2.16 (Pre-Release)
wheelSpeed | wheelXXXXSpeed | Wheel Speed | Wheel XX Speed |  | wheel(\d{0,4})Speed | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | common,wheel,speed,cmd | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelSpeedFb | wheelXXXXSpeedFb | Wheel Speed Feedback | Wheel XX Speed Feedback |  | wheel(\d{0,4})SpeedFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | common,wheel,speed,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelSpeedMaxSp | wheelXXXXSpeedMaxSp | Wheel Speed Max Setpoint | Wheel XX Speed Max Setpoint |  | wheel(\d{0,4})SpeedMaxSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | common,wheel,speed,max,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelSpeedMinSp | wheelXXXXSpeedMinSp | Wheel Speed Min Setpoint | Wheel XX Speed Min Setpoint |  | wheel(\d{0,4})SpeedMinSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | common,wheel,speed,min,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelSpeedOvr | wheelXXXXSpeedOvr | Wheel Speed Override | Wheel XX Speed Override |  | wheel(\d{0,4})SpeedOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | common,wheel,speed,ovr | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelSpeedSp | wheelXXXXSpeedSp | Wheel Speed Setpoint | Wheel XX Speed Setpoint |  | wheel(\d{0,4})SpeedSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | common,wheel,speed,effective,sp | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelStatus | wheelXXXXStatus | Wheel Status | Wheel XX Status |  | wheel(\d{0,4})Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | common,wheel,status,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
wheelTorque | wheelXXXXTorque | Wheel Torque | Wheel XX Torque |  | wheel(\d{0,4})Torque | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | common,wheel,torque,sensor | AHU,CRAC,CRAH,DHU,DOAS,ERU,HP,HRU,RTU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
windowClosedOvr | windowXXXXClosedOvr | Window Closed Override | Window XX Closed Override |  | window(\d{0,4})ClosedOvr | No | No | No | Bool | Closed/Auto | Closed/Auto | [6 empty] | window,closed,ovr | WNDW | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
window | windowXXXX | Window Command | Window XX Command |  | window(\d{0,4}) | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | window,status,cmd | WNDW | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
windowFb | windowXXXXFb | Window Feedback | Window XX Feedback |  | window(\d{0,4})Fb | Yes | Yes | No | Bool | Open/Closed | Open/Closed | percent | percent | 1 | 1 |  |  | window,status,sensor | WNDW | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
windowSpManual | windowXXXXSpManual | Window Manual Setpoint | Window XX Manual Setpoint |  | window(\d{0,4})SpManual | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | window,manual,sp | WNDW | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
windowOpenOvr | windowXXXXOpenOvr | Window Open Override | Window XX Open Override |  | window(\d{0,4})OpenOvr | No | No | No | Bool | Open/Auto | Open/Auto | [6 empty] | window,open,ovr | WNDW | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
windowSp | windowSp | Window Setpoint | Window Setpoint |  | windowSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | window,effective,sp | WNDW | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCoolSp | zoneCoolSp | Zone Active Cool Setpoint | Zone Active Cool Setpoint |  | zoneCoolSp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,temp,active,cool,common,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCoolSpOffset | zoneCoolSpOffset | Zone Active Cool Setpoint Offset | Zone Active Cool Setpoint Offset |  | zoneCoolSpOffset | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | zone,air,temp,active,cool,offset,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCoolSpOvr | zoneCoolSpOvr | Zone Active Cool Setpoint Override | Zone Active Cool Setpoint Override |  | zoneCoolSpOvr | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,temp,active,cool,spOvr | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneHeatSp | zoneHeatSp | Zone Active Heat Setpoint | Zone Active Heat Setpoint |  | zoneHeatSp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,temp,active,heat,common,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneHeatSpOffset | zoneHeatSpOffset | Zone Active Heat Setpoint Offset | Zone Active Heat Setpoint Offset |  | zoneHeatSpOffset | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | zone,air,temp,active,heat,offset,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneHeatSpOvr | zoneHeatSpOvr | Zone Active Heat Setpoint Override | Zone Active Heat Setpoint Override |  | zoneHeatSpOvr | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,temp,active,heat,spOvr | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneAlarm | zoneXXXXAlarm | Zone Alarm | Zone XX Alarm |  | zone(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,light,alarm | LTGE,LTGI,MSC,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCH4 | zoneCH4XXXX | Zone CH4 | Zone CH4 XX |  | zoneCH4(\d{0,4}) | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,ch4,sensor | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MMS,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCH4Alarm | zoneCH4XXXXAlarm | Zone CH4 Alarm | Zone CH4 XX Alarm |  | zoneCH4(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,ch4,common,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MMS,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCH4LevelAlarm | zoneCH4XXXXLevelYYYYAlarm | Zone CH4 Level Alarm | Zone CH4 XX Level YY Alarm |  | zoneCH4(\d{0,4})Level(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,ch4,level,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MMS,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCL2 | zoneCL2XXXX | Zone CL2 | Zone CL2 XX |  | zoneCL2(\d{0,4}) | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,cl2,sensor | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCL2LevelAlarm | zoneCL2XXXXLevelYYYYAlarm | Zone CL2 Level Alarm | Zone CL2 XX Level YY Alarm |  | zoneCL2(?:(\d{0,4})?)Level(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,cl2,level,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCO | zoneCOXXXX | Zone CO | Zone CO XX |  | zoneCO(?:(?!2)(\d{0,4})?) | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,co,sensor | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCOAlarm | zoneCOXXXXAlarm | Zone CO Alarm | Zone CO XX Alarm |  | zoneCO(?:(?!2)(\d{0,4})?)Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,co,common,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCODb | zoneCOXXXXDb | Zone CO Deadband | Zone CO XX Deadband |  | zoneCO(?:(?!2)(\d{0,4})?)Db | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,co,deadband,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCOHiAlarm | zoneCOXXXXHiAlarm | Zone CO High Alarm | Zone CO XX High Alarm |  | zoneCO(?:(?!2)(\d{0,4})?)HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,co,high,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCOHiSp | zoneCOXXXXHiSp | Zone CO High Setpoint | Zone CO XX High Setpoint |  | zoneCO(?:(?!2)(\d{0,4})?)HiSp | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,co,high,sp,active | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.14,2.15 (Released),2.16 (Pre-Release)
zoneCOLevelAlarm | zoneCOXXXXLevelYYYYAlarm | Zone CO Level Alarm | Zone CO XX Level YY Alarm |  | zoneCO(?:(?!2)(\d{0,4})?)Level(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,co,level,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCOLevelHiSp | zoneCOXXXXLevelYYYYHiSp | Zone CO Level High Setpoint | Zone CO XX Level YY High Setpoint |  | zoneCO(?:(?!2)(\d{0,4})?)Level(\d{0,4})HiSp | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,co,level,high,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.14,2.15 (Released),2.16 (Pre-Release)
zoneCOLoAlarm | zoneCOXXXXLoAlarm | Zone CO Low Alarm | Zone CO XX Low Alarm |  | zoneCO(?:(?!2)(\d{0,4})?)LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,co,low,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCOLoSp | zoneCOXXXXLoSp | Zone CO Low Setpoint | Zone CO XX Low Setpoint |  | zoneCO(?:(?!2)(\d{0,4})?)LoSp | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,co,low,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCOMax | zoneCOXXXXMax | zone CO Max | Zone CO XX Max |  | zoneCO(?:(?!2)(\d{0,4})?)Max | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,co,max,calc | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.15 (Released),2.16 (Pre-Release)
zoneCOMaxSp | zoneCOXXXXMaxSp | Zone CO Max Setpoint | Zone CO XX Max Setpoint |  | zoneCO(?:(?!2)(\d{0,4})?)MaxSp | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,co,max,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCOMinSp | zoneCOXXXXMinSp | Zone CO Min Setpoint | Zone CO XX Min Setpoint |  | zoneCO(?:(?!2)(\d{0,4})?)MinSp | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,co,min,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCOSp | zoneCOXXXXSp | Zone CO Setpoint | Zone CO XX Setpoint |  | zoneCO(?:(?!2)(\d{0,4})?)Sp | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,co,effective,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCO2 | zoneCO2XXXX | Zone CO2 | Zone CO2 XX |  | zoneCO2(?:(\d{0,4})?) | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,co2,sensor | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCO2Avg | zoneCO2Avg | Zone CO2 (Average) | Zone CO2 (Average) |  | zoneCO2Avg | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,co2,avg,calc | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.15 (Released),2.16 (Pre-Release)
zoneCO2Alarm | zoneCO2XXXXAlarm | Zone CO2 Alarm | Zone CO2 XX Alarm |  | zoneCO2(?:(\d{0,4})?)Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,co2,common,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCO2SpBAS | zoneCO2XXXXSpBAS | Zone CO2 BAS Setpoint | Zone CO2 XX BAS Setpoint |  | zoneCO2(?:(\d{0,4})?)SpBAS | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,co2,bas,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCO2Db | zoneCO2XXXXDb | Zone CO2 Deadband | Zone CO2 XX Deadband |  | zoneCO2(?:(\d{0,4})?)Db | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,co2,deadband,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCO2Fault | zoneCO2XXXXFault | Zone CO2 Fault | Zone CO2 XX Fault |  | zoneCO2(?:(\d{0,4})?)Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | zone,air,co2,fault | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCO2HiAlarm | zoneCO2XXXXHiAlarm | Zone CO2 High Alarm | Zone CO2 XX High Alarm |  | zoneCO2(?:(\d{0,4})?)HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,co2,high,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCO2HiSp | zoneCO2XXXXHiSp | Zone CO2 High Setpoint | Zone CO2 XX High Setpoint |  | zoneCO2(?:(\d{0,4})?)HiSp | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,co2,high,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCO2LevelAlarm | zoneCO2XXXXLevelYYYYAlarm | Zone CO2 Level Alarm | Zone CO2 XX Level YY Alarm |  | zoneCO2(?:(\d{0,4})?)Level(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,co2,level,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCO2SpLocal | zoneCO2XXXXSpLocal | Zone CO2 Local Setpoint | Zone CO2 XX Local Setpoint |  | zoneCO2(?:(\d{0,4})?)SpLocal | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,co2,local,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCO2LoAlarm | zoneCO2XXXXLoAlarm | Zone CO2 Low Alarm | Zone CO2 XX Low Alarm |  | zoneCO2(?:(\d{0,4})?)LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,co2,low,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCO2LoSp | zoneCO2XXXXLoSp | Zone CO2 Low Setpoint | Zone CO2 XX Low Setpoint |  | zoneCO2(?:(\d{0,4})?)LoSp | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,co2,low,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCO2Max | zoneCO2XXXXMax | Zone CO2 Max | Zone CO2 XX Max |  | zoneCO2(?:(\d{0,4})?)Max | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,co2,max,calc | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCO2MaxSp | zoneCO2XXXXMaxSp | Zone CO2 Max Setpoint | Zone CO2 XX Max Setpoint |  | zoneCO2(?:(\d{0,4})?)MaxSp | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,co2,max,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCO2MinSp | zoneCO2XXXXMinSp | Zone CO2 Min Setpoint | Zone CO2 XX Min Setpoint |  | zoneCO2(?:(\d{0,4})?)MinSp | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,co2,min,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCO2Sp | zoneCO2XXXXSp | Zone CO2 Setpoint | Zone CO2 XX Setpoint |  | zoneCO2(?:(\d{0,4})?)Sp | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,co2,effective,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zone | zoneXXXX | Zone Command | Zone XX Command |  | zone(\d{0,4}) | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | zone,light,status,cmd | LTGE,LTGI,MSC,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCoolingDemand | zoneCoolingDemand | Zone Cooling Demand | Zone Cooling Demand |  | zoneCoolingDemand | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | zone,air,cool,load,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCoolingReq | zoneCoolingReq | Zone Cooling Request | Zone Cooling Request |  | zoneCoolingReq | No | No | No | Bool | Request/No Request | Request/No Request | [6 empty] | zone,air,cool,request,cmd | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCoolingReqCount | zoneCoolingReqCount | Zone Cooling Request Count | Zone Cooling Request Count |  | zoneCoolingReqCount | Yes | Yes | No | Number |  |  |  |  | 0 | 0 |  |  | zone,air,cool,request,count | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCoolingReqDb | zoneCoolingReqDb | Zone Cooling Request Deadband | Zone Cooling Request Deadband |  | zoneCoolingReqDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | zone,air,cool,request,deadband,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCoolingReqDelayOffSp | zoneCoolingReqDelayOffSp | Zone Cooling Request Delay-Off Setpoint | Zone Cooling Request Delay-Off Setpoint |  | zoneCoolingReqDelayOffSp | No | No | No | Number |  |  | minute | minute | 0 | 0 |  |  | zone,air,cool,request,delay,off,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCoolingReqDelayOnSp | zoneCoolingReqDelayOnSp | Zone Cooling Request Delay-On Setpoint | Zone Cooling Request Delay-On Setpoint |  | zoneCoolingReqDelayOnSp | No | No | No | Number |  |  | minute | minute | 0 | 0 |  |  | zone,air,cool,request,delay,on,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCoolingReqDelayOnOffSp | zoneCoolingReqDelayOnOffSp | Zone Cooling Request Delay-On/Off Setpoint | Zone Cooling Request Delay-On/Off Setpoint |  | zoneCoolingReqDelayOnOffSp | No | No | No | Number |  |  | minute | minute | 0 | 0 |  |  | zone,air,cool,request,delay,onOff,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneCoolingReqSp | zoneCoolingReqSp | Zone Cooling Request Setpoint | Zone Cooling Request Setpoint |  | zoneCoolingReqSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,cool,request,effective,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneDischargeDamperMax | zoneDischargeDamperMax | Zone Damper Position Maximum | Zone Damper Position Maximum |  | zoneDischargeDamperMax | Yes | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | zone,entering,damper,max,air,position,calc | AHU,ATU,DHU,DOAS,ERU,HP,HRU,MAU,MSC,RTU,HP | 2.14,2.15 (Released),2.16 (Pre-Release)
zoneDehumidDb | zoneDehumidXXXXDb | Zone Dehumidification Deadband | Zone Dehumidification XX Deadband |  | zoneDehumid(\d{0,4})Db | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | zone,air,dehumid,deadband,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneDehumidMaxSp | zoneDehumidXXXXMaxSp | Zone Dehumidification Max Reset Setpoint | Zone Dehumidification XX Max Reset Setpoint |  | zoneDehumid(\d{0,4})MaxSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | zone,air,dehumid,max,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneDehumidMinSp | zoneDehumidXXXXMinSp | Zone Dehumidification Min Reset Setpoint | Zone Dehumidification XX Min Reset Setpoint |  | zoneDehumid(\d{0,4})MinSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | zone,air,dehumid,min,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneDehumidSp | zoneDehumidXXXXSp | Zone Dehumidification Setpoint | Zone Dehumidification XX Setpoint |  | zoneDehumid(\d{0,4})Sp | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | zone,air,dehumid,effective,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneDehumidSpOvr | zoneDehumidXXXXSpOvr | Zone Dehumidification Setpoint Override | Zone Dehumidification XX Setpoint Override |  | zoneDehumid(\d{0,4})SpOvr | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | zone,air,dehumid,effective,spOvr | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneDCVReqCount | zoneDCVReqCount | Zone Demand Control Ventilation Request Count | Zone Demand Control Ventilation Request Count |  | zoneDCVReqCount | Yes | Yes | No | Number |  |  |  |  | 0 | 0 |  |  | zone,request,count,calc,demand,ventilation | AHU,ATU,DHU,DOAS,ERU,HP,HRU,MAU,MSC,RTU,HP | 2.14,2.15 (Released),2.16 (Pre-Release)
zoneDewpoint | zoneDewpointXXXX | Zone Dewpoint | Zone Dewpoint XX |  | zoneDewpoint(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,dewpoint,sensor | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneDewpointSp | zoneDewpointXXXXSp | Zone Dewpoint Setpoint | Zone Dewpoint XX Setpoint |  | zoneDewpoint(\d{0,4})Sp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,dewpoint,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneDimmer | zoneXXXXDimmer | Zone Dimmer Command | Zone XX Dimmer Command |  | zone(\d{0,4})Dimmer | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | zone,dimmer,cmd | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneDimLevel | zoneXXXXDimLevel | Zone Dimming Level Command | Zone XX Dimming Level Command |  | zone(\d{0,4})DimLevel | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | zone,dimming,cmd | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneDimLevelFb | zoneXXXXDimLevelFb | Zone Dimming Level Feedback | Zone XX Dimming Level Feedback |  | zone(\d{0,4})DimLevelFb | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | zone,dimming,sensor | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneDimLevelOvr | zoneXXXXDimLevelOvr | Zone Dimming Level Override | Zone XX Dimming Level Override |  | zone(\d{0,4})DimLevelOvr | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | zone,dimming,ovr | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneDimLevelSp | zoneXXXXDimLevelSp | Zone Dimming Level Setpoint | Zone XX Dimming Level Setpoint |  | zone(\d{0,4})DimLevelSp | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | zone,dimming,sp | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneDisableSp | zoneDisableSp | Zone Disable Setpoint | Zone Disable Setpoint |  | zoneDisableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | zone,disable,sp | LTGE,LTGI,ZN | 2.15 (Released),2.16 (Pre-Release)
zoneDischargeFlow | zoneDischargeFlow | Zone Discharge Flow | Zone Discharge Flow |  | zoneDischargeFlow | Yes | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | zone,air,flowConsumption,sensor,entering,flow | AHU,ATU,DHU,DOAS,ERU,HP,HRU,MAU,MSC,RTU,HP | 2.14,2.15 (Released),2.16 (Pre-Release)
zoneDischargeFlowSp | zoneDischargeFlowSp | Zone Discharge Flow Setpoint | Zone Discharge Flow Setpoint |  | zoneDischargeFlowSp | Yes | No | No | Number |  |  | cubic_feet_per_minute | liters_per_second | 0 | 0 |  |  | zone,air,flowConsumption,reset,entering,flow | AHU,ATU,DHU,DOAS,ERU,HP,HRU,MAU,MSC,RTU,HP | 2.14,2.15 (Released),2.16 (Pre-Release)
zoneEnable | zoneEnable | Zone Enable Command | Zone Enable Command |  | zoneEnable | Yes | Yes | No | Bool | Enabled/Disabled | Enabled/Disabled | [6 empty] | zone,enable,cmd | LTGE,LTGI,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneEnableDb | zoneEnableDb | Zone Enable Deadband | Zone Enable Deadband |  | zoneEnableDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | zone,enable,deadband,sp | LTGE,LTGI,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneEnableReqCount | zoneEnableReqCount | Zone Enable Request Count | Zone Enable Request Count |  | zoneEnableReqCount | No | No | No | Number |  |  |  |  | 0 | 0 |  |  | zone,enable,request,count,calc | LTGE,LTGI,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneEnableReqCountSp | zoneEnableReqCountSp | Zone Enable Request Count Setpoint | Zone Enable Request Count Setpoint |  | zoneEnableReqCountSp | No | No | No | Number |  |  |  |  | 0 | 0 |  |  | zone,enable,request,count,sp | LTGE,LTGI,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneEnableSp | zoneEnableSp | Zone Enable Setpoint | Zone Enable Setpoint |  | zoneEnableSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | zone,enable,effective,sp | LTGE,LTGI,ZN | 2.15 (Released),2.16 (Pre-Release)
zoneEnergy | zoneXXXXEnergy | Zone Energy | Zone XX Energy |  | zone(\d{0,4})Energy | Yes | Yes | Yes | Number |  |  | kilowatt_hour | kilowatt_hour | 0 | 0 |  |  | zone,energy,sensor | LTGE,LTGI,MSC,ZN | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneEnthalpy | zoneEnthalpyXXXX | Zone Enthalpy | Zone Enthalpy XX |  | zoneEnthalpy(\d{0,4}) | Yes | Yes | No | Number |  |  | btu_per_pound | kilojoules_per_kilogram | 1 | 1 |  |  | zone,air,enthalpy,sensor | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneGasLevelAlarm | zoneGasXXXXLevelYYYYAlarm | Zone Gas Level Alarm | Zone Gas XX Level YY Alarm |  | zoneGas(\d{0,4})Level(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,gas,level,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneH2 | zoneH2XXXX | Zone H2 | Zone H2 XX |  | zoneH2(\d{0,4}) | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | zone,air,h2,sensor | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneH2Alarm | zoneH2XXXXAlarm | Zone H2 Alarm | Zone H2 XX Alarm |  | zoneH2(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,h2,common,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HDS,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneH2Fault | zoneH2XXXXFault | Zone H2 Fault | Zone H2 XX Fault |  | zoneH2(\d{0,4})Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | zone,air,h2,fault | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HDS,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneH2FlameAlarm | zoneH2XXXXFlameAlarm | Zone H2 Flame Alarm | Zone H2 XX Flame Alarm |  | zoneH2(\d{0,4})FlameAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,h2,flame,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneH2LevelAlarm | zoneH2XXXXLevelYYYYAlarm | Zone H2 Level Alarm | Zone H2 XX Level YY Alarm |  | zoneH2(\d{0,4})Level(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,h2,level,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HDS,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneH2SystemAlarm | zoneH2XXXXSystemAlarm | Zone H2 System Alarm | Zone H2 XX System Alarm |  | zoneH2(\d{0,4})SystemAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,h2,system,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneH2S | zoneH2SXXXX | Zone H2S | Zone H2S XX |  | zoneH2S(\d{0,4}) | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,h2s,sensor | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneH2SLevelAlarm | zoneH2SXXXXLevelYYYYAlarm | Zone H2S Level Alarm | Zone H2S XX Level YY Alarm |  | zoneH2S(?:(\d{0,4})?)Level(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,h2s,level,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneHeatIndex | zoneHeatIndexXXXX | Zone Heat Index | Zone Heat Index XX |  | zoneHeatIndex(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,heatIndex,sensor | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneHeatingDemand | zoneHeatingDemand | Zone Heating Demand | Zone Heating Demand |  | zoneHeatingDemand | Yes | Yes | No | Number |  |  | percent | percent | 1 | 1 |  |  | zone,air,heat,load,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneHeatingReq | zoneHeatingReq | Zone Heating Request | Zone Heating Request |  | zoneHeatingReq | No | No | No | Bool | Request/No Request | Request/No Request | [6 empty] | zone,air,heat,request,cmd | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneHeatingReqCount | zoneHeatingReqCount | Zone Heating Request Count | Zone Heating Request Count |  | zoneHeatingReqCount | Yes | Yes | No | Number |  |  |  |  | 0 | 0 |  |  | zone,air,heat,request,count | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneHeatingReqDb | zoneHeatingReqDb | Zone Heating Request Deadband | Zone Heating Request Deadband |  | zoneHeatingReqDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | zone,air,heat,request,deadband,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneHeatingReqDelayOffSp | zoneHeatingReqDelayOffSp | Zone Heating Request Delay Off Setpoint | Zone Heating Request Delay Off Setpoint |  | zoneHeatingReqDelayOffSp | No | No | No | Number |  |  | minute | minute | 0 | 0 |  |  | zone,air,heat,request,delay,off,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneHeatingReqDelayOnOffSp | zoneHeatingReqDelayOnOffSp | Zone Heating Request Delay On Off Setpoint | Zone Heating Request Delay On Off Setpoint |  | zoneHeatingReqDelayOnOffSp | No | No | No | Number |  |  | minute | minute | 0 | 0 |  |  | zone,air,heat,request,delay,onOff,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneHeatingReqDelayOnSp | zoneHeatingReqDelayOnSp | Zone Heating Request Delay On Setpoint | Zone Heating Request Delay On Setpoint |  | zoneHeatingReqDelayOnSp | No | No | No | Number |  |  | minute | minute | 0 | 0 |  |  | zone,air,heat,request,delay,on,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneHeatingReqSp | zoneHeatingReqSp | Zone Heating Request Setpoint | Zone Heating Request Setpoint |  | zoneHeatingReqSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,heat,request,effective,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneHumidHiSp | zoneHumidXXXXHiSp | Zone Humidification High Setpoint | Zone Humidification XX High Setpoint |  | zoneHumid(\d{0,4})HiSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | zone,air,humid,high,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneHumidLoSp | zoneHumidXXXXLoSp | Zone Humidification Low Setpoint | Zone Humidification XX Low Setpoint |  | zoneHumid(\d{0,4})LoSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | zone,air,humid,low,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneHumidMaxSp | zoneHumidXXXXMaxSp | Zone Humidification Max Setpoint | Zone Humidification XX Max Setpoint |  | zoneHumid(\d{0,4})MaxSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | zone,air,humid,max,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneHumidMinSp | zoneHumidXXXXMinSp | Zone Humidification Min Setpoint | Zone Humidification XX Min Setpoint |  | zoneHumid(\d{0,4})MinSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | zone,air,humid,min,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneHumidSp | zoneHumidXXXXSp | Zone Humidification Setpoint | Zone Humidification XX Setpoint |  | zoneHumid(\d{0,4})Sp | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | zone,air,humid,effective,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneHumidity | zoneHumidityXXXX | Zone Humidity | Zone Humidity XX |  | zoneHumidity(\d{0,4}) | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | zone,air,humidity,sensor | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneHumidityAvg | zoneHumidityAvg | Zone Humidity (Average) | Zone Humidity (Average) |  | zoneHumidityAvg | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | zone,air,humidity,avg,calc | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.15 (Released),2.16 (Pre-Release)
zoneHumidityCoolSp | zoneHumidityXXXXCoolSp | Zone Humidity Cool Setpoint | Zone Humidity XX Cool Setpoint |  | zoneHumidity(\d{0,4})CoolSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | zone,air,humidity,cool,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneHumidityDb | zoneHumidityXXXXDb | Zone Humidity Deadband | Zone Humidity XX Deadband |  | zoneHumidity(\d{0,4})Db | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | zone,air,humidity,deadband,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneHumidityFault | zoneHumidityXXXXFault | Zone Humidity Fault | Zone Humidity XX Fault |  | zoneHumidity(\d{0,4})Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | zone,air,humidity,fault | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneHumidityHeatSp | zoneHumidityXXXXHeatSp | Zone Humidity Heat Septoint | Zone Humidity XX Heat Septoint |  | zoneHumidity(\d{0,4})HeatSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | zone,air,humidity,heat,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneHumidityHiAlarm | zoneHumidityXXXXHiAlarm | Zone Humidity High Alarm | Zone Humidity XX High Alarm |  | zoneHumidity(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,humidity,high,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneHumidityHiSp | zoneHumidityXXXXHiSp | Zone Humidity High Setpoint | Zone Humidity XX High Setpoint |  | zoneHumidity(\d{0,4})HiSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | zone,air,humidity,high,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneHumidityLoAlarm | zoneHumidityXXXXLoAlarm | Zone Humidity Low Alarm | Zone Humidity XX Low Alarm |  | zoneHumidity(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,humidity,low,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneHumidityLoSp | zoneHumidityXXXXLoSp | Zone Humidity Low Setpoint | Zone Humidity XX Low Setpoint |  | zoneHumidity(\d{0,4})LoSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | zone,air,humidity,low,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneHumidityMaxSp | zoneHumidityXXXXMaxSp | Zone Humidity Max Reset Setpoint | Zone Humidity XX Max Reset Setpoint |  | zoneHumidity(\d{0,4})MaxSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | zone,air,humidity,max,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneHumidityMinSp | zoneHumidityXXXXMinSp | Zone Humidity Min Reset Setpoint | Zone Humidity XX Min Reset Setpoint |  | zoneHumidity(\d{0,4})MinSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | zone,air,humidity,min,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneHumiditySp | zoneHumidityXXXXSp | Zone Humidity Setpoint | Zone Humidity XX Setpoint |  | zoneHumidity(\d{0,4})Sp | Yes | Yes | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | zone,air,humidity,effective,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneHumiditySummerSp | zoneHumiditySummerSp | Zone Humidity Summer Setpoint | Zone Humidity Summer Setpoint |  | zoneHumiditySummerSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | zone,air,humidity,summer,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneHumidityWinterSp | zoneHumidityWinterSp | Zone Humidity Winter Setpoint | Zone Humidity Winter Setpoint |  | zoneHumidityWinterSp | No | No | No | Number |  |  | percent_relative_humidity | percent_relative_humidity | 1 | 1 |  |  | zone,air,humidity,winter,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneLightLevel | zoneXXXXLightLevelYYYY | Zone Light Level | Zone XX Light Level YY |  | zone(\d{0,4})LightLevel(\d{0,4}) | Yes | Yes | No | Number |  |  | footcandle | lux | 0 | 0 |  |  | zone,lightLevel,sensor | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneLightLevelMaxSp | zoneXXXXLightLevelYYYYMaxSp | Zone Light Level Max Setpoint | Zone XX Light Level YY Max Setpoint |  | zone(\d{0,4})LightLevel(\d{0,4})MaxSp | No | No | No | Number |  |  | footcandle | lux | 0 | 0 |  |  | zone,lightLevel,max,sp | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneLightLevelMinSp | zoneXXXXLightLevelYYYYMinSp | Zone Light Level Min Setpoint | Zone XX Light Level YY Min Setpoint |  | zone(\d{0,4})LightLevel(\d{0,4})MinSp | No | No | No | Number |  |  | footcandle | lux | 0 | 0 |  |  | zone,lightLevel,min,sp | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneLightLevelSp | zoneXXXXLightLevelYYYYSp | Zone Light Level Setpoint | Zone XX Light Level YY Setpoint |  | zone(\d{0,4})LightLevel(\d{0,4})Sp | Yes | Yes | No | Number |  |  | footcandle | lux | 0 | 0 |  |  | zone,lightLevel,effective,sp | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneLPGAlarm | zoneLPGXXXXAlarm | Zone LPG Alarm | Zone LPG XX Alarm |  | zoneLPG(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,lpg,common,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneLPGFaultCode | zoneLPGXXXXFaultCode | Zone LPG Fault Code | Zone LPG XX Fault Code |  | zoneLPG(\d{0,4})FaultCode | Yes | Yes | No | Str | [8 empty] | zone,lpg,fault,code | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.15 (Released)
zoneN2 | zoneN2XXXX | Zone N2 | Zone N2 XX |  | zoneN2(\d{0,4}) | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,n2,sensor | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneN2Alarm | zoneN2XXXXAlarm | Zone N2 Alarm | Zone N2 XX Alarm |  | zoneN2(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,n2,common,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneN2Db | zoneN2XXXXDb | Zone N2 Deadband | Zone N2 XX Deadband |  | zoneN2(\d{0,4})Db | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,n2,deadband,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneN2HiAlarm | zoneN2XXXXHiAlarm | Zone N2 High Alarm | Zone N2 XX High Alarm |  | zoneN2(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,n2,high,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneN2HiSp | zoneN2XXXXHiSp | Zone N2 High Setpoint | Zone N2 XX High Setpoint |  | zoneN2(\d{0,4})HiSp | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,n2,high,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneN2LevelAlarm | zoneN2XXXXLevelYYYYAlarm | Zone N2 Level Alarm | Zone N2 XX Level YY Alarm |  | zoneN2(\d{0,4})Level(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,n2,level,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneN2LoAlarm | zoneN2XXXXLoAlarm | Zone N2 Low Alarm | Zone N2 XX Low Alarm |  | zoneN2(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,n2,low,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneN2LoSp | zoneN2XXXXLoSp | Zone N2 Low Setpoint | Zone N2 XX Low Setpoint |  | zoneN2(\d{0,4})LoSp | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,n2,low,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneN2MaxSp | zoneN2XXXXMaxSp | Zone N2 Max Setpoint | Zone N2 XX Max Setpoint |  | zoneN2(\d{0,4})MaxSp | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,n2,max,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneN2MinSp | zoneN2XXXXMinSp | Zone N2 Min Setpoint | Zone N2 XX Min Setpoint |  | zoneN2(\d{0,4})MinSp | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,n2,min,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneN2Sp | zoneN2XXXXSp | Zone N2 Setpoint | Zone N2 XX Setpoint |  | zoneN2(\d{0,4})Sp | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,n2,effective,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneNO | zoneNOXXXX | Zone NO | Zone NO XX |  | zoneNO(?:(?!2)(\d{0,4})?) | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,no,sensor | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneNOAlarm | zoneNOXXXXAlarm | Zone NO Alarm | Zone NO XX Alarm |  | zoneNO(?:(?!2)(\d{0,4})?)Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,no,common,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneNODb | zoneNOXXXXDb | Zone NO Deadband | Zone NO XX Deadband |  | zoneNO(?:(?!2)(\d{0,4})?)Db | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,no,deadband,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneNOHiAlarm | zoneNOXXXXHiAlarm | Zone NO High Alarm | Zone NO XX High Alarm |  | zoneNO(?:(?!2)(\d{0,4})?)HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,no,high,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneNOHiSp | zoneNOXXXXHiSp | Zone NO High Setpoint | Zone NO XX High Setpoint |  | zoneNO(?:(?!2)(\d{0,4})?)HiSp | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,no,high,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneNOLevelAlarm | zoneNOXXXXLevelYYYYAlarm | Zone NO Level Alarm | Zone NO XX Level YY Alarm |  | zoneNO(?:(?!2)(\d{0,4})?)Level(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,no,level,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneNOLoAlarm | zoneNOXXXXLoAlarm | Zone NO Low Alarm | Zone NO XX Low Alarm |  | zoneNO(?:(?!2)(\d{0,4})?)LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,no,low,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneNOLoSp | zoneNOXXXXLoSp | Zone NO Low Setpoint | Zone NO XX Low Setpoint |  | zoneNO(?:(?!2)(\d{0,4})?)LoSp | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,no,low,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneNOMaxSp | zoneNOXXXXMaxSp | Zone NO Max Setpoint | Zone NO XX Max Setpoint |  | zoneNO(?:(?!2)(\d{0,4})?)MaxSp | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,no,max,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneNOMinSp | zoneNOXXXXMinSp | Zone NO Min Setpoint | Zone NO XX Min Setpoint |  | zoneNO(?:(?!2)(\d{0,4})?)MinSp | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,no,min,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneNOSp | zoneNOXXXXSp | Zone NO Setpoint | Zone NO XX Setpoint |  | zoneNO(?:(?!2)(\d{0,4})?)Sp | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,no,effective,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneNO2 | zoneNO2XXXX | Zone NO2 | Zone NO2 XX |  | zoneNO2(?:(\d{0,4})?) | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,no2,sensor | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneNO2Alarm | zoneNO2XXXXAlarm | Zone NO2 Alarm | Zone NO2 XX Alarm |  | zoneNO2(?:(\d{0,4})?)Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,no2,common,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneNO2Db | zoneNO2XXXXDb | Zone NO2 Deadband | Zone NO2 XX Deadband |  | zoneNO2(?:(\d{0,4})?)Db | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,no2,deadband,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneNO2HiAlarm | zoneNO2XXXXHiAlarm | Zone NO2 High Alarm | Zone NO2 XX High Alarm |  | zoneNO2(?:(\d{0,4})?)HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,no2,high,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneNO2HiSp | zoneNO2XXXXHiSp | Zone NO2 High Setpoint | Zone NO2 XX High Setpoint |  | zoneNO2(?:(\d{0,4})?)HiSp | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,no2,high,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneNO2LevelAlarm | zoneNO2XXXXLevelYYYYAlarm | Zone NO2 Level Alarm | Zone NO2 XX Level YY Alarm |  | zoneNO2(?:(\d{0,4})?)Level(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,no2,level,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneNO2LoAlarm | zoneNO2XXXXLoAlarm | Zone NO2 Low Alarm | Zone NO2 XX Low Alarm |  | zoneNO2(?:(\d{0,4})?)LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,no2,low,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneNO2LoSp | zoneNO2XXXXLoSp | Zone NO2 Low Setpoint | Zone NO2 XX Low Setpoint |  | zoneNO2(?:(\d{0,4})?)LoSp | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,no2,low,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneNO2MaxSp | zoneNO2XXXXMaxSp | Zone NO2 Max Setpoint | Zone NO2 XX Max Setpoint |  | zoneNO2(?:(\d{0,4})?)MaxSp | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,no2,max,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneNO2MinSp | zoneNO2XXXXMinSp | Zone NO2 Min Setpoint | Zone NO2 XX Min Setpoint |  | zoneNO2(?:(\d{0,4})?)MinSp | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,no2,min,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneNO2Sp | zoneNO2XXXXSp | Zone NO2 Setpoint | Zone NO2 XX Setpoint |  | zoneNO2(?:(\d{0,4})?)Sp | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,no2,effective,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneNoiseLevel | zoneNoiseLevel | Zone Noise Level | Zone Noise Level |  | zoneNoiseLevel | Yes | Yes | No | Number |  |  | decibel | decibel | 1 | 1 |  |  | zone,noise,sensor | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneO2 | zoneO2XXXX | Zone O2 | Zone O2 XX |  | zoneO2(\d{0,4}) | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,o2,sensor | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneO2Alarm | zoneO2XXXXAlarm | Zone O2 Alarm | Zone O2 XX Alarm |  | zoneO2(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,o2,common,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneO2LevelAlarm | zoneO2XXXXLevelYYYYAlarm | Zone O2 Level Alarm | Zone O2 XX Level YY Alarm |  | zoneO2(\d{0,4})Level(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,o2,level,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneOffCmd | zoneXXXXOffCmd | Zone Off Command | Zone XX Off Command |  | zone(\d{0,4})OffCmd | Yes | Yes | No | Bool | Off/Auto | Off/Auto | [6 empty] | zone,light,off,cmd | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneOnCmd | zoneXXXXOnCmd | Zone On Command | Zone XX On Command |  | zone(\d{0,4})OnCmd | Yes | Yes | No | Bool | On/Auto | On/Auto | [6 empty] | zone,light,on,cmd | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneOneThird | zoneXXXXOneThird | Zone One Third | Zone XX One Third |  | zone(\d{0,4})OneThird | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | zone,light,oneThird,cmd | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneOvr | zoneXXXXOvr | Zone Override | Zone XX Override |  | zone(\d{0,4})Ovr | No | No | No | Bool | On/Off | On/Off | [6 empty] | zone,light,status,ovr | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zonePM25 | zonePM25 | Zone Particulate Matter 2.5 | Zone Particulate Matter 2.5 |  | zonePM25 | Yes | Yes | No | Number |  |  | micrograms_per_cubic_meter | micrograms_per_cubic_meter | 1 | 1 |  |  | zone,air,pm25,sensor | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zonePM10 | zonePM10 | Zone Particulate Matter 10 | Zone Particulate Matter 10 |  | zonePM10 | Yes | Yes | No | Number |  |  | micrograms_per_cubic_meter | micrograms_per_cubic_meter | 1 | 1 |  |  | zone,air,pm10,sensor | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zonePressure | zonePressureXXXX | Zone Pressure (Space-to-Space) | Zone Pressure XX (Space-to-Space) |  | zonePressure(\d{0,4}) | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 3 | 1 |  |  | zone,air,pressure,sensor | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zonePressureDb | zonePressureXXXXDb | Zone Pressure Deadband | Zone Pressure XX Deadband |  | zonePressure(\d{0,4})Db | No | No | No | Number |  |  | inches_of_water | pascal | 3 | 1 |  |  | zone,air,pressure,effective,deadband,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zonePressureHiAlarm | zonePressureXXXXHiAlarm | Zone Pressure High Alarm | Zone Pressure XX High Alarm |  | zonePressure(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,static,pressure,high,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zonePressureHiSp | zonePressureXXXXHiSp | Zone Pressure High Setpoint | Zone Pressure XX High Setpoint |  | zonePressure(\d{0,4})HiSp | No | No | No | Number |  |  | inches_of_water | pascal | 3 | 1 |  |  | zone,air,static,pressure,high,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zonePressureLoAlarm | zonePressureXXXXLoAlarm | Zone Pressure Low Alarm | Zone Pressure XX Low Alarm |  | zonePressure(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,static,pressure,low,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zonePressureLoSp | zonePressureXXXXLoSp | Zone Pressure Low Setpoint | Zone Pressure XX Low Setpoint |  | zonePressure(\d{0,4})LoSp | No | No | No | Number |  |  | inches_of_water | pascal | 3 | 1 |  |  | zone,air,static,pressure,low,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zonePressureMaxSp | zonePressureXXXXMaxSp | Zone Pressure Max Reset Setpoint | Zone Pressure XX Max Reset Setpoint |  | zonePressure(\d{0,4})MaxSp | No | No | No | Number |  |  | inches_of_water | pascal | 3 | 1 |  |  | zone,air,static,pressure,max,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zonePressureMinSp | zonePressureXXXXMinSp | Zone Pressure Min Reset Setpoint | Zone Pressure XX Min Reset Setpoint |  | zonePressure(\d{0,4})MinSp | No | No | No | Number |  |  | inches_of_water | pascal | 3 | 1 |  |  | zone,air,static,pressure,min,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zonePressureOffDb | zonePressureOffDb | Zone Pressure Off Deadband | Zone Pressure Off Deadband |  | zonePressureOffDb | No | No | No | Number |  |  | inches_of_water | pascal | 3 | 1 |  |  | zone,air,pressure,off,deadband,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zonePressureOnDb | zonePressureOnDb | Zone Pressure On Deadband | Zone Pressure On Deadband |  | zonePressureOnDb | No | No | No | Number |  |  | inches_of_water | pascal | 3 | 1 |  |  | zone,air,pressure,on,deadband,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zonePressureReq | zonePressureReq | Zone Pressure Request | Zone Pressure Request |  | zonePressureReq | No | No | No | Bool | Request/No Request | Request/No Request | [6 empty] | zone,air,pressure,request,cmd | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zonePressureReqCount | zonePressureReqCount | Zone Pressure Request Count | Zone Pressure Request Count |  | zonePressureReqCount | Yes | Yes | No | Number |  |  |  |  | 0 | 0 |  |  | zone,air,pressure,request,count | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zonePressureReqDb | zonePressureReqDb | Zone Pressure Request Deadband | Zone Pressure Request Deadband |  | zonePressureReqDb | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | zone,air,pressure,request,deadband,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zonePressureReqDelayOffSp | zonePressureReqDelayOffSp | Zone Pressure Request Delay-Off Setpoint | Zone Pressure Request Delay-Off Setpoint |  | zonePressureReqDelayOffSp | No | No | No | Number |  |  | minute | minute | 0 | 0 |  |  | zone,air,pressure,request,delay,off,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zonePressureReqDelayOnSp | zonePressureReqDelayOnSp | Zone Pressure Request Delay-On Setpoint | Zone Pressure Request Delay-On Setpoint |  | zonePressureReqDelayOnSp | No | No | No | Number |  |  | minute | minute | 0 | 0 |  |  | zone,air,pressure,request,delay,on,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zonePressureReqDelayOnOffSp | zonePressureReqDelayOnOffSp | Zone Pressure Request Delay-On/Off Setpoint | Zone Pressure Request Delay-On/Off Setpoint |  | zonePressureReqDelayOnOffSp | No | No | No | Number |  |  | minute | minute | 0 | 0 |  |  | zone,air,pressure,request,delay,onOff,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zonePressureReqSp | zonePressureReqSp | Zone Pressure Request Setpoint | Zone Pressure Request Setpoint |  | zonePressureReqSp | No | No | No | Number |  |  | percent | percent | 1 | 1 |  |  | zone,air,pressure,request,effective,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zonePressureSp | zonePressureXXXXSp | Zone Pressure Setpoint | Zone Pressure XX Setpoint |  | zonePressure(\d{0,4})Sp | Yes | Yes | No | Number |  |  | inches_of_water | pascal | 3 | 1 |  |  | zone,air,pressure,common,effective,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zonePurge | zonePurge | Zone Purge Command | Zone Purge Command |  | zonePurge | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | zone,air,purge,status,cmd | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FP,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,SMEX,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zonePurgeStatus | zonePurgeStatus | Zone Purge Status | Zone Purge Status |  | zonePurgeStatus | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | zone,air,purge,status,sensor | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FP,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,SMEX,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zonePurgeSwitch | zonePurgeSwitch | Zone Purge Switch | Zone Purge Switch |  | zonePurgeSwitch | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | zone,air,purge,switch,cmd | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FP,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,SMEX,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneR11 | zoneR11XXXX | Zone R11 | Zone R11 XX |  | zoneR11((?!4)(\d{0,4})?) | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,r11,sensor | AC,AHU,ATU,CF,CLR,CRAC,CRAH,CUH,CWS,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,GEO,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,WS,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneR11LevelAlarm | zoneR11XXXXLevelYYYYAlarm | Zone R11 Level Alarm | Zone R11 XX Level YY Alarm |  | zoneR11(?:(?!4)(\d{0,4})?)Level(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,r11,level,alarm | AC,AHU,ATU,CF,CLR,CRAC,CRAH,CUH,CWS,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,GEO,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,WS,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneR22 | zoneR22XXXX | Zone R22 | Zone R22 XX |  | zoneR22(\d{0,4}) | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,r22,sensor | AC,AHU,ATU,CF,CLR,CRAC,CRAH,CUH,CWS,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,GEO,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,WS,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneR22LevelAlarm | zoneR22XXXXLevelYYYYAlarm | Zone R22 Level Alarm | Zone R22 XX Level YY Alarm |  | zoneR22(?:(\d{0,4})?)Level(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,r22,level,alarm | AC,AHU,ATU,CF,CLR,CRAC,CRAH,CUH,CWS,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,GEO,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,WS,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneR114 | zoneR114XXXX | Zone R114 | Zone R114 XX |  | zoneR114(\d{0,4}) | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,r114,sensor | AC,AHU,ATU,CF,CLR,CRAC,CRAH,CUH,CWS,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,GEO,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,WS,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneR114LevelAlarm | zoneR114XXXXLevelYYYYAlarm | Zone R114 Level Alarm | Zone R114 XX Level YY Alarm |  | zoneR114(?:(\d{0,4})?)Level(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,r114,level,alarm | AC,AHU,ATU,CF,CLR,CRAC,CRAH,CUH,CWS,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,GEO,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,WS,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneR123 | zoneR123XXXX | Zone R123 | Zone R123 XX |  | zoneR123(\d{0,4}) | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,r123,sensor | AC,AHU,ATU,CF,CLR,CRAC,CRAH,CUH,CWS,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,GEO,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,WS,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneR123LevelAlarm | zoneR123XXXXLevelYYYYAlarm | Zone R123 Level Alarm | Zone R123 XX Level YY Alarm |  | zoneR123(?:(\d{0,4})?)Level(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,r123,level,alarm | AC,AHU,ATU,CF,CLR,CRAC,CRAH,CUH,CWS,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,GEO,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,WS,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneR125 | zoneR125XXXX | Zone R125 | Zone R125 XX |  | zoneR125(\d{0,4}) | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,r125,sensor | AC,AHU,ATU,CF,CLR,CRAC,CRAH,CUH,CWS,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,GEO,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,WS,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneR125LevelAlarm | zoneR125XXXXLevelYYYYAlarm | Zone R125 Level Alarm | Zone R125 XX Level YY Alarm |  | zoneR125(?:(\d{0,4})?)Level(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,r125,level,alarm | AC,AHU,ATU,CF,CLR,CRAC,CRAH,CUH,CWS,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,GEO,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,WS,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneR134A | zoneR134AXXXX | Zone R134A | Zone R134A XX |  | zoneR134A(\d{0,4}) | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,r134a,sensor | AC,AHU,ATU,CF,CLR,CRAC,CRAH,CUH,CWS,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,GEO,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,WS,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneR134ALevelAlarm | zoneR134AXXXXLevelYYYYAlarm | Zone R134A Level Alarm | Zone R134A XX Level YY Alarm |  | zoneR134A(?:(\d{0,4})?)Level(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,r134a,level,alarm | AC,AHU,ATU,CF,CLR,CRAC,CRAH,CUH,CWS,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,GEO,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,WS,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneR410A | zoneR410AXXXX | Zone R410A | Zone R410A XX |  | zoneR410A(\d{0,4}) | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,r410a,sensor | AC,AHU,ATU,CF,CLR,CRAC,CRAH,CUH,CWS,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,GEO,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,WS,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneR410ALevelAlarm | zoneR410AXXXXLevelYYYYAlarm | Zone R410A Level Alarm | Zone R410A XX Level YY Alarm |  | zoneR410A(?:(\d{0,4})?)Level(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,r410a,level,alarm | AC,AHU,ATU,CF,CLR,CRAC,CRAH,CUH,CWS,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,GEO,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,WS,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneSO2 | zoneSO2XXXX | Zone SO2 | Zone SO2 XX |  | zoneSO2(\d{0,4}) | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,so2,sensor | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneSO2LevelAlarm | zoneSO2XXXXLevelYYYYAlarm | Zone SO2 Level Alarm | Zone SO2 XX Level YY Alarm |  | zoneSO2(?:(\d{0,4})?)Level(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,so2,level,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
standbyCoolSp | standbyCoolSp | Zone Standby Cool Setpoint | Zone Standby Cool Setpoint |  | standbyCoolSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,temp,standby,cool,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RP,RPC,RPF,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
standbyHeatSp | standbyHeatSp | Zone Standby Heat Setpoint | Zone Standby Heat Setpoint |  | standbyHeatSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,temp,standby,heat,sp | AHU,ATU,CRAC,CRAH,CUH,DH,DHU,DOAS,EC,FCU,FPB,HP,MAU,RP,RPC,RPF,RTU,UV,VAV,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneStatus | zoneXXXXStatus | Zone Status | Zone XX Status |  | zone(\d{0,4})Status | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | zone,light,status,sensor | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTemp | zoneTempXXXX | Zone Temperature | Zone Temperature XX |  | zoneTemp(\d{0,4}) | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,temp,sensor | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTempAvg | zoneTempAvg | Zone Temperature (Average) | Zone Temperature (Average) |  | zoneTempAvg | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,temp,avg,calc | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.15 (Released),2.16 (Pre-Release)
zoneTempSpBAS | zoneTempXXXXSpBAS | Zone Temperature BAS Setpoint | Zone Temperature XX BAS Setpoint |  | zoneTemp(\d{0,4})SpBAS | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,temp,active,bas,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTempCoolDb | zoneTempXXXXCoolDb | Zone Temperature Cooling Deadband | Zone Temperature XX Cooling Deadband |  | zoneTemp(\d{0,4})CoolDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | zone,air,temp,cool,deadband,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTempDb | zoneTempXXXXDb | Zone Temperature Deadband | Zone Temperature XX Deadband |  | zoneTemp(\d{0,4})Db | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | zone,air,temp,effective,deadband,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTempDbOvr | zoneTempXXXXDbOvr | Zone Temperature Deadband Override | Zone Temperature XX Deadband Override |  | zoneTemp(\d{0,4})DbOvr | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | zone,air,temp,effective,deadband,ovr | AC,AHU,ATU,CF,CRAC,CRAH,CU,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTempDelta | zoneTempXXXXDelta | Zone Temperature Delta | Zone Temperature XX Delta |  | zoneTemp(\d{0,4})Delta | Yes | Yes | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | zone,air,temp,delta | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTempFault | zoneTempXXXXFault | Zone Temperature Fault | Zone Temperature XX Fault |  | zoneTemp(\d{0,4})Fault | Yes | Yes | No | Bool | Fault/Normal | Fault/Normal | [6 empty] | zone,air,temp,fault | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTempHeatDb | zoneTempXXXXHeatDb | Zone Temperature Heating Deadband | Zone Temperature XX Heating Deadband |  | zoneTemp(\d{0,4})HeatDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | zone,air,temp,heat,deadband,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTempHiAlarm | zoneTempXXXXHiAlarm | Zone Temperature High Alarm | Zone Temperature XX High Alarm |  | zoneTemp(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,temp,high,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTempHiSp | zoneTempXXXXHiSp | Zone Temperature High Setpoint | Zone Temperature XX High Setpoint |  | zoneTemp(\d{0,4})HiSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,zone,air,temp,high,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTempSpLocal | zoneTempXXXXSpLocal | Zone Temperature Local Setpoint | Zone Temperature XX Local Setpoint |  | zoneTemp(\d{0,4})SpLocal | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,temp,active,local,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTempLoAlarm | zoneTempXXXXLoAlarm | Zone Temperature Low Alarm | Zone Temperature XX Low Alarm |  | zoneTemp(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,temp,low,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTempLoSp | zoneTempXXXXLoSp | Zone Temperature Low Setpoint | Zone Temperature XX Low Setpoint |  | zoneTemp(\d{0,4})LoSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,zone,air,temp,low,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTempMax | zoneTempXXXXMax | Zone Temperature Max | Zone Temperature XX Max |  | zoneTemp(\d{0,4})Max | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,temp,max,calc | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTempMaxSp | zoneTempXXXXMaxSp | Zone Temperature Max Setpoint | Zone Temperature XX Max Setpoint |  | zoneTemp(\d{0,4})MaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,zone,air,temp,max,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTempMin | zoneTempXXXXMin | Zone Temperature Min | Zone Temperature XX Min |  | zoneTemp(\d{0,4})Min | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,temp,min,calc | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTempMinSp | zoneTempXXXXMinSp | Zone Temperature Min Setpoint | Zone Temperature XX Min Setpoint |  | zoneTemp(\d{0,4})MinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | common,zone,air,temp,min,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTempSp | zoneTempXXXXSp | Zone Temperature Setpoint | Zone Temperature XX Setpoint |  | zoneTemp(\d{0,4})Sp | Yes | Yes | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,temp,active,effective,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTempSpOffset | zoneTempXXXXSpOffset | Zone Temperature Setpoint Offset | Zone Temperature XX Setpoint Offset |  | zoneTemp(\d{0,4})SpOffset | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | zone,air,temp,offset,effective,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTempSpOffsetDb | zoneTempXXXXSpOffsetDb | Zone Temperature Setpoint Offset Deadband | Zone Temperature XX Setpoint Offset Deadband |  | zoneTemp(\d{0,4})SpOffsetDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | zone,air,temp,offset,deadband,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTempSpOffsetHiSp | zoneTempXXXXSpOffsetHiSp | Zone Temperature Setpoint Offset High Setpoint | Zone Temperature XX Setpoint Offset High Setpoint |  | zoneTemp(\d{0,4})SpOffsetHiSp | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | zone,air,temp,offset,high,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTempSpOffsetLoSp | zoneTempXXXXSpOffsetLoSp | Zone Temperature Setpoint Offset Low Setpoint | Zone Temperature XX Setpoint Offset Low Setpoint |  | zoneTemp(\d{0,4})SpOffsetLoSp | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | zone,air,temp,offset,low,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTempSpOvr | zoneTempXXXXSpOvr | Zone Temperature Setpoint Override | Zone Temperature XX Setpoint Override |  | zoneTemp(\d{0,4})SpOvr | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,temp,active,effective,ovr | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTempSummerDb | zoneTempSummerDb | Zone Temperature Summer Deadband | Zone Temperature Summer Deadband |  | zoneTempSummerDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | zone,air,temp,active,summer,deadband,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTempSummerMaxSp | zoneTempSummerMaxSp | Zone Temperature Summer Max Reset Setpoint | Zone Temperature Summer Max Reset Setpoint |  | zoneTempSummerMaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,temp,active,summer,max,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTempSummerMinSp | zoneTempSummerMinSp | Zone Temperature Summer Min Reset Setpoint | Zone Temperature Summer Min Reset Setpoint |  | zoneTempSummerMinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,temp,active,summer,min,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTempSummerSp | zoneTempSummerSp | Zone Temperature Summer Setpoint | Zone Temperature Summer Setpoint |  | zoneTempSummerSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,temp,active,summer,common,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTempWinterDb | zoneTempWinterDb | Zone Temperature Winter Deadband | Zone Temperature Winter Deadband |  | zoneTempWinterDb | No | No | No | Number |  |  | fahrenheit_degrees | celsius_degrees | 1 | 1 |  |  | zone,air,temp,active,winter,deadband,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTempWinterMaxSp | zoneTempWinterMaxSp | Zone Temperature Winter Max Reset Setpoint | Zone Temperature Winter Max Reset Setpoint |  | zoneTempWinterMaxSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,temp,active,winter,max,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTempWinterMinSp | zoneTempWinterMinSp | Zone Temperature Winter Min Reset Setpoint | Zone Temperature Winter Min Reset Setpoint |  | zoneTempWinterMinSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,temp,active,winter,min,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTempWinterSp | zoneTempWinterSp | Zone Temperature Winter Setpoint | Zone Temperature Winter Setpoint |  | zoneTempWinterSp | No | No | No | Number |  |  | fahrenheit | celsius | 1 | 1 |  |  | zone,air,temp,active,winter,common,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneThreeThird | zoneXXXXThreeThird | Zone Three Third | Zone XX Three Third |  | zone(\d{0,4})ThreeThird | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | zone,light,threeThird,cmd | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneTwoThird | zoneXXXXTwoThird | Zone Two Third | Zone XX Two Third |  | zone(\d{0,4})TwoThird | Yes | Yes | No | Bool | On/Off | On/Off | [6 empty] | zone,light,twoThird,cmd | LTGE,LTGI | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneVOC | zoneVOCXXXX | Zone VOC | Zone VOC XX |  | zoneVOC(\d{0,4}) | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,voc,sensor | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneVOCAlarm | zoneVOCXXXXAlarm | Zone VOC Alarm | Zone VOC XX Alarm |  | zoneVOC(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,voc,common,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneVOCDb | zoneVOCXXXXDb | Zone VOC Deadband | Zone VOC XX Deadband |  | zoneVOC(\d{0,4})Db | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,voc,deadband,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneVOCHiAlarm | zoneVOCXXXXHiAlarm | Zone VOC High Alarm | Zone VOC XX High Alarm |  | zoneVOC(\d{0,4})HiAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,voc,high,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneVOCHiSp | zoneVOCXXXXHiSp | Zone VOC High Setpoint | Zone VOC XX High Setpoint |  | zoneVOC(\d{0,4})HiSp | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,voc,high,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneVOCLevelAlarm | zoneVOCXXXXLevelYYYYAlarm | Zone VOC Level Alarm | Zone VOC XX Level YY Alarm |  | zoneVOC(\d{0,4})Level(\d{0,4})Alarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,voc,level,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneVOCLoAlarm | zoneVOCXXXXLoAlarm | Zone VOC Low Alarm | Zone VOC XX Low Alarm |  | zoneVOC(\d{0,4})LoAlarm | Yes | Yes | No | Bool | Alarm/Normal | Alarm/Normal | [6 empty] | zone,air,voc,low,alarm | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneVOCLoSp | zoneVOCXXXXLoSp | Zone VOC Low Setpoint | Zone VOC XX Low Setpoint |  | zoneVOC(\d{0,4})LoSp | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,voc,low,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneVOCMaxSp | zoneVOCXXXXMaxSp | Zone VOC Max Setpoint | Zone VOC XX Max Setpoint |  | zoneVOC(\d{0,4})MaxSp | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,voc,max,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneVOCMinSp | zoneVOCXXXXMinSp | Zone VOC Min Setpoint | Zone VOC XX Min Setpoint |  | zoneVOC(\d{0,4})MinSp | No | No | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,voc,min,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)
zoneVOCSp | zoneVOCXXXXSp | Zone VOC Setpoint | Zone VOC XX Setpoint |  | zoneVOC(\d{0,4})Sp | Yes | Yes | No | Number |  |  | parts_per_million | parts_per_million | 0 | 0 |  |  | zone,air,voc,effective,sp | AC,AHU,ATU,CF,CRAC,CRAH,CUH,DAC,DH,DHU,DOAS,EC,EF,ERU,FCU,FPB,HP,HRU,HVHS,HVLS,MAU,MSC,PH,PIU,RP,RPC,RPF,RTU,UH,UV,VAV,VRF,ZD,ZN,FCU,HP | 2.12,2.13,2.14,2.15 (Released),2.16 (Pre-Release)